## Change Log
Date | Table | Description of Change | Cell Color/Text Color
2024-06-11 | F - Controlled Receptacles | Add footnote 2 | Yellow/Red
2024-06-11 | F - Controlled Receptacles, Column 02 | Revised two dropdown options | Yellow/Red
2025-02-11 | F - Controlled Receptacles, Column 04 | Revised dropdown option
2024-06-11 | F - Controlled Receptacles, Column 05 | Remove "durable" from "permanent durable…" column header | Yellow/Red
2024-06-11 | F- Electric Ready | Remove text from "Gas/ Propane Clothes Dryers In Common Areas" field | Yellow/Red
2024-06-11 | F- Electric Ready | Add new fields - "Gas/Propane Water Heaters Serving Individual Dwelling Units" and "Gas/Propane Water Heaters Serving Multiple Dwelling Units" | Yellow/Red

## NRCI Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | NRCI-ELC-E
This Certificate of Installation documents the installation of electrical power distribution system features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | NRCI-ELC-E
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator

## LMCI Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | LMCI-ELC-E
This Certificate of Installation documents the installation of electrical power distribution system features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for low-rise residential and low-rise mixed-use occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | LMCI-ELC-E
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator

## Table A. General
A. GENERAL INFORMATION
01 | Project Location (city): | A01_ProjectCity | 05 | Authority Having Jurisdiction:
02 | Zip Code: |  | 06 | Building Permit #:
03 | Date of Permit Set used for construction: |  | 07 | Date of As-built Set:
04 | Name of Permit Set used for construction: |  | 08 | Name of As-built Set:

## Table B. Scope
B. INSTALLER SCOPE
This table indicates the construction systems and materials documented on this Certificate of Installation.
01
□ | Electric Service Meter(s) | □ | Voltage Drop to feeders
□ | Separation of load downstream of meter(s) | □ | Voltage drop to branch circuits
□ | 120V Receptacle (Outlet) Control(s)
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing general lighting vs. decorative/ accent lighting, this will show what is being documented.
Note on B5: 4.15.21 Triggers Electrical Metering sub-table
Note on B6: 4.15.21 Separation of Circuits sub-table
Note on F6: 5.14.21: Both of these trigger the Voltage Drop subtable
Note on B7: 4.15.21 Controlled Receptacle sub-table

## Table C. Compliance
C. COMPLIANCE RESULTS
This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance. If the installation is not equal or better, Section 10-103(a)2B requires the Certificate of Compliance form to be revised accordingly to demonstrate compliance.
01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE
Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply.
The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly.
c
Note on B4: 10/7/22 -IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INCOMPLETE", this says "FORM NOT COMPLETE" OR - IF cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" OR - IF ALL assemblies/equipment compliance columns in ALL subtables triggered say "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE", that is what is shown here. OR - IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED", that is what is shown here. ELSE - this field says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A5: Sally Blair: Excel Row 5 triggered if "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE" OR "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" is triggered in 01.
Note on A6: Sally Blair: Excel Row 6 triggered if "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" is triggered in 01.

## Table D Exceptional Conditions
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact requirements documented on the Certificate of Compliance.
Remarks below are triggered from other tables in the CI Form and are not editable by the user.
ADD NOTES FOR CONTROL CHANGES
Metering capabilites on the Electrical Metering subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets metering capability requirements.
Receptacle controls on the Controlled Receptacles subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets control requirements.
Note on B10: 4.15.21 This note triggers if any of the per NRCC capabilites do not match the as-built capabilites in the Electrical Metering sub-table
Note on B11: 4.15.21 This note triggers if any of the per NRCC capabilites do not match the as-built capabilites in the Electrical Metering sub-table

## Table E. Notes
E. INSTALLER NOTES
This table includes remarks made by the installer to the Authority Having Jurisdiction.

## Table F. Install Details
F. INSTALLATION DETAILS
The following tables indicate performance requirements as documented on the permitted Certificate of Compliance for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.
After this table heading, the appropriate Table F "Subtables" from the other tabs would appear based on what scope the installer is completing the form for.
Example, if they are completing the form for installing receptacle controls, subtable on the "F.Receptacle Controls" tab would appear here.

## F. Electrical Metering
|  |  | From NRCC |  |  | user Input |  | Calculated
Service Electrical Metering
01 |  | 02 | 03 | 04 | 05 | 06 | 07
Electrical Service Designation/ Description |  | Rating (kVA) | Required Metering Capabilities |  |  |  | Metering Compliance
|  |  | Instantaneous Demand (kW) | Historical Peak Demand (kW) | Tracking kWh for user-defined period | kWh per rate period
Per C of C | F01_ElectricalServiceName | F02_ElectricalServiceRating | F03a_MeteringDemandRequired | F03b_MeteringPeakDemandRequired | F03c_MeteringkWhPerUserPeriodRequired | F03d_MeteringkWhPerRatePeriodRequired
As-built Conditions |  |  | dropdown | dropdown | dropdown | dropdown
1 FOOTNOTES: Service is defined as "the conductors and equipment for delivering electric energy from the serving utility to the wiring system of the premise served" in §100.1 of the Energy Standards. 'Electrical Services' applies to the building service-entrance rating or to the submetering service. For a building with submetering, this applies to the submetering service size to the common use areas.
2 Feeder is defined as "all circuit conductors between the service equipment, the source of a separately derived system, or other power supply source and the final branch-circuit overcurrent device,” in Article 100 of the California Electrical Code.
3 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  |  | Instantaneous Dropdown | Historical Dropdown | Tracking Dropdown | Per Rate Dropdown
|  |  | Capability provided at service(s)1 | Capability provided at service(s)1 | Capability provided at service(s)1 | Capability provided at service(s)1
|  |  | Capability provided at panel(s) | Capability provided at panel(s) | Capability provided at panel(s) | Capability provided at panel(s)
|  |  | Capability provided at feeder(s)2 | Capability provided at feeder(s)2 | Capability provided at feeder(s)2 | Capability provided at feeder(s)2
|  |  | NA: Utilty Provided Metering System | NA: Utilty Provided Metering System | NA: Utilty Provided Metering System | NA: Utilty Provided Metering System
|  |  | NA: Subject to California Electrical Code Article 517 | NA: Installed kVA <= 250 | NA: Subject to California Electrical Code Article 517 | NA: Installed kVA <= 1,000
|  |  |  | NA: Subject to California Electrical Code Article 517 |  | NA: Subject to California Electrical Code Article 517
Note on A4: 4.15.21 This table triggers if "Electrical Metering" is selected in Table B
Note on D8: Sally Blair: If any NRCC F03 capabilities are applicable to this service, display term here should be "Required". Otherwise, you can use the "NA" display terms in the dropdowns for the other fields from the NRCC.
Note on H8: 10/7/22 If: All fields not gray/blank are not complete 07 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED3" Else if: 02-06 per C of C match 02-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: 02-06 C of C don't match 02-06 as-built 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## F.Separation Of Circuits
Separation of Electrical Circuits for Energy Monitoring
Submetered electrical power distribution systems that provide power to dwelling units/common living areas only in multifamily occupancies do not need to be included.
Electrical Service Designation/ Description: |  | from NRCC/LMCC Table G
01 |  | 02 | 03 | 04
Load Type1 |  | Minimum Required Separation of Load | Separation Method 2 | Compliance
Per C of C | G01_ElectricalLoadType | G02_ElectricalLoadSeparationRequirement | G03_ElectricalLoadComplianceMethod G03_NotApplicableMessage
As-built Conditions |  |  | dropdown
1 FOOTNOTES: For each separate load type, up to 10% of the connected load may be of any type.
2 See Chapter 8 of the Nonresidential Compliance Manual for more detail on Compliance Methods. https://www.energy.ca.gov/media/3881
3 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Seperation Method Dropdown
Method 1: Switchboards, motor control centers, or panelboard loads disaggregated for each load type
Method 2: Switchboards/ motor control centers/ panelboard supply other distribution equipment with loads disaggregated for each load type
Method 3: Branch circuits serve load types individually & provisions for adding future branch curcuit monitoring
Method 4: Complete metering system measures and reports loads by type
NA: New or replacement service meter only
NA: Add/Alt to feeders and branch circuits only
NA: System subject to CA Elec Code Article 517
Note on A5: Sally Blair: Each Electrical service designated in the NRCC will need to have it's own section (rows 5-9) in this table.
Note on E8: 4.15.21 If: All fields not gray/blank are not complete 04 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED3" Else if: 03 per NRCC match 03 as-built 04 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: 03 per NRCC does not match 03 as-built 04 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A11: 2.11.22: Need to update hyperlink when available

## F. Voltage Drop
Feeder and Branch Circuit Conductor Voltage Drop
01 |  | 02 | 03 | 04 | 05 | 06 | 07
Electrical Service Designation/ Description |  | Combined Voltage Drop on Installed Feeder/Branch Circuit Conductors Compliance Method | Voltage Drop Calculations | Voltage Drop to the Feeder(s) (%) | Voltage Drop After the Feeder(s) (%) | Total Voltage Drop (%) | Voltage Drop Compliance
Per C of C | H01_ElectricalServiceName | H02a_CircuitVoltageDropCompliance H02b_CircuitVoltageDropCompliance | H03_CircuitVoltageDropCalculations
As-built Conditions |  | dropdown | dropdown |  |  | equals 04 + 05
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  | Method Dropdown | Calculation Dropdown
|  | Voltage drop <= 5% | In Construction Documents
|  | Voltage drop > 5% & permitted by CA Electrical Code 647.4, 695.6, 695.7 | Contractor Provided
Gina, we aren't going to be able to combine voltage drops from two different NRCI-ELCs, but if we show it this way, the inspector could see that they are separate installers, and could look to see what the total would be if necessary.
Note on D6: Sally Blair: If NRCC = "In construction documents" OR "Attached" the display term here should be "In Construction Documents"
Note on F6: 5.14.21: NRCC row for columns 04-06 are blank and grey always because we don't collect this info in the NRCC, but want to collect it from the installer.
Note on H6: 10/7/22 If: 02-03 are not complete 07 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 02-03 per NRCC match 02-03 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: 02-03 per NRCC do not match 02-03 as-built 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## F. Controlled Receptacles
| From NRCC |  | user Input |  |  |  | Calculated
Circuit Controls and Controlled Receptacles
01 |  | 02 | 03 | 04 | 05 | 06
Room Name or Description |  | Location/ Type of Controlled Receptacles 1, 2 | Shut-Off Controls | Demand Response Controls | Permanent Durable Marking is Used | Compliance
Per C of C | I01_SpaceDescription | I02_ControlledReceptacleComplianceType | I03_ControlledReceptacleShutOffControl I03_NotApplicableMessage | I.04 (from NRCC; schema terms not yet available) | I05_AreControlledReceptaclesPermanentlyMarked I05_NotApplicableMessage
As-built Conditions |  | dropdown | dropdown | dropdown | dropdown
1 FOOTNOTES: Office areas, lobbies, conference rooms, kitchen areas in office spaces, and copy rooms must meet controlled receptacle requirements
2 Plug-in strips and other plug-in devices shall not be used to comply with the requirements of section 130.5(d)
The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  | Controlled Receptacles Dropdown | Shut-Off Controls | Demand Response Dropdown | Marking Dropdown
|  | Within 6ft of uncontrolled receptacles | Auto Time-Switch with applicable overrides | Included w capabilities per §110.12(e) | Controlled and Uncontrolled Receptacles Identified with Permanent Marking
|  | Split-wired receptacles Multiple receptacle with > 1 controlled and uncontrolled receptacle | Occupancy Sensor | NA: Spaces where demand responsive lighting controls are not installed. Building does not require demand responsive lighting controls per §110.12(c) | NA: Data Equipment Receptacle
|  | Within 6ft of uncontrolled AND multiple receptacle outlet Split-wired receptacles | Occ-sensing Hardwired Power Strip | NA: Health/ life safety regulation does not permit the receptacles to be automatically controlled | NA: Circuit > 20 Amperes
|  | 50% are controlled receptacles (hotel/motel room only) | Captive Card Key (hotel only) |  | NA: Uninteruptible Power Supply Receptacle intended for 24/7/365
|  | NA: Data Equipment Receptacle | NA: Data Equipment Receptacle |  | NA: Clock Receptacle >= 6FT Above Floor
|  | NA: Circuit > 20 Amperes | NA: Circuit > 20 Amperes |  | NA: Refrigerator/Water Dispenser Receptacle
|  | NA: Uninteruptible Power Supply Receptacle intended for 24/7/365 | NA: Uninteruptible Power Supply Receptacle intended for 24/7/365 |  | NA: Healthcare Facility
|  | NA: Clock Receptacle >= 6FT Above Floor | NA: Clock Receptacle >= 6FT Above Floor
|  | NA: Refrigerator/Water Dispenser Receptacle | NA: Refrigerator/Water Dispenser Receptacle
|  | NA: Healthcare Facility | NA: Healthcare Facility
Note on F7: Sally Blair: Display term can be "Included in Design" if NRCC-ELC I04 is true.
Note on G7: 10/7/22 If: All fields not gray/blank are not complete 06 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED2" Else if: 02-05 per NRCC match 02-05 as-built 06 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: 02-05 per NRCC do not match 02-05 as-built 06 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on C13: 5.14.21: Let's make all three of these dropdowns "select all that apply". For 2022 NRCC updates, we can make them "select all that apply" on that form too.

## F. Electric Ready
| User input | auto calculated | From another Table | From look up table
Electric Ready for Multifamily Occupancies
Gas/ Propane Furnaces Serving Individual Dwelling Units (Heat Pump Space Heater Ready) |  |  | << Triggered if triggered in NRCC/LMCC
Requirement
A dedicated 240 volt branch circuit shall be installed within 3 feet from the furnace and accessible to the furnace with no obstructions. The branch circuit shall be rated at 30 amps minimum. The blank cover shall be identified as “240V ready”. All electrical components shall be installed in accordance with the California Electrical Code.
The main electrical service panel shall have a reserved space to allow for the installation of a double pole circuit breaker for a future heat pump space heater installation. The reserved space shall be permanently marked as “For Future 240V use”.
Gas/ Propane Cooktops Serving Individual Dwelling Units |  |  | << Triggered if triggered in NRCC/LMCC
Requirement
A dedicated 240 volt branch circuit shall be installed within 3 feet from the cooktop and accessible to the cooktop with no obstructions. The branch circuit shall be rated at 50 amps minimum. The blank cover shall be identified as “240V ready”. All electrical components shall be installed in accordance with the California Electrical Code.
The main electrical service panel shall have a reserved space to allow for the installation of a double pole circuit breaker for a future electric cooktop installation. The reserved space shall be permanently marked as “For Future 240V use”.
Gas/ Propane Clothes Dryers Serving Individual Dwelling Units |  |  | << Triggered if triggered in NRCC/LMCC
Requirement
A dedicated 240 volt branch circuit shall be installed within 3 feet from the clothes dryer and accessible to the clothes dryer with no obstructions. The branch circuit shall be rated at 30 amps minimum. The blank cover shall be identified as “240V ready”. All electrical components shall be installed in accordance with the California Electrical Code.
The main electrical service panel shall have a reserved space to allow for the installation of a double pole circuit breaker for a future electric clothes dryer installation. The reserved space shall be permanently marked as “For Future 240V use”.
Gas/ Propane Clothes Dryers In Common Areas |  |  | << Triggered if triggered in NRCC/LMCC
Requirement
Conductors or raceway shall be installed with termination points at the main electrical panel, via subpanels panels if applicable, to a location no more than 3 feet from each gas outlet or a designated location of future electric replacement equipment. Both ends of the conductors or raceway shall be labelled “Future 240V Use.” The conductors or raceway and any intervening subpanels, panelboards, switchboards, and busbars shall be sized to meet the future electric power requirements, at the service voltage to the point at which the conductors serving the building connect to the utility distribution system, as specified below. The capacity requirements may be adjusted for demand factors in accordance with the California Electric Code. Gas flow rates shall be determined in accordance with the California Plumbing Code. Capacity shall be one of the following: - 24 amps at 208/240 volts per clothes dryer; - 2.6 kVA for each 10,000 Btu per hour of rated gas input or gas pipe capacity; or - The electrical power required to provide equivalent functionality of the gas-powered equipment as calculated by the responsible person.
Gas/Propane Water Heaters Serving Individual Dwelling Units |  |  |  | << Triggered if triggered in NRCC/LMCC
Requirement
A dedicated 125 volt, 20 amp electrical receptacle that is connected to the electric panel with a 120/240 volt 3 conductor branch circuit rated to 30 amps minimum, within 3 feet from the water heater and accessible to the water heater with no obstructions. In addition, all the following: - Both ends of the unused conductor shall be labeled with the word “spare” and be electrically isolated; and - A reserved single pole circuit breaker space in the electrical panel adjacent to the circuit breaker for the branch circuit in A above and labeled with the words “Future 240V Use”
The construction drawings shall designate a space at least 39 inches by 39 inches and 96 inches tall for the future location of heat pump water heater
Gas/Propane Water Heaters Serving Multiple Dwelling Units |  |  |  | << Triggered if triggered in NRCC/LMCC
Requirement
Physical space shall be reserved on the bus system of the main switchboard or on the bus system of a distribution board to serve the future heat pump water heater system including the heat pump and temperature maintenance tanks. In addition, the physical space reserved shall be capable of providing adequate power to the future heat pump water heater in accordance with the following: - Heat Pump. Meet one of the following: - The electrical power required to power a heat pump water heater system heat pump that meets the total building hot water demand as calculated and documented by the responsible person associated with the project. - The electrical power required that meets the requirements specified for the heat pump in Joint Appendix JA15.2.5. - Temperature Maintenance Tank. Meet one of the following: - The electrical power required to power a heat pump water heater system temperature maintenance tank that meets the total building hot water demand as calculated and documented by the responsible person associated with the project. - The electrical power required that meets the requirements specified for the temperature maintenance tank in Joint Appendix JA15.2.5.