## Change Log
Date | Table | Description of Change | Cell Color/Text Color
2025-01-03 | F - Dry Systems | Added Refrigerant Loop Heat Recovery field | Yellow Red Text
2025-01-03 | F- Boiler | Added Hot Water Suply Temperature field | Yellow Red Text
2025-01-03 | F - Chiller | Modified title of chiller table | Yellow Red Text
2025-01-03 | F - Mechanical Heat Recovery | Added new mechanical heat recovery table | Yellow Red Text
2025-01-03 | G -NRCA/NRCV/LMCV | modified NRCA, NRCV, LMCV certificates

## NRCI Headers
| NRCC-MCH schema term | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | NRCI-MCH-E
This Certificate of Installation is used to document the installation of mechanical features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies.
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | NRCI-MCH-E
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator

## LMCI Headers
| NRCC-MCH schema term | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | LMCI-MCH-E
This Certificate of Installation documents the installation of mechanical features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for low-rise residential and low-rise mixed-use occupancies.
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | LMCI-MCH-E
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator

## Table A. General
| NRCC-MCH schema term | calculated | user entry
A. GENERAL INFORMATION
01 | Project Location (city) | A01_ProjectCity PRF SCHEMA TERMS BELOW: Info01_ProjectCity | 04 | Authority Having Jurisdiction
02 | Zip Code |  | 05 | Building Permit #
03 | Date of Permit Set used for construction |  | 06 | Date of As-built Set

## Table B. Scope
B. INSTALLER SCOPE
This table indicates construction systems and materials documented on this Certificate of Installation.
01
□ | Dry System (Airside) Equipment | □ | Ventilation (including DOAS, ERV and HRV) | □ | System Controls | □ | Ductwork
□ | Boiler | □ | Pumps | □ | Terminal Box Controls | □ | Piping
□ | Chiller | □ | Fans and Air Economizers | □ | Heat Rejection Equipment (cooling towers, condensers, waterside economizers) | □ | Electric Resistance Heating
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing wall ductwork vs. piping, this will show what is being documented.
Note on A7: Sally Blair: In the UI, this will be a dropdown where the installer selects all that applies to their scope of work. The selections they make will trigger the appropriate subtable(s) in Table F.

## Table C. Compliance
C. COMPLIANCE RESULTS
This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance. If the installation is not equal or better, Section 10-103(a)2B requires the Certificate of Compliance form to be revised accordingly to demonstrate compliance.
01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE
Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply.
The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly.
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Note on B4: 10/7/22 -IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INCOMPLETE", this says "FORM NOT COMPLETE" OR - IF cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" OR - IF ALL assemblies/equipment compliance columns in ALL subtables triggered say "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE", that is what is shown here. OR - IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED", that is what is shown here. ELSE - this field says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A5: Sally Blair: Excel Row 5 triggered if "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE" OR "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" is triggered in 01.
Note on A6: Sally Blair: Excel Row 6 triggered if "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" is triggered in 01.

## Table D. Exceptional Condition
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact requirements documented on the Certificate of Compliance.
Remarks below are triggered from other tables in the NRCI/LMCI Form and are not editable by the user.
Control requirements on the Boiler Efficiency and Controls subtable do not match what was permitted on the Certificate of Compliance. Please verify installation meets controls requirements.
Control requirements on the Chiller Efficiency and Controls subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets controls requirements.
Control requirements on the Heat Rejection Equipment subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets controls requirements.
Control requirements on the Pumps subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets controls requirements.
Control requirements on the System Controls subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets controls requirements.
Control requirements on the Ventilation subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets controls requirements.
Fan economizer requirements on the Fans and Air Economizer subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets economizer requirements.
Note on A8: Sally Blair: Triggered in Boiler Efficiency and Controls subtable if any selection in columns 07 OR 08 differ from NRCC/LMCC.
Note on A9: Sally Blair: Triggered in Chiller Efficiency and Controls subtable if any selection in columns 09 OR 10 differ from NRCC/LMCC.
Note on A10: Sally Blair: Triggered in Heat Rejection Equipment subtable if any selection in columns 06 - 10 differ from NRCC/LMCC.
Note on A11: Sally Blair: Triggered in Pumps subtable if any selection in columns 05 - 08 differ from NRCC/LMCC.
Note on A12: Sally Blair: Triggered in System Controls subtable if any selection in columns 02 - 07 differ from NRCC/LMCC.
Note on A13: Sally Blair: Triggered in Ventilation subtable if any selection in columns 05 - 07 differ from NRCC/LMCC.
Note on A14: Sally Blair: Triggered in Fan and Air Economizer subtable if any selection in column 03 differ from NRCC/LMCC.

## Table E. Notes
E. INSTALLER NOTES
This table includes remarks made by the installer to the Authority Having Jurisdiction.
The UI would allow the installer to put in any notes they wish for the AHJ.

## F. Mechanical Heat Recovery
Mechanical Heat Recovery
01 |  | 02 | 03
Name or Item Tag |  | Simultaneous Mechanical Heat Recovery | Heat Recovery Requirements per §140.4(s)
Per C of C |  | Provided | Heat Recovery Systems Shall: - Transfer the lesser of the following from spaces in cooling to spaces in heating: - 25% of the peak heat rejection of the cooling system. - 25% of design capacity of all service water heating systems + design capacity of all space heating systems. - Heat or preheat the service water heating to the smaller of: - 30% of the peak heat rejection of the cooling system; or - 30% of design capacity of all service water heating systems.
As-built Conditions
Dropdown
Provided
Laboratory building with Exhaust Air Heat Recovery per 140.9(c)6
Buildings In Climate Zone 15 with SWHCAP < 600 kBtuh
Note on A3: 12/11/24 Table only shows up when HR is required and provided per the CC.
Note on C6: 12/11/24 = "Required" if: A.02 != 15 And F04 >= 600 kbtuh AND F02 + 0.1 * (F03 - F02) >= 2400 kbtu AND F04 + F05 >= 2200 kbtu OR F03 >= 3600 kbtu AND F04 + 0.1 * F05 >= 700 kBtu Else = "Not Required"
Note on D6: 12/11/24 If F06 = required and F04>= 500kbtu then this text shows up Else if F06 = required and F04 < 500kbtu, then this text shows up without the heat or preheat service water heating part else if F06 - not required, this field in BlankGrayedOut
Note on C7: 12/11/24 = "Required" if: A.02 != 15 And F04 >= 600 kbtuh AND F02 + 0.1 * (F03 - F02) >= 2400 kbtu AND F04 + F05 >= 2200 kbtu OR F03 >= 3600 kbtu AND F04 + 0.1 * F05 >= 700 kBtu Else = "Not Required"

## Table F. Install Details
F. INSTALLATION DETAILS
The following tables indicate performance requirements as documented on the permitted Certificate of Compliance for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.
After this table heading, the appropriate Table F "Subtables" from the other tabs would appear based on what scope the installer is completing the form for.
Example, if they are completing the form for installing boilers, subtable on the "Table F. Boilers" tab would appear here.
Diane, for ALL subtables, if there is no "NRCC/LMCC" value from the NRCC/LMCC-PRF, OR if the value is grey and blank in the NRCC/LMCC-MCH, then both the NRCC/LMCC cell AND the as-built condition cell are blank and grey and the compliance logic comparing the as-built condition to the NRCC/LMCC condition becomes excluded from the compliance logic (meaning if there is no NRCC value to compare the as-built condition to, it should not impact the compliance logic). Not sure how to reflect this in the schema, let's talk more about it. As we update this NRCI/LMCI, we can continue to add fields to the NRC/LMCC-PRF to fill these holes, but that's a future software endeavor.
Diane, we've received feedback that the "Yes" term for providing controls is too ambiguous so we'd like to replace that display term with "Provided" for both the NRCC/LMCC and NRCI/LMCI. We've noted a few places showing this, but everywhere you see "Provided" in this mock-up (highlighted in pink text), it says "Yes" in the NRCC/KMCI. There is also a place in Heat Rejection subtable (column 10) where the display term was "No", and we'd like to change it to "Not Provided". I've noted that in the Heat Rejection subtable. Other than this, all of the control dropdowns match the NRCC-MCH dropdowns.

## F. Dry Systems
|  |  | NRCC schema term | From NRCC |  |  |  |  | user Input | [5 empty] | Calculated
Dry System Equipment Schedule
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 0809 | 0910 | 1011 | 1112 | 1213 | 1314
Name or Item Tag |  | Model # | Equipment Type | Heating Mode |  |  |  |  | Cooling Mode |  |  |  |  | Equipment Compliance
|  |  |  | Rated Output (kBtu/h) | Supplemental Heating Output (kBtu/h) | Efficiency | Efficiency Unit | Refrigerant Loop Heat Recovery | Rated Output (kBtu/h) | Efficiency | Efficiency Unit | Efficiency | Efficiency Unit
Per C of C | F01_HvacSystemName PRF SCHEMA TERMS BELOW: HvacDry01_HvacSystemName | Always Gray | F03_ComputerRoomAC F03_FurnaceAC F03_FurnaceUnitHeater F03_HeatPumpAC F03_PTAC_PTHP F03_RoomAC_HP F03_SinglePackageVerticalACHP F03_UnitaryCondensersAC F03_UnitaryHeatPumps F03_VariableRefrigerantFlow PRF SCHEMA TERMS BELOW: NOTE, THESE TERMS DO NOT MATCH THE PRESCRIPTIVE TERMS YET. IN THE WORKS HvacDry02_AirSystemType HvacDry02_ZoneSystemType HvacDry02a_AirSubType | F06_HeatingRatedCapacity F06_NotApplicableMessage Fb02_HeatingRatedCapacity Fb02_NotApplicableMessage PRF SCHEMA TERMS BELOW: HvacDry04_HeatingDesignCapacity | F07_HeatingSupplementalCapacity F07_NotApplicableMessage PRF SCHEMA TERMS BELOW: HvacDry05_HeatingSupplementalCapacity | Fa06_EfficiencyAFUE Fa06_EfficiencyCOP Fa06_EfficiencyHSPF Fa06_CombustionEfficiency Fa06_ThermalEfficiency Fa06_NotApplicableMessage Fb03_EfficiencyMinimumValueCOP Fb03_NotApplicableMessage PRF SCHEMA TERMS BELOW HvacDry06b_EfficiencyAFUE HvacDry06b_EfficiencyCOP HvacDry06b_EfficiencyHSPF HvacDry06b_EfficencyNA | Fa04_EfficiencyType Fa04_NotApplicableMessage COP (Diane - display COP when 06 = "Fb03_EfficiencyMinimumValueCOP") PRF SCHEMA TERMS BELOW: HvacDry06a_EfficiencyType HvacDry06a_NotApplicableMessage |  | F09_CoolingRatedCapacity F09_NotApplicableMessage Fb05_CoolingRatedCapacity Fb05_NotApplicableMessage PRF SCHEMA TERMS BELOW: HvacDry07_CoolingSensibleDesignCapacity | Fa09_EfficiencyCOP Fa09_EfficiencyEER Fa09_EfficiencySCOP Fa09_EfficiencySEER Fb07_EfficiencyEER Fb07_NotApplicableMessage PRF SCHEMA TERMS BELOW HvacDry08b_EfficiencyEER HvacDry08b_EfficiencySEER HvacDry08b_EfficencyNA | Fa07_EfficiencyType EER (display "EER" when 09 = "Fb07_EfficiencyEER") PRF SCHEMA TERMS BELOW: HvacDry08a_EfficiencyType HvacDry08a_NotApplicableMessage | Fa09_EfficiencyCOP Fa09_EfficiencyEER Fa09_EfficiencySCOP Fa09_EfficiencySEER PRF SCHEMA TERMS BELOW HvacDry08b_EfficiencyEER HvacDry08b_EfficiencySEER HvacDry08b_EfficencyNA | Fa07_EfficiencyType PRF SCHEMA TERMS BELOW: HvacDry08a_EfficiencyType HvacDry08a_NotApplicableMessage
As-built Conditions |  |  | true/false in UI
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Dual Fuel Heat Pump Equipment Schedule
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13
Name or Item Tag |  | 02: Model #; 03: Heating Mode; 07: Cooling Mode; 13: Equipment Compliance
|  |  | System Category | Size Category (Btu/h) | Efficiency | Efficiency Unit | System Category | Size Category (Btu/h) | Efficiency | Efficiency Unit | Efficiency | Efficiency Unit
Per C of C |  | 02: Always Gray
|  |  | true/false in UI | true/false in UI |  |  | true/false in UI | true/false in UI
As-built Conditions |  | 03: true/false in UI; 04: true/false in UI
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
This entire subtable is new for 2022
DX DOAS Schedule
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Name or Item Tag |  | Model # | Equipment Type | Energy Recovery | Rating Condition | Efficiency | Efficiency Unit | Efficiency | Efficiency Unit | Equipment Compliance
Per C of C |  | 02: Always Gray; 07: ISMRE; 09: ISCOP
As-built Conditions |  | 03: true/false in UI; 04: true/false in UI; 05: true/false in UI
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
UI will have to present what was recorded in the NRCC/LMCC and ask if they installed exactly that (true/false) for each field, or if they installed something different, and then allow them to user enter their change.
For user entry fields that compliance logic depends on (such as efficiency in this table), need same data type/restrictions as in the NRCC/LMCC so the NRC/LMCC and NRCI/LMCI fields can be compared.
Note on O10: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" IF column 03 does not match NRCC (false in UI) OR IF column 06as-built < column 06NRCC OR IF column 10 as-built < column 10 NRCC OR If column 08 per C of C== Installed and 08 as-built != installed THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 03-06 & 08-10 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" OR IF column 06 as-built >= column 06 NRCC OR IF column 09 as-built >= column 09 NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on A16: 3.16.22: This table shows up if the Dual Fuel Heat Pump table shows up in NRCC/LMCC-MCH Table F.
Note on N20: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" IF columns 03, 04, 07, 08 does not match NRCC (false in UI) OR IF column 05as-built < column 05CofC OR IF column 09as-built < column 09CofC OR IF column 11as-built < column 11CofC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 03-12 as-built match CofC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" OR IF column 05as-built >= column 05CofC OR IF column 09as-built >= column 09CofC OR IF column 11as-built >= column 11CofC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on D21: 1/29/25 If system type in CC is dual fuel heat pump, this second row is here to support the gas part of the dual fuel system. If not dual fuel, then gray out the second row in both the Per C of C and the as-built
Note on D23: Lalor, Ben: If system type in CC is dual fuel heat pump, this second row is here to support the gas part of the dual fuel system. If not dual fuel, then gray out the second row in both the Per C of C and the as-built
Note on A27: 3.16.22: This table shows up if the DX-DOAS Efficiency table shows up in NRCC/LMCC-MCH Table F.
Note on K31: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" IF columns 03, 04, 05 do not match NRCC (false in UI) OR IF column 06as-built < column 06CofC OR IF column 08as-built < column 08CofC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 03-08 as-built match CofC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" OR IF column 06as-built >= column 06CofC OR IF column 08as-built >= column 08CofC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"

## F. Boiler
|  |  |  | Input from NRCC | UI/Installer Input |  | Calculated
Boiler Efficiency and Controls
01 |  | 02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 10
Tag/Plan Detail ID |  | Model # | Equipment Type |  | Quantity | Rated Input (Btu/h) | Rated Efficiency | Efficiency Unit | Controls |  |  | Equipment Compliance
[9 empty] | Isolation Valve | Temperature Reset | Hot Water Suply Temperature
Per C of C | Fc01_BoilerName PRF SCHEMA TERMS BELOW: HvacWet01_HvacEquipmentName | Always Gray | Fc02_BoilerType PRF SCHEMA TERMS BELOW: HvacWet02_BoilerType |  | Fc03_BoilerCount PRF SCHEMA TERM NOT AVAILABLE RIGHT NOW | Fc04_BoilerRatedInputRange PRF SCHEMA TERMS BELOW: HvacWet04_CapacityRated | Fc05_EfficiencyAFUE Fc05_ThermalEfficiency Fc05_CombustionEfficiency PRF SCHEMA TERMS BELOW: HvacWet06_EfficiencyAFUE HvacWet06_ThermalEfficiency HvacWet06_CombustionEfficiency | Fc07_EfficiencyType PRF SCHEMA TERMS BELOW HvacWet07_EfficiencyType HvacWet07_NotApplicableMessage | Fc08_BoilerIsolationValve NO PERFORMANCE SCHEMA TERM AVAILABLE | Fc09_TempResetControl NO PERFORMANCE SCHEMA TERM AVAILABLE
As-built Conditions |  |  | true/false in UI |  | 08: dropdown; 09: dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
[9 empty] | Isolation Dropdown | Temperature Reset Dropdown
[9 empty] | Provided | Provided
[9 empty] | NA: only 1 boiler in plant | NA: < 500,000 Btu/h
NA: Variable Flow Controls
NA: System serves Healthcare
Note on O7: 3/13/25 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" IF column 03 AND column 05 do not match NRCC (false in UI) OR IF column 06 as-built < column 06 NRCC OR if 10 as-built GT 10 perCofC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 03-06 & 08-09 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF column 06 as-built >= column 06 NRCC Or 10-as-built LT 10-Per C of C THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C" Note: Since the compliance logic says "INCOMPLETE" if columns 08 & 09 aren't completed, I think that covers the compliance logic for 08 & 09. If the installer matches the NRCC for these columns (along with everything else), the logic will say EXACTLY MATCHES, and if it doesn't match, but is completed, it will say "EQUAL OR BETTER".
Note on L12: Sally Blair: The NRCC display term is "Yes", but we'd like to replace that with "Provided" throughout the NRCC too. I've highlighted where this occurs throughout this mock-up in pink text.
Note on M13: Sally Blair: If any choice is selected in columns 07 or 08 that differ than what was on the NRCC, Table D needs to return the Row 8 note on the Table D tab.

## F. Chiller
|  |  | Input from NRCC | UI/Installer Input |  | Calculated
Chiller & Air To Water Heat Pump Efficiency and Controls
01 | 02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12
Tag/Plan Detail ID | Model # | Equipment Type |  | Quantity | Size (tons) | Rated Efficiency #1 | Efficiency Unit #1 | Rated Efficiency #2 | Efficiency Unit #2 | Controls |  | Equipment Compliance
[10 empty] | Isolation Valve | Temperature Reset
| Always Gray | Fd02_ChillerType PERFORMANCE SCHEMA TERMS BELOW HvacWet02_ChillerType |  | Fd03_ChillerCount PRF SCHEMA TERM NOT AVAILABLE RIGHT NOW | Fd04_ChillerTonsRange PERFORMANCE SCHEMA TERMS BELOW HvacWet04_ChillerCapacity | Fd06a_ChillerCOP Fd06a_EfficiencyCOP Fd06a_EfficiencyEER Fd06a_EfficiencyKWperTon Fd06b_EfficiencyCOP_IPLV Fd06b_EfficiencyEER_IPLV Fd06b_EfficiencyKWperTon_IPLV PRF SCHEMA TERMS BELOW: HvacWet06_EfficiencyEER HvacWet06_EfficiencyKWperTon NOTE - IPLV IS AN OPTION FOR EFFICIENCY UNIT AND I DO NOT SEE THAT OPTION IN THE SCHEMA | Fd08a_EfficiencyType PRF SCHEMA TERMS BELOW: HvacWet07_EfficiencyType HvacWet07_NotApplicableMessage | Fd06b_ChillerCOP Fd06b_EfficiencyCOP Fd06a_EfficiencyEER Fd06a_EfficiencyKWperTon Fd06b_EfficiencyCOP_IPLV Fd06b_EfficiencyEER_IPLV Fd06b_EfficiencyKWperTon_IPLV PRF SCHEMA TERMS BELOW: HvacWet06_EfficiencyEER HvacWet06_EfficiencyKWperTon NOTE - IPLV IS AN OPTION FOR EFFICIENCY UNIT AND I DO NOT SEE THAT OPTION IN THE SCHEMA | Fd08b_EfficiencyType PRF SCHEMA TERMS BELOW: HvacWet07_EfficiencyType HvacWet07_NotApplicableMessage | Fd09_ChillerIsolationValve NO PERFORMANCE SCHEMA TERM AVAILABLE | Fd10_TempResetControl NO PERFORMANCE SCHEMA TERM AVAILABLE
|  | true/false in UI |  | 05: true/false in UI; 10: dropdown; 11: dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
[10 empty] | Isolation Dropdown | Temp Reset Dropdown
[10 empty] | Provided | Provided
[10 empty] | NA: only 1 chiller in plant | NA: ≤ 500 kBtu/hr (41.67 tons)
[10 empty] | NA: chillers in series | NA: Variable Flow Controls
NA: System serves Healthcare
Note on J5: Sally Blair: Columns 05 & 06 are the top row in the NRCC
Note on L5: Sally Blair: Columns 07 & 08 are the bottom row in the NRCC, which may or may not apply. If they don't apply, blank and grey out.
Note on P7: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" IF column 03 AND column 05 do not match NRCC (false in UI) OR IF column 06 as-built < column 06 NRCC AND if unit in column 07 is "EER" or "COP" OR IF column 08as-built < column 08 NRCC AND 08 is not grey AND if unit in column 09 is "EER" or "COP" OR IF column 06 as-built < column 06 NRCC AND if unit in column 07 is IPLV and column 03 is EITHER Air Cooled: Condenser elec. operated or Air Cooled: w/o condenser elec operated or Absorption Double effect, indirect fired or Absorption Double effect, direct fired or Water Cooled: Gas engine OR IF column 08 as-built < column 08 NRCC AND 07 is not grey AND unit in column 08 is IPLV and column 02 is EITHER Air Cooled: Condenser elec. operated or Air Cooled: w/o condenser elec operated or Absorption Double effect, indirect fired or Absorption Double effect, direct fired or Water Cooled: Gas engine OR IF column 05as-built > column 05NRCC AND if unit in column 06 is "KW/ton" OR IF column 07as-built > column 07NRCC AND 07 is not grey AND if unit in column 08 is "kW/ton" OR IF column 05as-built > column 05NRCC AND if unit in column 06 is IPLV and column 02 is EITHER Water Cooled: Reciprocating or Water Cooled: Positive displacement or Water Cooled: Centrifugal IF column 07as-built > column 07NRCC AND 07 is not grey AND unit in column 08 is IPLV and column 02 is EITHER Water Cooled: Reciprocating or Water Cooled: Positive displacement or Water Cooled: Centrifugal THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 02-05 & 07 & 9-10 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" OR IF column 05as-built >= column 05NRCC AND if unit in column 06 is "EER" or "COP" OR IF column 07as-built >= column 07NRCC AND 07 is not grey AND if unit in column 08 is "EER" or "COP" OR IF column 05as-built >= column 05NRCC AND if unit in column 06 is IPLV and column 02 is EITHER Air Cooled: Condenser elec. operated or Air Cooled: w/o condenser elec operated or Absorption Double effect, indirect fired or Absorption Double effect, direct fired or Water Cooled: Gas engine OR IF column 07as-built >= column 07NRCC AND if unit in column 08 is IPLV and column 02 is EITHER Air Cooled: Condenser elec. operated or Air Cooled: w/o condenser elec operated or Absorption Double effect, indirect fired or Absorption Double effect, direct fired or Water Cooled: Gas engine OR IF column 05as-built <= column 05NRCC if unit in column 06 is kW/ton OR IF column 07as-built <= column 07NRCC if unit in column 08 is kW/ton OR IF column 05as-built <= column 05NRCC if unit in column 06 is IPLV and column 02 is EITHER Water Cooled: Reciprocating or Water Cooled: Positive displacement or Water Cooled: Centrifugal OR IF column 07as-built <= column 07NRCC AND 07 is not grey AND unit in column 08 is IPLV and column 02 is EITHER Water Cooled: Reciprocating or Water Cooled: Positive displacement or Water Cooled: Centrifugal THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C" Note: Since the compliance logic says "INCOMPLETE" if columns 09 & 10 aren't completed, I think that covers the compliance logic for 09 & 10. If the installer matches the NRCC for these columns (along with everything else), the logic will say EXACTLY MATCHES, and if it doesn't match, but is completed, it will say "EQUAL OR BETTER".
Note on O12: Sally Blair: The NRCC says "Yes", but we'd like to replace that with "Provided" throughout the NRCC.
Note on N13: Sally Blair: If any choice is selected in columns 09 or 10 that differ than what was on the NRCC, Table D needs to return the Row 9 note on the Table D tab.

## F. Heat Rejection
|  |  |  | Input from NRCC | UI/Installer Input |  | Calculated
Heat Rejection Equipment (Cooling Towers, Condensers, Waterside Economizers) Efficiency and Controls
01 |  | 02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12
Tag/Plan Detail ID |  | Model # | Equipment Type |  | 04: Quantity; 05: Rated Performance; 06: Performance Unit; 07: Controls; 12: Equipment Compliance
[8 empty] | Fan Speed Control | Tower Flow Turndown | Fan Control in Multiple Cell Equipment | Economizer Control | Condenser Water Temp. Reset
Per C of C | Fe01_HeatRejectionName | Always Gray | Fe02_HeatRejectionType PRF SCHEMA TERMS BELOW HvacWet02_HeatRejectionType |  | Fe03_HeatRejectionEquipmentCount Fe03_NotApplicableMessage PRF SCHEMA TERM NOT AVAILABLE RIGHT NOW | Fe05_CoolingTowerCapacityRated Fe05_HeatRejectionCondenserCapacityRated Fe05_NotApplicableMessage PEFORMANCE SCHEMA TERMS BELOW: HvacWet04_CapacityRated | Fe07_HeatRejectionCapacityUnits Fe07_NotApplicableMessage PERFORMANCE SCHEMA TERMS BELOW: HvacWet05_CapacityUnits | Fe08_HeatRejectionFanSpeedControl Fe08_NotApplicableMessage NO PEFORMANCE SCHEMA TERM AVAILABLE | Fe09_HeatRejectionTowerFlowTurnDown Fe09_NotApplicableMessage NO PEFORMANCE SCHEMA TERM AVAILABLE | Fe10_HeatRejectionFanControlMultipleCells Fe10_NotApplicableMessage NO PEFORMANCE SCHEMA TERM AVAILABLE | Fe11_HasWaterEconomizerControls Fe11_NotApplicableMessage PRF SCHEMA TERMS BELOW: HvacDry09_EconomizerControlMethod HvacDry09_NotApplicableMessage | Fe12_HasTempResetControls Fe12_NotApplicableMessage NO PERFORMANCE SCHEMA TERM AVAILABLE
As-built Conditions |  |  | true/false in UI |  | 07: dropdown; 08: dropdown; 09: dropdown; 10: dropdown; 11: dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
[8 empty] | Fan Speed Control Dropdown | Tower Flow Turndown Dropdown | Fan Control Dropdown | Economizer Control Dropdown | Cond. Water Temp Reset Controls Dropdown
[8 empty] | Provided | Provided | Provided | Designed per §140.4(e) | Provided
[8 empty] | NA: Fan motor < 7.5hp (5.6kW) | NA: Single condenser water pump | NA: Not multiple cell |  | Not Provided
[8 empty] | NA: Integral to other equip. | NA: Not open-circuit tower | NA: No variable speed drives
NA: Cond. fans serving > 1 refrigerant circuits
NA: Cond. fans serving flooded cond.
NA: Mult. fans & lead fans meet req.
Note on P7: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" OR IF column 02 does not match NRCC (false in UI) OR IF column 04as-built < column 04NRCC OR THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 02-04 & 06-10 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF column 04as-built >= column 04NRCC OR THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C" Note: Since the compliance logic says "INCOMPLETE" if columns 06- 10 aren't completed, I think that covers the compliance logic for 06- 10. If the installer matches the NRCC for these columns (along with everything else), the logic will say EXACTLY MATCHES, and if it doesn't match, but is completed, it will say "EQUAL OR BETTER".
Note on O13: Sally Blair: In the NRCC-MCH, this says "No", but we should change it to "Not Provided"
Note on M14: Sally Blair: If any choice is selected in columns 06-10 that differ from what was on the NRCC, Table D needs to return the Row 10 note on the Table D tab.

## F. Elec. Res
|  |  | Input from NRCC |  | UI/Installer Input | Calculated
Electric Resistance Heating
01 |  | 02 | 03 | 04 | 05
Name or Tag ID |  | Model # | Equipment Description | Output Capacity (kW) | Equipment Compliance
Per C of C | Ff01_ElectricResistanceName NOT SURE WHERE THE PRF SCHEMA TERM IS | Always Gray | Ff02_ElectricResistanceHeatingType NOT SURE WHERE THE PRF SCHEMA TERM IS | Ff03_ElectricResistanceHeatingCapacity NOT SURE WHERE THE PRF SCHEMA TERM IS
As-built Conditions
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Note on F7: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" OR If columns 04 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE This says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"

## F. Pumps
|  | Input from NRCC |  |  | UI/Installer Input |  |  |  |  | Calculated
Pumps
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Name or Tag ID |  | Type | Quantity | Horsepower (HP) | Controls |  |  |  | Equipment Compliance
[5 empty] | Variable Flow Controls | Hydronic Heat Pump Isolation | VSD on Pumps > 5HP | Differential Pressure Sensor
Per C of C | G01_PumpName PRF SCHEMA TERMS BELOW Pump01_HvacEquipmentName | G02_PumpOperationType PRF SCHEMA TERMS BELOW Pump02_PumpOperationType | G03_PumpCount PRF SCHEMA TERMS BELOW Pump03_PumpCount | G04_PumpMotorHP PRF SCHEMA TERMS BELOW Pump04_PumpMotorHP | G05_PumpControlVF G05_NotApplicableMessage PRF SCHEMA TERMS BELOW: Pump06_IsVSD | G06_HeatPumpIsolation G06_NotApplicableMessage SCHEMA TERM NOT AVAILABLE | G07_PumpControlVSD G07_NotApplicableMessage SCHEMA TERM NOT AVAILABLE | G08_DifferentialPressureSensorRequired SCHEMA TERM NOT AVAILABLE
As-built Conditions |  | 05: dropdown; 06: dropdown; 07: dropdown; 08: dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
[5 empty] | VF Dropdown | WLHP Dropdown | VSD Dropdown | DPS
[5 empty] | Provided | Provided | Provided | Provided
[5 empty] | NA: < 3 control valves | NA: Not connected to common water loop | NA: Not serving variable flow system
[5 empty] | NA: pump system < 1.5 hp | NA: No hydronic heat pump | NA: Condenser water serving only water-cooled chillers
Note on J7: 3.15.22: IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" If columns 03 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C OF C" ELSE This says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on F14: Sally Blair: If any choice is selected in columns 05-08 that differ from what was on the NRCC, Table D needs to return the Row 11 note on the Table D tab.

## F. Fans
|  | Input from NRCC |  | UI/Installer Input |  |  | Calculated
Fans and Air Economizers
01 | 02 | 03 | 04 | 05 | 06
Name or Tag ID | Quantity | Fan Function | Economizer | Fan Electrical Input Power (kW) | System Compliance
Per C of C |  |  |  | this should be allowance from NRCC
As-built Conditions |  | dropdown | dropdown
1 FOOTNOTE: Computer room economizers must meet requirements of §140.9(a) and will be documented on the NRCC-PRC-E document.
2 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  | Economizer Dropdown | Economizer Dropdown
|  | Supply | Fixed Temperature
|  | Return | Fixed Enthalpy
|  | Exhaust | Differential Temperature
|  | relief | Differential Enthalpy
|  | transfer | Waterside Economizer
NA: < 33 kBtu/h cooling
NA: Special OA filtration
NA: multifamily/hotel/motel
NA: Efficiency per Table 140.4-D
NA: DOAS with EAHR
See NRCC-PRC for details1
NA: Altered other than packaged AC or HP<54kBtu/h
NA: Controlled Environment Horticulture
This table is new for 2025
Fans and Air Economizers
01 | 02 | 03 | 06
Name or Tag ID | Economizer Type | Exception | System Compliance
Per C of C
As-built Conditions |  | dropdown
This entire subtable is new for 2022
Dedicated Outdoor Air System (DOAS)
01 | 02 | 03 | 04 | 05 | 06 | 07
System Name | Quantity | Delivered Directly To The Space | DOAS Fan Control | Multi-Zone DOAS with Cooling | Multifamily DOAS | System Compliance
Per C of C |  |  | Dropdown | Dropdown | Dropdown
As-built Conditions |  | dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  | Delivery Dropdown | Fan Control Dropdown | Multi-zone DOAS dropdown | DOAS Dropdown
|  | Yes | >=3 speeds | No heating or heat recovery to warm supply air > 60F when majority of zones require cooling | Not Serving Multifamily Common Use Space
|  | NA: Active Chilled Beam System |  | NA: No Mechanical cooling and heating | Option 1 - 170.2(c)4Nia
|  | NA: Exception 2 per 140.4(p)2/170.2(c)4N |  | NA: Single Zone | Option 2 - 170.2(c)4Nib
|  | NA: Exception 3 per 140.4(p)2/170.2(c)4N |  |  | Option 3 - 170.2(c)4Nic
This entire subtable is new for 2022
Exhaust Air Heat Recovery
01 | 02 | 03 | 04 | 05 | 06 |  | 07
Fan System Name | Required? | Type of Heat Recovery Rating | Required Recovery Ratio | Installed Recovery Ratio | Energy Recovery Bypass |  | System Compliance
Per C of C |  |  |  | NA
As-built Conditions |  | dropdown |  |  | dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Delivery Dropdown
|  | Sensible Energy Recovery Ratio |  |  | Bypass Dropdown
|  | Enthalpy Recovery Ratio |  |  | Energy Recovery Bypass or similar control Installed per 140.4(q)2
NA: DOAS unit with shut-off capabilities per 140.4(q)2
This entire subtable is new for 2022
Dwelling Unit Fan Efficacy & Energy/Heat Recovery
01 | 02 | 03 | 04 | 05 | 06 | 07
Fan System Name or Item Tag | System Airflow (cfm) | Input Power (kW) | Watts/CFM | Energy/Heat Recovery Ventilation | Sensible Recovery/Effectiveness | System Compliance
dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
ERV/HRV Dropdown
ERV Provided
HRV Provided
NA: CZ 3-10
NA: CFI
H. Fan Energy Index (FEI)
01 | 02 | 03 |  | 04
Fan System Name or Item Tag | Name or Item Tag | FEI Exception |  | FEI
Per C of C
As-built Conditions
Note on G6: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED2" IF column 05 as-built > column 05NRCC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 02- 05 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF column 05 as-built <= column 05 NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on E14: Sally Blair: If any choice is selected in column 03 that differ from what was on the NRCC, Table D needs to return the Row 14 note on the Table D tab.
Note on A33: 1/29/25 This table is only used for peformance (NRCC-PRF parent)
Note on E36: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED2" IF column 05 as-built > column 05NRCC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 02- 05 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF column 05 as-built <= column 05 NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on A47: 3.16.22: This table shows up if the DOAS table shows up in NRCC/LMCC-MCH Table H.
Note on H52: 10/11/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" OR If columns 02-06 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSe: THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on A63: 3.16.22: This table shows up if the Exahust Air Heat Recovery table shows up in NRCC/LMCC-MCH Table H.
Note on D65: Sally Blair: If col02 = "Not Required" THEN col03-06 all say "NA" in the Per C of C and As-built rows AND col 07 says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on C68: Sally Blair: Comes from CC: - Required for both heating and cooling design conditions - Not required - Required for heating design conditions - Required for cooling design conditions
Note on J68: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" IF column 05 as-built < column 04as-built THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 03-06 as-built match CofC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF column 05 as-built >= column 04 as-built OR column 02 says "Not required" THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on E69: Sally Blair: 0.60 if H.08 = "Sensible" 0.50 if H.08 = "Enthalpy"
Note on A85: 3.16.22: This table shows up if the Dwelling Unit Fan Efficacy & Energy/Heat Recovery table shows up in NRCC/LMCC-MCH Table H.
Note on E89: 11/30/21 =(03* 1,000) /02 for both CofC and as-built rows
Note on G89: 4.6.22 = 0.67 if 05as-built = Provided Else06 CofC and 06as-built ="NA"
Note on H89: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" IF column 06 as-built < column 06CofC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 02-06 as-built match CofC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF column 06 as-built >= column 6CofC OR column 06 says "NA" THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"

## F. Sys Controls
|  | Input from NRCC |  |  | UI/Installer Input |  | Calculated
System Controls
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 09 10 | 10 11
System Name |  | Thermostats | Shut-Off Controls | Isolation Zone Controls | Demand Response | Supply Air Temp. Reset | Window Interlocks | Direct Digital Control (DDC) | JA18 Guideline 36 Library Version | Heat Pump Defrost | System Compliance
Per C of C | I01_ControlSystemName PRF SCHEMA TERMS BELOW: NOT SURE WHERE ANY OF THESE TERMS ARE | I04_ThermostatType PRF SCHEMA TERMS BELOW: NOT SURE WHERE ANY OF THESE TERMS ARE | I05_ControlSystemShutOff PRF SCHEMA TERMS BELOW: NOT SURE WHERE ANY OF THESE TERMS ARE | I06_ControlSystemZone PRF SCHEMA TERMS BELOW: NOT SURE WHERE ANY OF THESE TERMS ARE | I07_ControlSystemDR PRF SCHEMA TERMS BELOW: NOT SURE WHERE ANY OF THESE TERMS ARE | I08_ControlSystemTempReset PRF SCHEMA TERMS BELOW: NOT SURE WHERE ANY OF THESE TERMS ARE | I09_ControlSystemWindows HvacSpec03_OperableWindowsHaveInterlock
As-built Conditions |  | dropdown | dropdown | dropdown | dropdown | dropdown | dropdown | dropdown | User Input
1 FOOTNOTES: Gravity gas wall heaters, gravity floor heaters, gravity room heaters, non-central electric heaters, fireplaces or decorative gas appliances, wood stoves are not required to have setback thermostats.
2 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  | Thermostat Dropdown | Shut Off Dropdown | Isolation Zone Dropdown | Demand Response Dropdown | SA Temp Reset Dropdown | Window Interlock Dropdown | DDC Dropdown |  | Heat Pump Defrost Dropdown
|  | Setback Thermostat | Auto Timeswitch | Auto Timeswitch | EMCS | Provided | Provided | Provided |  | Provided
|  | EMCS | Occ. Sensor | Occ. Sensor | DR Tstat per §110.12 | NA: Alteration | NA: Auto-closing doors | NA: Single Zone |  | NA: No Heat Pump
|  | Setback + DR Tstat per §110.12 | 4 Hour Timer | 4 Hour Timer |  | NA: Single Zone | NA: No thermostatic control | NA: Multifamily |  | NA Heat Pump not serving dwelling units
|  | NA: Eq. type per §110.2(c) exception1 | EMCS | EMCS | NA: PTAC, PTHP, Rm AC, HP | NA: Healthcare only | NA: Alteration project |  |  | NA: CZ 1, 6-10, 15 or 16
|  | Thermostat or EMCS capable of modulating compressor speed in reponse to space loads | Card Key (hotel/motel) | NA: Continuous Heat/Cool | NA: Healthcare only | NA: Would increase energy use | NA: No operable windows |  |  | NA: Altered Equipment
|  |  | NA: 7 day per §120.2(e)1 | NA: Altered per §141.0(b)2E | NA: Serves temp. sensitive process | NA: Serves humidity sensitive process | NA: Healthcare only |  |  | NA: Multifamily Bldg
|  |  | NA: Altered per §141.0(b)2E | NA: Single Zone |  | NA: Controls prevent reheat/recool/simultaneous | NA: dwelling unit
|  |  | NA: Healthcare only | NA: Serves < 25k ft2 |  | NA: Dwelling unit
|  |  | NA: dwelling unit | NA: Dwelling unit
Note on L6: 1/29/25 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED2" If columns 02-09 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE This says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on K12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Guideline 36 only applies to new/replaced equipment but not if the equipment is being altered. Should this be added as a choice? Reply: Guideline 36 does not apply to multifamily buildings at all, even common use area systems Reply: Addressed
Note on C13: Sally Blair: If any choice is selected in columns 02-07 that differ from what was on the NRCC, Table D needs to return the Row 12 note on the Table D tab.

## F. Ventilation
|  | Input from NRCC |  |  | UI/Installer Input |  |  | Calculated
Nonresidential, Hotel/Motel and Multifamily Common Use Ventilation Systems
01 |  | 02 |  |  | 03 |  |  | 04
System Name |  | System Design OA CFM Airflow1 |  |  | System Design Transfer Air CFM |  |  | Air Filtration2
J04_VentilationSystemName |  | J05_VentSystemOA PRF SCHEMA TERMS BELOW: Vent04_VentSystemOA |  |  | J06_VentSystemTransferAir PRF SCHEMA TERM UNAVAILABLE |  |  | J07_AirFiltrationRequirements PRF SCHEMA TERM UNAVAILABLE
dropdown
05 |  | 06 |  |  | 07 |  | 08 |  | 09
Space Name |  | Exhaust Ventilation |  |  | Occupant Sensor Controls |  | Demand Control Ventilation |  | System Compliance
Per C of C | J08_SpaceName | J15_ExhaustPerSpace J15_NotApplicableMessage PRF SCHEMA TERM BELOW Vent05_ExhaustFlowRate |  |  | J16b_OccupantSensorVent PRF SCHEMA TERMS BELOW: Vent07_MechVentControls |  | J16a_DemandControlVent PRF SCHEMA TERMS BELOW: Vent07_MechVentControls
As-built Conditions |  |  |  |  | dropdown |  | dropdown
1 FOOTNOTES: System CFM should include both mechanical and natural ventilation for the zone/system.
2 Air filtration requirements apply to the following three system types per §120.1(c)1A: space conditioning systems utilizing ducts to supply air to occupiable space; supply-only ventilation systems providing outside air to occupiable space; supply side of balanced ventilation systems including heat recovery and energy recovery ventilation systems providing outside air to occupiable space.
3 Uniform Mechanical Code may have more stringent ventilation requirements; the most stringent code requirement takes precedence.
4 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
[6 empty] | Occ Sens Dropdown | DCV Dropdown | Air filtration dropdown
[6 empty] | Provided per §120.1(d)5 | Provided per §120.1(d)4 | Provided
[6 empty] | NA: Continously operated per §120.2(e)3 exception | NA: Not required per §120.1(d)3 | NA: Not system type specified in footnote 2
[6 empty] | NA: System < 2kW demand + manual shutoff per §120.2(e)3 exception | NA: Space exhaust is > design ventilation rate exception
[6 empty] | NA: Hotel/ motel + manual shutoff per §120.2(e)3 exception | NA: Processes that generate dust, fumes, etc.& no local exhaust
[6 empty] | NA: Not required space type | NA: Area <150 ft2 or design occupancy < 10 people
Multifamily Dwelling Unit Ventilation Systems
01 |  | 02 | 0302 | 0403 | 0504 | 0605 | 06 | 0706
Space Name |  | Outside Air CFM1 | Supply Air CFM | Exhaust CFM | Local Exhaust | Air Filtration3 | Compartmentalization test4 | Space Compliance
Per C of C | J19_SpaceName PRF SCHEMA TERM BELOW: VentRes01_ThermalZoneName | J23_OA_SpaceRequiredMin PRF SCHEMA TERM BELOW: VentRes04_VentSystemOA | J24_VentilationPerSpace PRF SCHEMA TERM UNAVAILABLE | J25_ExhaustPerSpace PRF SCHEMA TERM BELOW: VentRes05_ExhaustFlowRate | J26a_BathroomIAQ J26b_BathroomVentIAQ J26c_KitchenHoodRange PRF SCHEMA TERM UNAVAILABLE | J27_AirFiltrationRequirements PRF SCHEMA TERM UNAVAILABLE | 0.3 CFM50/ft2 Required
As-built Conditions |  |  |  |  | dropdown | dropdown | user input
1 FOOTNOTES: Uniform Mechanical Code may have more stringent ventilation requirements; the most stringent code requirement takes precedence.
2 Kitchen range hood will be verified per NA7.18.1 to confirm model is rated by HVI or AHAM. |  |  |  |  | Local Exhaust dropdown | Air filtration dropdown
3 Air filtration requirements apply to the following three system types per §160.2(b)1 space conditioning systems utilizing ducts to supply air to occupiable space; supply-only ventilation systems providing outside air to occupiable space; supply side of balanced ventilation systems including heat recovery and energy recovery ventilation systems providing outside air to occupiable space. |  |  |  |  | Bathroom/Kitchen IAQ | Provided
4 The air leakage rate shall not exceed 0.3 cubic feet per minute at 50 Pa (0.2 inch water) per ft2 of dwelling unit envelope surface area, verified per RA3.8 or NA2.3. |  |  |  |  | Bathroom/Kitchen IAQ & Vent. | NA: Evaporative Cooler
Kitchen Range Hood 2
Bathroom IAQ
Bathroom IAQ & Vent.
Kitchen Range Hood 2
Note on L10: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED4" IF columns 02, 03 or 06 as-built < columns 02, 03 or 06 per NRCC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 02--04 and 06-08 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF columns 02 03 and 06 as-built >= columns 02 03, 06 NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C" Note: Since the compliance logic says "INCOMPLETE" if columns 05-07 aren't completed, I think that covers the compliance logic for 04, 07, 08. If the installer matches the NRCC for these columns (along with everything else), the logic will say EXACTLY MATCHES, and if it doesn't match, but is completed, it will say "EQUAL OR BETTER".
Note on I19: Sally Blair: If any choice is selected in columns 05-07 that differ from what was on the NRCC, Table D needs to return the Row 13 note on the Table D tab.
Note on K19: Sally Blair: Let's remove "Table J" from this and the NRCC display term, to keep the display terms consistent between the two forms.
Note on C26: 1/16/25 Remove 02 for 2025
Note on K28: 5/20/26 IF all fields aren't complete this says "INCOMPLETE" OR IF columns 02-04as-built < columns 02-04NRCC Or 06as-built > 06cc THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED NRCC C of C REVISED" OR If columns 02-06 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC C of C" ELSE IF columns 02-04as-built >= columns 02-04NRCC Or Or 06as-built < 06cc THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED NRCC C of C" Note: Since the compliance logic says "INCOMPLETE" if columns 05-06 aren't completed, I think that covers the compliance logic for 05-6. If the installer matches the NRCC for these columns (along with everything else), the logic will say EXACTLY MATCHES, and if it doesn't match, but is completed, it will say "EQUAL OR BETTER".
Note on H32: Sally Blair: User needs to be able to select more than one option here.

## F. Terminal Box Controls
Input from NRCC
Terminal Box Controls
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Zone/System/VAV Box Name or Item Tag |  | 02: Zonal Control Strategy; 03: Design; 07: Reheated, Recooled, Mixed Air Compliance; 09: Zone/ Box/ System Compliance
|  |  | Peak Primary Airflow CFM | Primary Air in Deadband CFM | Reheated Recooled Mixed Airflow CFM | Outside Air CFM | 1st Stage Modulates <95oF and Maintains DB Rate? | 2nd Stage Modulates from DB Flow to Heating Max Flow?
Per C of C | K01_ThermalZoneName | K02_ZonalControlStrategy PRF SCHEMA TERMS BELOW: Zone03_TerminalUnitType | K03_PrimaryAirFlowMaximum PRF SCHEMA TERMS BELOW: Zone06_PrimaryAirFlowMaximum | K04_PrimaryAirInDeadband PRF SCHEMA TERMS BELOW: Zone07_PrimaryAirInDeadband Zone07_NotApplicableMessage | K05_ReheatRecoolMixAirFlow PRF SCHEMA TERM UNAVAILABLE | K06_TerminalUnitOA PRF SCHEMA TERM UNAVAILABLE | K10_Stage1ModulatesLTE95F PRF SCHEMA TERM UNAVAILABLE | K11_Stage2ModulatesDBtoHeatFlow PRF SCHEMA TERM UNAVAILABLE
As-built Conditions |  | 02: Dropdown; 07: Dropdown; 08: Dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Zonal Ctrl Strategy dropdown
|  | No Reheat, Recool, Mixing |  |  |  |  | 1st Stage Dropdown | 2nd Stage Dropdown
|  | VAV w DDC @ zone |  |  |  |  | Yes | Yes
VAV w/o DDC @ zone
NA: Pressurization control
NA: Reheat via site/solar source
NA: Humidity control
NA: Peak SA < 300 CFM
NA: Healthcare Facility
We will need to look at more than just Zone03_TerminalUnitType to determine whether DDC is at the zone or not when parent is PRF. Looking into it with Nikhil. DDC is reported at the system level so we may need to look at the terminal units parent system, if thats possible. Note - DDC is a zonal input in EnergyPro
Note on H6: Ben Lalor: Do we really need 07 & 08? They wont be on the PRF. Only option is "Yes" in NRCC,
Note on J7: 3.15.22: IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" If columns 02-06 & 10-11 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" OR IF column 02as-built selection is ANY of the following - No Reheat, Recool, Mixing - NA: Pressurization Control - NA: Reheat via site/solar source - NA: Humidity Control - NA: Peak SA < 300 CFM - NA: Healthcare Facility OR column 02 says "VAV w/o DDC@zone" AND 05 as-built < 05 per NRCC OR column 02 says "VAV w DDC@zone" AND 05 as-built < 05 per NRCC AND 04 as-built <04 per NRCC AND both columns 10 & 11 say "Yes". THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C" ELSE This says "INSTALLED FEATURES DO NOT COMPLY PLEASE REVISE" Note: Diane, logic in bold here is same as Table K in NRCC-MCH
Note on C11: Sally Blair: Selection of VAV w DDC opens 03-11. Selection of VAV w/o DDC opens 03, 05,06,07,08.

## F. Ducts
Input from NRCC
Ducts
The following duct systems require duct leakage testing by a certified Mechanical Acceptance Test Technician or a HERS Rater. Learn more about the Acceptance Testing Program on the Energy Commission website here: https://www.energy.ca.gov/programs-and-topics/programs/acceptance-test-technician-certification-provider-program Learn more about the HERS Program on the Energy Commission website here: https://www.energy.ca.gov/programs-and-topics/programs/home-energy-rating-system-hers-program
01
Diane, this field would be L10a_DuctSystems ONLY IF L10b_DuctLeakageTestRequired = true
from NRCC | <<list all duct system names where L10b_DuctLeakageTestRequired = true
from NRCC
from NRCC
from NRCC

## F. Pipes
| Input from NRCC | UI/Installer Input | Calculated
Pipe Insulation
Insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Insulation exposed to weather shall be installed with a cover suitable for outdoor service. Insulation covering chilled water piping and refrigerant suction piping located outside the conditioned space shall have a Class I or Class II vapor retarder. All penetrations and joints of which shall be sealed. Insulation thickness (in) or R-value shall be per the following Title 24, Part 6 Table 120.3-A/ 160.3-D.

## G. NRCA
G. ACCEPTANCE TESTS & FIELD VERIFICATION
The following Acceptance Tests and HERS Verifications related to the systems or materials documented on this Certificate of Installation have been indicated on the permitted Certificate of Compliance as being required to comply with Title 24, Part 6.
Form/Title | Systems to be Field Verified
Certificates of Acceptance
Mechanical Acceptance Tests must be completed by a certified Acceptance Testing Technician and Certificate of Acceptance forms completed through an approved Acceptance Test Technician Certification Provider database. The Certificate of Acceptance forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
NRCA-MCH-02-A Outdoor Air must be submitted for all newly installed HVAC units. Note: MCH-02-A can be performed in conjunction with MCH-07-A Supply Fan VFD Acceptance (if applicable) since testing activities overlap. | AC-1; AC-2; XCV-1
NRCA-MCH-03-A - Must be submitted for Constant Volume Single Zone HVAC. | AC-1; AC-2; XCV-1 | < only trigger rows that are required by the project.
NRCA-MCH-04 - Must be submitted for Air Distribution Duct Leakage. | from NRCC
NRCA-MCH-05-A - Must be submitted for Air Economizer, DOAS, HRV and ERV Controls | from NRCC
NRCA-MCH-06-A - Must be submitted for Demand Control Ventilation. | from NRCC
NRCA-MCH-07-A - Must be submitted for Supply Fan Variable Flow Controls. | from NRCC
NRCA-MCH-08-A - Must be submitted for Valve Leakage Test. | from NRCC
NRCA-MCH-09-A - Must be submitted for Supply Water Temperature Reset Controls. | from NRCC
NRCA-MCH-10-A - Must be submitted for Hydronic System Variable Flow Controls. | from NRCC
NRCA-MCH-11-A - Must be submitted for Automatic Demand Shed Controls. | from NRCC
NRCA-MCH-12-A-FDD-F - Must be submitted for Packaged Direct Expansion Units. | from NRCC
NRCA-MCH-13-A-FDD - Must be submitted for Air Handling Units and Zone Terminal Units. | from NRCC
NRCA-MCH-14-A - Must be submitted for Distributed Energy Storage DX-AC Systems. | from NRCC
NRCA-MCH-15-A - Must be submitted for Thermal Energy Storage. | from NRCC
NRCA-MCH-16-A - Must be submitted for Supply Air Temperature Reset Controls. | from NRCC
NRCA-MCH-17-A - Must be submitted for Condenser Water. | from NRCC
NRCA-MCH-18-A - Must be submitted for Energy Management Control Systems. | from NRCC
NRCA-MCH-19-A - Must be submitted for Occupancy Sensor Controls. | from NRCC
NRCA-MCH-20-H - Must be submitted for Multifamily Ventilation. | from NRCC
NRCA-MCH-21-H - Must be submitted for Multifamily Envelope. | from NRCC
NRCA-MCH-22-A - Must be submitted for Multifamily Duct Leakage. | from NRCC
NRCA-MCH-23-A - Must be submitted for Multifamily HRV/ERV Verification. | from NRCC
NRCA-MCH-24A Cooling Tower Conductivity Controls | from NRCC
Certificates of Verification
HERS verifications must be completed by a HERS Rater and NRCV forms completed through an approved HERS Provider database. The Certificate of Verification forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
NRCV-MCH-04-H Duct Leakage Test | from NRCC
NRCV-MCH-24 Enclosure Air Leakage Worksheet | from NRCC
NRCV-MCH-27 High-rise Residential | from NRCC
NRCV-MCH-32 Local Mechanical Exhaust | from NRCC
There are no Acceptance Tests or HERS verifications indicated on the permitted Certificate of Compliance related to the systems or materials documented on this Certificate of Installation. |  | << Excel row 36 is triggered if no other rows in this table are triggered.
A copy of this Certificate of Installation should be distributed to the certified Acceptance Test Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A37: Sally Blair: This is a static field that is always on this table.

## G. LMCA
G. ACCEPTANCE TESTS & FIELD VERIFICATION
The following Acceptance Tests and HERS Verifications related to the systems or materials documented on this Certificate of Installation have been indicated on the permitted Certificate of Compliance as being required to comply with Title 24, Part 6.
Form/Title | Systems to be Field Verified
Certificates of Acceptance
Mechanical Acceptance Tests must be completed by a certified Acceptance Testing Technician and Certificate of Acceptance forms completed through an approved Acceptance Test Technician Certification Provider database. The Certificate of Acceptance forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
NRCA-MCH-02-A Outdoor Air must be submitted for all newly installed HVAC units. Note: MCH-02-A can be performed in conjunction with MCH-07-A Supply Fan VFD Acceptance (if applicable) since testing activities overlap. | AC-1; AC-2; XCV-1
NRCA-MCH-03-A - Must be submitted for Constant Volume Single Zone HVAC. | AC-1; AC-2; XCV-1 | < only trigger rows that are required by the project.
NRCA-MCH-04b-A - Must be submitted for Air Distribution Duct Leakage. | from LMCC
NRCA-MCH-05-A - Must be submitted for Air Economizer, DOAS, HRV and ERV Controls | from LMCC
NRCA-MCH-06-A - Must be submitted for Demand Control Ventilation. | from LMCC
NRCA-MCH-07-A - Must be submitted for Supply Fan Variable Flow Controls. | from LMCC
NRCA-MCH-08-A - Must be submitted for Valve Leakage Test. | from LMCC |  | NOT SURE IF THESE LMCA FORMS ARE GOING TO BE CREATED FOR 2022? CEC to confirm
NRCA-MCH-09-A - Must be submitted for Supply Water Temperature Reset Controls. | from LMCC
NRCA-MCH-10-A - Must be submitted for Hydronic System Variable Flow Controls. | from LMCC
NRCA-MCH-11-A - Must be submitted for Automatic Demand Shed Controls. | from LMCC
NRCA-MCH-12-A-FDD-F - Must be submitted for Packaged Direct Expansion Units. | from LMCC
NRCA-MCH-13-A-FDD - Must be submitted for Air Handling Units and Zone Terminal Units. | from LMCC
NRCA-MCH-14-A - Must be submitted for Distributed Energy Storage DX-AC Systems. | from LMCC
NRCA-MCH-15-A - Must be submitted for Thermal Energy Storage. | from LMCC
NRCA-MCH-16-A - Must be submitted for Supply Air Temperature Reset Controls. | from LMCC
NRCA-MCH-17-A - Must be submitted for Condenser Water. | from LMCC
NRCA-MCH-18-A - Must be submitted for Energy Management Control Systems. | from LMCC
NRCA-MCH-19-A - Must be submitted for Occupancy Sensor Controls. | from LMCC
NRCA-MCH-20-H - Must be submitted for Multifamily Ventilation. | from LMCC
NRCA-MCH-21-H - Must be submitted for Multifamily Envelope. | from LMCC
NRCA-MCH-22-A - Must be submitted for Multifamily Duct Leakage. | from LMCC
NRCA-MCH-23-A - Must be submitted for Multifamily HRV/ERV Verification. | from LMCC
NRCA-MCH-24A Cooling Tower Conductivity Controls | from NRCC
Certificates of Verification
HERS verifications must be completed by a HERS Rater and NRCV forms completed through an approved HERS Provider database. The Certificate of Verification forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
LMCV-MCH-04a-H - Must be completed by installer and submitted for Air Distribution Duct Leakage. | from LMCC
LMCV-MCH-04-H Duct Leakage Test | from LMCC
LMCV-MCH-24 Enclosure Air Leakage Worksheet | from LMCC
LMCV-MCH-27 High-rise Residential | from LMCC
LMCV-MCH-32 Local Mechanical Exhaust | from LMCC | << Triggered if no other rows in this table are triggered.
There are no Acceptance Tests or HERS verifications indicated on the permitted Certificate of Compliance related to the systems or materials documented on this Certificate of Installation.
A copy of this Certificate of Installation should be distributed to the certified Acceptance Test Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A38: Sally Blair: This is a static field that is always on this table.