## Change Log
Date | Table | Description of Change | Cell Color/Text Color
2025-02-07 | B | Added Pool/Spa scope checkbox | Yellow with red text
2025-02-07 | Equipment | Modify 03 header and enumerations | Yellow with red text
2025-02-07 | Equipment | Modify 04 enumerations | Yellow with red text
2025-02-07 | Equipment | Add fields to Domestic Hot Water Equipment Additional Requirements sub table | Yellow with red text
2025-02-07 | Equipment | Add electric ready requirements subtable | Yellow with red text
2025-02-07 | Distribution | Add system name to all sub-tables | Yellow with red text
2025-02-07 | Distribution | Modify display text for Recirculation Loop subtable | Yellow with red text
2025-02-07 | Controls | Modify display text for one field | Yellow with red text
2025-02-07 | Pool/Spa | Add new table | Yellow with red text
2025-03-21 | Equipment | Removed Columns 09 and 10 | Yellow with red text
2025-03-21 | Distribution | Revised trigger logic for rows | Yellow with red text

## NRCI Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | NRCI-PLB-E
This Certificate of Installation documents the installation of service water heating features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | NRCI-PLB-E
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator

## LMCI Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | LMCI-PLB-E
This Certificate of Installation documents the installation of service water heating features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential spaces with water heating systems in low-rise mixed-use buildings. Low-rise multifamily buildings which are not mixed-use should document water heatings systems on the LMCI-PLB-01-E for Central Water Heating systems in Dwelling Units and the LMCI-PLB-02-E for Single Dwelling Unit Water Heating Systems through HERS Providers Registries. |  |  |  | < language from 10-103(a)3
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | LMCI-PLB-E
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator

## Table A. General
A. GENERAL INFORMATION
01 | Project Location (city): | A01_ProjectCity | 05 | Authority Having Jurisdiction:
02 | Zip Code: | A02_Zipcode | 06 | Building Permit #:
03 | Date of Permit Set used for construction: |  | 07 | Date of As-built Set:
04 | Name of Permit Set used for construction: |  | 08 | Name of As-built Set:

## Table B. Scope
B. INSTALLER SCOPE
This table indicates construction systems and materials documented on this Certificate of Installation.
01 |  | 02 |  | 03 |  | 04
□ | Water Heating Equipment | □ | Distribution (piping, valves, insulation, etc.) | □ | Controls | □ | Pool/Spa
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing piping vs. controls, this will show what is being documented.

## Table C. Compliance
C. COMPLIANCE RESULTS
This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance. If the installation is not equal or better, Section 10-103(a)2B requires the Certificate of Compliance to be revised accordingly to demonstrate compliance.
01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE
Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply.
The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly.
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Note on B4: 10/7/22 -IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INCOMPLETE", this says "FORM NOT COMPLETE" OR - IF cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" OR - IF ALL assemblies/equipment compliance columns in ALL subtables triggered say "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE", that is what is shown here. OR - IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED", that is what is shown here. ELSE - this field says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A5: Sally Blair: Excel Row 5 triggered if "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE" OR "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" is triggered in 01.
Note on A6: Sally Blair: Excel Row 6 triggered if "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" is triggered in 01.

## Table D. Exceptional Condition
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact requirements documented on the Certificate of Compliance.
Remarks below are triggered from other tables in the NRCI/LMCI form and are not editable by the user.
Diane, there are no exceptional conditions for PLB at this time.

## Table E. Notes
E. INSTALLER NOTES
This table includes remarks made by the installer to the Authority Having Jurisdiction.
The UI would allow the installer to put in any notes they wish for the AHJ.

## Table F. Install Details
F. INSTALLATION DETAILS
The following tables indicate performance requirements as documented on the permitted Certificate of Compliance for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.
After this table heading, the appropriate Table F "Subtables" from the other tabs would appear based on what scope the installer is completing the form for.
Example, if they are completing the form for installing piping, subtable on the "F. Distribution" tab would appear here.

## F. Equipment
|  |  |  | From NRCC |  |  |  | user Input |  | Calculated
Domestic Hot Water Equipment Efficiency
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 09
Name or Item Tag |  | Model # | Space Type Individual or Central System | Equipment Type | Volume (gal) | Rated Input Capacity (Btu/h) | Capacity Unit | Rated Efficiency | Efficiency Unit | Standby Loss | DHW Equipment Compliance
Per C of C | F01_WaterHeaterName F07_WaterHeaterName PRF SCHEMA TERMS BELOW Water01_WaterHeaterName | Always Gray | "Individual if 01 comes from F01_WaterHeaterName Else "Central" PRF SCHEMA TERM NOT AVAILABLE IN TABLE I OF THE PRF | F02_WaterHeaterType F08_WaterHeaterType NO PRF SCHEMA TERM FOUND IN PRF TABLE I1 | F03_WaterHeaterVolume F03_NotApplicableMessage F09_WaterHeaterTankVolume F09_NotApplicableMessage PRF SCHEMA TERM BELOW Water05_StorageCapacity Water05_NotApplicableMessage | F10_WaterHeaterCapacityRated F10_NotApplicableMessage PRF SCHEMA TERMS BELOW Water06_WaterHeaterElectricFiredRatedInput Water06_WaterHeaterGasRatedInput | If prescriptive this is always "Btu/hr" IF PRF SCHEMA TERMS BELOW Water07_WaterHeaterRatedInputUnits | F11_ThermalEfficiency F11_EfficiencyAFUE F05_UniformEnergyFactor PRF SCHEMA TERMS BELOW Water08_EfficiencyCOP Water08_ThermalEfficiency Water08_EnergyFactor Water08_UniformEnergyFactor | F13_EfficiencyType F13_NotApplicableMessage (if 08 = F05_UniformEnergyFactor then this = "UEF") PRF SCHEMA TERMS BELOW Water08_NotApplicableMessage | F14_StandbyLoss F14_WaterHeaterStandbyLossFraction F14_NotApplicableMessage PRF SCHEMA TERMS BELOW Water11_WaterHeaterStandbyLossFraction Water11_NotApplicableMessage
As-built Conditions |  | 03: Dropdown; 04: Dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  |  | System Dropdown | Type Dropdown
|  |  | Individual | Gas Instantaneous
|  |  | Central | Electric Instantaneous
|  |  | Multiple Dwelling Units/Hotel/Motel Guest Rooms | Gas Storage
|  |  | Individual Dwelling Unit/Hotel/Motel Guest Room | Electric Storage
|  |  | Common Use Area | NEEA Individual Heat Pump Water Heater
|  |  | Nonresidential | Non-NEEA Individual Heat Pump Water Heater
|  |  | State Building | Air Source Heat Pump Water Heater
|  |  | School | Gas-Fired Instantaneous (50,000-200,000 BTUH)
|  |  | Individual School Bathroom | Gas-Fired Storage (< 75,000 BTUH)
Residential-Duty Commercial Gas-Fired Storage (75,000-105,000 BTUH)
Electric Instantaneous (<12kW)
Residential-Duty Commercial Electric Instantaneous (12-58.6kW)
Electric Storage
Electric Tabletop Water Heater
Replacement with Heat Pump Water Heater
Boiler
Indirect
Commercial Packaged Boiler
Commercial Instantaneous (>200kBtu/h or >12kW)
Commercial Storage (>75kBtu/h or >12kW)
Gas Storage Water Heater
Gas Instantaneous Water Heater
Gas Hot Water Supply Boilers
Electric Storage Water Heater
Residential-duty Gas Hot Water Supply Boilers (<300k Btu/h)
Commercial Package Gas Hot Water Supply Boilers (300k- < 1MM Btu/h)
Commercial Package Gas Hot Water Supply Boilers (>= 1MM Btu/h)
Domestic Hot Water Equipment Additional Requirements
The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
| System Name: | 03: Pulls in name from CC-PLB table F
(Applies to New Construction only) For gas or propane water heaters serving individual dwelling units, the follow components are included in the installation per Title 24, Part 6 §150.0(n)1: - Dedicated 125V, 20 amp electrical receptacle that is connected to the panel with a 120/240V 3 conductor, 10 AWG copper branch circuit within 3 ft from the water heater that's accessible and with both ends of the unused conductor labeled with the word "spare" and be electrically isolated. A single pole circuit breaker space in the panel adjacent to the circuit breaker for the branch circuit is provided labeled with the word "future 240V use"; and - Category III or IV vent, or Type B vent with straight pipe between the outside termination and where the water heater is installed; and - Condensate drain that is no more than 2in higher than the base of the water heater and drains without pump assistance; and - Gas supply line with a capacity of at least 200,000 BTUH
Unfired storage tank insulation shall have Internal + External ≥ R-16 OR External ≥ R-12. Label required per Title 24, Part 6 §110.3(c)3
(Applies to new state buildings only) 60% of energy for service water heating is from site solar energy or recovered energy per Title 24, Part 6 §110.3(c)5
Isolation valves installed for instantaneous water heater with input rating > 6.8 kBTUH or 2 kW per Title 24, Part 6 §110.3(c)6.
Backup heat is required when inlet air is unconditioned unless the compressor cut-off temperature is below the Heating Winter Median of Extremes for the closest location listed in Table 2-3 from Reference Joint Appendix JA2.
Consumer integrated HPWHs shall meet the following requirement:
From NRCC dropdown F.22
The primary storage tank temperature setpoint shall be at least 135°F - §170.2(d)2Aiv
The minimum heat pump water heater compressor cut-off temperature shall be equal to or lower than 40°F ambient air temperature
Electric Ready Requirements
| System Name: | 03: Pulls in name from CC-PLB table G
A condensate drain that is no more than 2 inches higher than the base of the installed water heater, and allows natural draining without pump assistance
A ventilation method meeting one of the following: - The designated space for the future heat pump water heater shall have a minimum volume of 700 cubic feet; or - The designated space for the future heat pump water heater shall vent to a communicating space in the same pressure boundary via permanent openings with a minimum total NFA of 250 square inches., so that the total combined volume connected via permanent openings is 700 cubic feet or larger. The permanent openings shall be: - Fully louvered doors with fixed louvers; or - Two permanent fixed openings located within 12 inches from the enclosure top and bottom; - The designated space for the future heat pump water heater shall include two 8 inches capped ducts, venting to the building exterior: - All ducts, connections, and building penetrations shall be sealed. - Exhaust air ducts and all ducts which cross pressure boundaries shall be insulated to a minimum insulation level of R-6. - Airflow from termination points shall be diverted away from each other.
Space shall be reserved for a Heat Pump. The minimum space reserved shall include space for service clearances and air flow clearances and shall meet one of the following: - The space reserved shall be the space required for a heat pump water heater system that meets the total building hot water demand as calculated and documented by the responsible person associated with the project; or - The space reserved shall meet the requirements specified in Joint Appendix JA15.2.1.
Space shall be reserved for Tanks.The minimum space reserved shall include space for service clearances and shall meet one of the following: - The space reserved shall be the space required for a heat pump water heater system that meets the total building hot water demand as calculated and documented by the responsible person associated with the project; or - The space reserved shall meet the requirements specified in Joint Appendix JA15.2.2.
Ventilation shall be provided by meeting one of the following: - Physical space reserved for the heat pump shall be located outside; or - A pathway shall be reserved for future routing of supply and exhaust air via ductwork from the reserved heat pump location to a suitable outdoor location. Penetrations through the building envelope for louvers and ducts shall be planned and identified for future use. The reserved pathway and penetrations through the building envelope shall be sized to meet one of the following: - The reserved pathway and penetrations shall be sized to serve a heat pump water heater system that meets the total building hot water demand as calculated and documented by the responsible person associated with the project. - The reserved pathway and penetrations shall be sized to meet the requirements specified in Joint Appendix JA15.2.3.
Condensate drainage piping. An approved receptacle that is sized per the California Plumbing Code for condensate drainage shall be installed within 3 feet of the reserved heat pump location, or piping shall be installed from within 3 feet of the reserved heat pump location to an approved discharge location that is sized in accordance with the California Plumbing Code, and meet one of the following: - Condensate drainage shall be sized to serve a heat pump water heater system that meets the total building hot water demand as calculated and documented by the responsible person associated with the project. - Condensate drainage piping shall be sized to meet the requirements specified in Joint Appendix JA15.2.4.
'we
Note on K6: Sally Blair: This is only relevant for the following system types in column 03. - electric storage - gas storage - gas fired instantaneous - hot water supply boilers
Note on D7: 2/7/25 This pulls enumeration from F.02 of the CC-PLB indicating the space type the WH system is serving.
Note on G7: Ben Lalor: This is kbtu/h in the PRF, can we convertto btu/h if this comes from the PRF?
Note on J7: Sally Blair: This is either: - Thermal Efficiency (Et) - Combustion Efficiency (Ec) - AFUE - Uniform Energy Factor (UEF)
Note on L7: 10/7/22 IF all fields aren't complete or grey this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" IF column 04 does not match C of C (false in UI) OR IF column 08as-built < column 08NRCC OR IF column 10as-built > column 10NRCC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 03-08 & 10 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF column 08as-built >= column 08NRCC OR IF column 10as-built <= column 10NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on K8: Sally Blair: This is a calculated field. If column 04 is electric storage, the equation is = 0.30+ (27/col 05) If column 04 is gas storage, gas fired instantaneous or hot water supply boilers, the equation is = (col 06/800)+(110 * col 05 x 0.5)
Note on E11: 2/7/25 This matches the simplified enumerations from F.06 of the CC-PLB. For PRF projects we will need to match the 2025 enumerations there.
Note on B44: Sally Blair: triggered if F.18 is "Yes" on NRCC-PLB
Note on B46: Sally Blair: triggered if F.20 is "Yes" on NRCC-PLB
Note on B47: 2/7/25 This row is rendered when CC-PLB F.22 == true Else this row stays minimized
Note on B48: 2/7/25 This row is rendered when CC-PLB F.22 == true Else this row stays minimized
Note on B49: Alexis Markstrum: This is the value from the dropdwon F.22
Note on B50: 2/7/25 This row is rendered when F.23b == true Else this rows stays minimized
Note on B51: 2/7/25 This row is rendered when F.23d == true Else this rows stays minimized
Note on B55: 2/7/25 This row is rendered when I.02 == true Else this rows stays minimized
Note on B56: 2/7/25 This row is rendered when I.03 == true Else this rows stays minimized
Note on B57: 2/7/25 This row is rendered when I.04 == true Else this rows stays minimized
Note on B58: 2/7/25 This row is rendered when I.05 == true Else this rows stays minimized
Note on B59: 2/7/25 This row is rendered when I.06 == true Else this rows stays minimized
Note on B60: 2/7/25 This row is rendered when I.07 == true Else this rows stays minimized

## F. Distribution
| From NRCC |  | user Input | Calculated
Domestic Hot Water Distribution Requirements
The following requirements have been included on the permitted Certificate of Compliance to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
Recirculation Loops in Central Systems Serving Dwelling Units or Nonresidential Spaces |  | << Section heading triggers if one of the requirements listed below triggers | PRESCRIPTIVE SCHEMA TERMS - NON OF THIS IS AVAILABLE IN THE PRF, WE SHOULD ALWAYS TRIGGER THIS WHOLE SECTION IF PRF IS THE ONE PROVIDING THE DATA
System Name: | Pulls in system name from CC-PLB Table G
Automatic air release valve no more than 4 feet from pump or verticle pump installation |  | << triggers if G.01 from NRCC/LMCC-PLB says "Yes" | G01_AirReleaseValve
Check valve or similar located between recirculation pump and water heating equipment to prevent backflow |  | << triggers if G.02 from NRCC/LMCC-PLB says "Yes" | G02_BackflowCheckValve
Hose bibb installed between pump and equipment and isolation valve between hose bibb and equipment |  | << triggers if G.03 from NRCC/LMCC-PLB says "Yes" | G03_HoseBibb
Isolation valves on both sides of the pump |  | << triggers if G.04 from NRCC/LMCC-PLB says "Yes" | G04_IsolationValves
Cold water and recirculation loop piping is not connected to the hot water storage tank drain port |  | << triggers if G.05 from NRCC/LMCC-PLB says "Yes" | G05_TankDrainPort
Check valve is installed on cold water supply between hot water system and next closest tee on cold water supply |  | << triggers if G.06 from NRCC/LMCC-PLB says "Yes" | G06_ColdWaterCheckValve
DWELLING UNITS ONLY: For central systems serving multiple dwelling units, design includes a recirculation system serving separate dwelling units per §170.2(d) unless building has < 8 dwelling units. |  | << triggers if G.07 from NRCC/LMCC-PLB says "Yes" | G07_RecircLoopCount
DWELLING UNITS ONLY: For heat pump water heating systems, the hot water return from the recirculation loop shall connect to a recirculation loop tank and shall not directly connect to the primary heat pump water heater inlet or the primary thermal storage tanks per §170.2(d)2Aii. |  | << triggers if G.0807 from NRCC/LMCC-PLB says "Yes"
DWELLING UNITS ONLY: For heat pump water heating systems, the fuel source for the recirculation loop tank shall be electricity if auxiliary heating is needed. The recirculation loop heater shall be capable of multi-pass water heating operation per §170.2(d)2AiiiB. |  | << triggers if G.0908 from NRCC/LMCC-PLB says "Yes"
DWELLING UNITS ONLY: The recirculation loop tank temperature setpoint shall be at least 10°F lower than the primary thermal storage tank temperature setpoint - §170.2(d)2Av |  | << triggers if G.09 from NRCC/LMCC-PLB says "Yes"
DWELLING UNITS ONLY: All hot water distribution piping shall be sized in accordance with the California Plumbing Code Appendix M per §170.2(d)2C. |  | << triggers if G.10 from NRCC/LMCC-PLB says "Yes"
DWELLING UNITS ONLY:A recirculation system with mechanical or digital thermostatic master mixing valve on each distribution supply and return loop and meet the requirements in Reference Appendix RA4.4, unless building has ≤ 8 dwelling units |  | Triggers if G.11 from CC-PLB says "Yes"
Distribution of Individual System(s) serving Dwelling Units |  | << Section heading triggers if one of the requirements listed below triggers
System Name: | Pulls in system name from CC-PLB Table G
Single 240 volt heat pump water heaters serving dwelling units must also include systems with: |  | << triggers if G.10 13 from NRCC/LMCC-PLB says "Yes"
| - Compact hot water distribution system as specified in Reference Appendix RA4.4.16 in climate zone 1 & 16; AND | << triggers if G.10a 13a from NRCC/LMCC-PLB says "Yes"
| - A drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9 in climate zone 16. | << triggers if G.10b 13b from NRCC/LMCC-PLB says "Yes"
A drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9 in climate zone 16. |  | << triggers if G.11 14 from NRCC-PLB says "Yes"
For recirculation distribution systems serving individual dwelling units, only Demand Recirculation Systems with manual on/off control as specified in the Reference Appendix RA4.4.9 shall be used. |  | << triggers if G.12 15 from NRCC-PLB says "Yes"
Mandatory Pipe Insulation Requirements |  | < This section is always triggered
System Name: | Pulls in system name from CC-PLB Table G
For systems serving dwelling units and common areas, pipe insulation must meet the minimum insulation requirements in Table 160.4-A (see below) except: - Piping that penetrates framing members shall not be required to have pipe insulation for the distance of the framing penetration. Piping that penetrates metal framing shall use grommets, plugs, wrapping or other insulating material to assure that no contact is made with the metal framing. Insulation shall abut securely against all framing members. - Piping installed in interior or exterior walls shall not be required to have pipe insulation if all of the requirements are met for compliance with Quality Insulation Installation (QII) as specified in the Reference Residential Appendix RA3.5. - Piping surrounded with a minimum of 1 inch of wall insulation, 2 inches of crawlspace insulation, or 4 inches of attic insulation, shall not be required to have pipe insulation. |  | << triggers if G.13 16 from NRCC-PLB says "Yes"
For systems serving nonresidential spaces, pipe insulation for the following applications must comply with the following: - Recirculating system piping, including supply and return piping of the water heater - The first 8 ft of hot and cold outlet piping, including between storage tank and heat trap, for a nonrecirculating storage system - Pipes that are externally heated |  | << triggers if G.14 17 from NRCC-PLB says "Yes"
Insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Insulation exposed to weather shall be installed with a cover suitable for outdoor service per §120.3(b)/ §160.4(f). Pipe insulation buried below grade must be installed in a water proof and non-crushable casing or sleeve. |  | << triggers if G.15 18 from NRCC-PLB says "Yes"
Insulation for hot water pipes shall be field verified as specifid in Reference Appendix RA3.6.3 |  | Triggers if G.12 from CC-PLB says "Yes"
Note on A3: Sally Blair: Triggers if Distribution selected in Table B.
Note on B41: 3.8.22: Let's copy this 120.3-A/160.4-A table over from the NRCC/LMCC-PLB so the installers can see the insulation requirements right here.

## F. Controls
| From NRCC |  | user Input | Calculated
Domestic Hot Water System Controls
The following requirements have been included on the permitted Certificate of Compliance to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance. |  |  | PRESRIPTIVE SCHEMA TERMS BELOW. NON OF THIS IS AVAILABLE IN THE PRF, WE SHOULD ALWAYS TRIGGER THIS WHOLE SECTION IF PRF IS THE ONE PROVIDING THE DATA
Manufacturers must certify that service water-heating systems shall be equipped with automatic temperature controls capable of adjustment from the lowest to the highest acceptable temperature settings for the intended use as listed in Table 3, Chapter 50 of the ASHRAE Handbook, HVAC Applications Volume or Table 613.1 of the California Plumbing Code for healthcare facilities. |  | << triggers if H.01 from NRCC/LMCC-PLB says "Yes" | H01_TempControlsCertification
On systems that have a total capacity greater than 167,000 Btu/hr, outlets that require higher than service water temperatures as listed- in the ASHRAE Handbook, Applications Volume, shall have separate remote heaters, heat exchangers, or boosters to supply the outlet with the higher temperature unless covered by California Plumbing Code Section 613.0. |  | << triggers if H.02 fromNRCC/LMCC-PLB says "Yes" | H02_OutletTempControls
Controls for circulating pumps or electrical heat trace systems are capable of automatically turning off the system unless system serves healthcare facility. |  | << triggers if H.03 from NRCC/LMCC-PLB says "Yes" | H03_CirculatingPumpControls
For recirculation systems serving multiple dwelling units, design includes automatic pump controls a mechanical or digital thermostatic master mixing valve on each distribution supply and return loop per §170.2(d), or §180.1(b)3 for additions. |  | << triggers if H.04 from NRCC/LMCC-PLB says "Yes" | H04_MultipleUnitsPumpControls
For recirculation systems serving individual dwelling units, design includes manual on/off controls as specified in Reference Appendix RA 4.4.9 per §170.2(d). |  | << triggers if H.05 from NRCC/LMCC-PLB says "Yes" | H05_SingleUnitOnOffControls
Combustion air positive shut-off shall be provided per §160.4(e) on all newly installed commercial boilers as follows: - Boiler with input capacity >= 2.5 MMBtu/h, in which the boiler is designed to operate with a nonpositive vent static pressure - Boilers where one stack serves two or more boilers with a total combined input capacity per stack of 2.5 MMBtu/h. |  | << triggers if H.06 from NRCC/LMCC-PLB says "Yes"
Boiler combustion air fans with motors >= 10 hp shall meet one of the following for newly installed boilers: - The fan motor shall be driven by a variable speed drive OR - The fan motor shall include controls that limit the fan motor demand to <= 30% of the total design wattage at 50% of the design air volume. |  | << triggers if H.07 from NRCC/LMCC-PLB says "Yes"
Newly installed boilers with an input capacity >= 5 MMbtu/h and a steady state full-load combustion efficiency < 90% shall maintain excess (stack-gas) oxygen concentrations <= 5% by volume on a dry basis over firing rates of 20-100%. Combustion air volume shall be controlled with respect to firing rate or flue gas oxygen concentration. Use of a common gas and combustion air control linkage or jack shaft is prohibited. |  | << triggers if H.08 fromNRCC/LMCC-PLB says "Yes"
Note on A3: Sally Blair: Triggers if Controls selected in Table B.

## F. Pool Spa
New Table For 2025
Pool & Spa
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Pool/ Spa Description | Pool/Spa Service Type | On/Off Control | Instructions | Covers | Electric Resistance Heating Equipment | Heating Source Sizing | Piping | Pool Directional Inlets & Pump Control
Per C of C | bar: 03 to 10
As-built Conditions
Additional Requirements for Pool/ Spa Serving One Tenant §150.0(p)
Pool/Spa Description | 02: Pulls from 01 above
Dedicated-purpose pool pumps and replacement dedicated-purpose pump motors subject to State or Federal appliance standards shall be listed in the Commission's directory of certified equipment. - Dedicated-purpose pool pumps shall meet 20 CCR § 1605.1(g)(7) of the Appliance Efficiency Regulations. - Replacement dedicated-purpose pool pumpmotors shall meet 20 CCR § 1605.3 of the Appliance Efficiency Regulations.
Filtration pumps shall be sized, or if programmable, shall be programmed, so that the filtration flow rate is not greater than the rate needed to turn over the pool water volume in 6 hours or 36 gpm, whichever is greater.
Dedicated-purpose pool pumps with more than one speed shall have: - Controls that default to the filtration flow rate when no auxilary pool loads are operating, and; - Controls that default to the filtration flow rate setting within 24 hours and shall have an override capability for servicing.
System Piping must meet the following requirements: - A length of straight pipe that is greater than or equal to at least 4 pipe diameters shall be installed before the pump; and - Pool piping shall be sized so that the velocity of the water at maximum flow for auxiliary pool loads does not exceed 8 feet per second in the return line and 6 feet per second in the suction line; and - All elbows shall be sweep elbows or of an elbow-type that has a pressure drop of less than the pressure drop of straight pipe with a length of 30 pipe diameters.
Filters shall be at least the size specified in NSF/ANSI 50 for public pool intended applications.
Minimum diameter of backwash valves shall be 2 inches or the diameter of the return pipe, whichever is greater.
Note on K6: 2/7/25 IF all fields aren't complete or grey this says "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else IF 02-09 perCC does not match 02-09 AsBuilt THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" Else If columns 02-09 perCC does match 02-09 AsBuilt THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C"
Note on A11: Alexis Markstrum: This row is rendered if J.11 == true Else this row stays minimized
Note on A12: 2/7/25 This row is rendered if J.13 == true Else this row stays minimized
Note on A13: 2/7/25 This row is rendered if J.14 == true Else this row stays minimized
Note on A14: 2/7/25 This row is rendered if J.15 == true Else this row stays minimized
Note on A15: 2/7/25 This row is rendered if J.16 == true Else this row stays minimized
Note on A16: 2/7/25 This row is rendered if J.17 == true Else this row stays minimized

## G.NRCA NRCV
G. ACCEPTANCE TESTS & FIELD VERIFICATION
The following Acceptance Tests and HERS Verifications related to the systems or materials documented on this Certificate of Installation have been indicated on the permitted Certificate of Compliance as being required to comply with Title 24, Part 6.
Form/Title | Systems to be Field Verified
Certificates of Acceptance
There are no Certificates of Acceptance applicable to service water heating requirements.
Certificates of Verification
There are no Certificates of Verification applicable to service water heating requirements.
A copy of this Certificate of Installation should be distributed to the Field Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A9: Sally Blair: This is a static field that is always on this table.

## G.LMCA LMCV
G. ACCEPTANCE TESTS & FIELD VERIFICATION
The following Acceptance Tests and HERS Verifications related to the systems or materials documented on this Certificate of Installation have been indicated on the permitted Certificate of Compliance as being required to comply with Title 24, Part 6.
Form/Title | Systems to be Field Verified
Certificates of Acceptance
There are no Certificates of Acceptance applicable to service water heating requirements.
Certificates of Verification
HERS verifications must be completed by a HERS Rater and LMCV forms completed through an approved HERS Provider database. The Certificate of Verification forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
LMCV-PLB-21-H Central Hot Water Distribution HERS Verification | K01_SystemsToFieldVerify | THESE ARE NOT AVAILABLE IN THE PRF, ATLEAST NOT YET.
LMCV-PLB-22-H Individual Dwelling Unit Hot Water Distribution HERS Verification | K02_SystemsToFieldVerify
There are no Acceptance Tests or HERS verifications indicated on the permitted LMCC related to the systems or materials documented on this LMCI. |  | << Excel row 11 is triggered if no other rows in this table are triggered.
A copy of this Certificate of Installation should be distributed to the Field Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A12: Sally Blair: This is a static field that is always on this table.