## Change Log
Date | Table | Description of Change | Cell Color/Text Color
2025-02-12 | B | Remove Pool and Spa | Yellow Red Text
2025-02-12 | Refrigerated Warehouse/Space Condensers | Modify 06 enumerations to match CC | Yellow Red Text
2025-02-12 | B | Add Pipe Insulation checkbox | Yellow Red Text
2025-02-12 | Refrigerated Warehouse/Space Condensers | Add Pipe Insulation subtable | Yellow Red Text
2025-02-12 | Commercial Refrigeration | Add Pipe Insulation subtable | Yellow Red Text
2025-02-12 | Computer Room | Modify 02 economizer enumerations to match CC | Yellow Red Text
2025-02-12 | Lab factory | Add Fans and Exhaust Systems subtables | Yellow Red Text
2025-02-12 | Kitchen | Add Electric Ready Commercial Kitchens subtable | Yellow Red Text
2025-02-12 | Space Conditioning for Plant Production | Modify 02 enumeration to match CC | Yellow Red Text
2025-02-12 | CEH | Add Greenhouse Envelope subtable | Yellow Red Text

## NRCI Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | NRCI-PRC-E
This Certificate of Installation documents the installation of process system features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | NRCI-PRC-E
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator

## LMCI Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | LMCI-PRC-E
This Certificate of Installation documents the installation of process system features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for low-rise multifamily and low-rise mixed-use occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | LMCI-PRC-E
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator

## Table A. General
A. GENERAL INFORMATION
01 | Project Location (city): | A01_ProjectCity | 05 | Authority Having Jurisdiction:
02 | Zip Code: |  | 06 | Building Permit #:
03 | Date of Permit Set used for construction: |  | 07 | Date of As-built Set:
04 | Name of Permit Set used for construction: |  | 08 | Name of As-built Set:

## NRCI Table B. Scope
B. INSTALLER SCOPE
This table indicates construction systems and materials documented on this Certificate of Installation.
01
Electrical
□ | Elevator Lighting | □ | Escalator and Moving Walkways Controls
HVAC
□ | Refrigerated Spaces Underslab Heating | □ | Parking Garage Exhaust | □ | Elevator Ventilation Controls
□ | Computer Rooms | □ | Commercial Kitchen Ventilation | □ | Laboratory/Factory Exhuast & Fume Hood
Insulation | [5 empty] | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC
□ | Refrigerated Spaces Exterior Insulation
Plumbing
□ | Process Boilers | □ | Compressed Air Systems
Refrigeration
|  | □ | Refrigerated Space >= 3,000 ft2 Fan Powered Evaporators | □ | Refrigerated Space >= 3,000 ft2 Condensers
□ | Refrigerated Space >= 3,000 ft2 Compressors | □ | Refrigerated Space >= 3,000 ft2 Infiltration Barriers | □ | Transcritical CO2 Fan-powered Gas Coolers (new only)
□ | Pipe Insulation
Specialty
□ | Commercial Kitchen Hood | □ | Escalator and Moving Walkways Controls
□ | Controlled Environment Horticulture - Space Conditioning For Plant Production | □ | New Steam Traps | □ | Pool/Spa
Controlled Environment Horticulture - Lighting
Food/Beverage Stores >= 8,000 ft2
□ | Condensers Serving Commercial Refrigeration System | □ | Compressors and Condensing Units Serving Commercial Refrigeration System | □ | Refrigerated Display Cases
□ | Heat Recovery of Refrigeration System | □ | Transcritical CO2 Fan-powered Gas Coolers | □ | Pipe Insulation
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing Kitchen ventilation from pool/spa systems, this will show what is being documented.
Note on A6: 6.17.21 Triggers Elevator Lighting Table
Note on C6: 6.17.21 Triggers Escalator Table
Note on A8: 6.17.21 Triggers Underslab Heating Table
Note on C8: 6.17.21 Triggers Parking Garage Exhuast and Parking Garage Controls Tables
Note on E8: 6.17.21 Triggers Elevator Ventilation Controls Table
Note on A9: 6.17.21 Triggers Computer Room Table
Note on C9: 6.17.21 Triggers Kitchen Ventilation Table
Note on E9: 6.17.21 Triggers Lab/Factory Table
Note on A11: 6.17.21 Triggers the Refrig Space Ext Insulation Table
Note on A13: 6.17.21 Triggers the Process Boiler Table
Note on C13: 6.17.21 Triggers the Compressed Air Table
Note on C15: 7.23.21 Triggers Fan Power Evaporator subtable on Refrig Warehouse Table
Note on E15: 7.23.21 Triggers Condenser subtable on Refrig Warehouse Table
Note on A16: 7.23.21: Triggers Compressor subtable on Refrig Warehouse Table.
Note on C16: 7.23.21 Triggers Infiltration barrier subtable on Refrig Warehouse Table
Note on E16: 3.9.22: Triggers Transcritical CO2 subtable on Refrig Warehouse Table
Note on A17: 2/12/25 Triggers Pipe Insulation subtable on Refrig Warehouse Table.
Note on A19: 6.17.21 Triggers Kitchen Hood
Note on C19: 6.17.21 Triggers Escalator Table
Note on A20: 3.9.22: Triggers CEH table
Note on C20: 3.9.22: Triggers Steam Traps table
Note on E20: 3.9.22: Triggers Pool/Spa table
Note on A23: 6/21/23 Triggers Applicable subtable in Commerical Refrigeration Section
Note on C23: 6/21/23 Triggers Applicable subtable in Commerical Refrigeration Section
Note on E23: 6/21/23 Triggers Applicable subtable in Commerical Refrigeration Section
Note on A24: 6/21/23 Triggers Applicable subtable in Commerical Refrigeration Section
Note on C24: 6/21/23 Triggers Applicable subtable in Commerical Refrigeration Section
Note on E24: 2/12/25 Triggers Pipe Insulation subtable on Commercial RefrigerationTable.

## LMCI Table B. Scope
B. INSTALLER SCOPE
This table indicates construction systems and materials documented on this Certificate of Installation.
01
Electrical
□ | Elevator Lighting
HVAC
□ | Commercial Kitchen Ventilation | □ | Parking Garage Exhaust | □ | Elevator Ventilation Controls
Specialty
□ | Commercial Kitchen Hood | □ | Pool/Spa
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing Kitchen ventilation from pool/spa systems, this will show what is being documented.
Note on A6: 6.17.21 Triggers Elevator Lighting Table
Note on A8: 6.17.21 Triggers Kitchen Ventilation Table
Note on C8: 6.17.21 Triggers Parking Garage Exhuast and Parking Garage Controls Tables
Note on E8: 6.17.21 Triggers Elevator Ventilation Controls Table
Note on A10: 6.17.21 Triggers Kitchen Hood
Note on C10: 3.9.22: Triggers Pool/Spa table

## Table C. Compliance
C. COMPLIANCE RESULTS
This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance. If the installation is not equal or better, Section 10-103(a)2B requires the Certificate of Compliance form to be revised accordingly to demonstrate compliance.
01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE
Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply.
The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly.
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Note on B4: 10/7/22 -IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INCOMPLETE", this says "FORM NOT COMPLETE" OR - IF cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" OR - IF ALL assemblies/equipment compliance columns in ALL subtables triggered say "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE", that is what is shown here. OR - IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED", that is what is shown here. ELSE - this field says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A5: Sally Blair: Excel Row 5 triggered if "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE" OR "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" is triggered in 01.
Note on A6: Sally Blair: Excel Row 6 triggered if "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" is triggered in 01.

## Table D Exceptional Conditions
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact requirements documented on the Certificate of Compliance.
Remarks below are triggered from other tables in the NRCI/LMCI Form and are not editable by the user.
There are no exceptional conditions for the NRCI/LMCI-PRC

## Table E. Notes
E. INSTALLER NOTES
This table includes remarks made by the installer to the Authority Having Jurisdiction.

## F. Install Details
F. INSTALLATION DETAILS
The following tables indicate performance requirements as documented on the permitted Certificate of Compliance for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.
After this table heading, the appropriate Table F "Subtables" from the other tabs would appear based on what scope the installer is completing the form for.
Example, if they are completing the form for installing elevator controls, subtable on the "F. Elevator" tab would appear here.

## NRCI F. Refrigerated Warehouse
|  |  |  | From NRCC |  |  | user Input |  | Calculated
Refrigerated Warehouse/Space Fan Powered Evaporators
01 |  | 02 | 03 | 04 | 05 | 06 | 07
Name or Item Tag |  | Model # | Motor HP | Phase | Type or Efficiency | Fan Controls | Evaporator Compliance
Per NRCC | Ffan01_FanName | Always Grey | Ffan02_FanMotorHP | Ffan03_FanPhase Ffan03_NotApplicableMessage | Ffan04_FanMotorEfficiency Ffan04_NotApplicableMessage | Ffan06_EvapFanControl
As-built |  |  | dropdown | dropdown | dropdown | dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  |  | Motor HP Dropdown | Phase Dropdown | Efficiency Dropdown | Fan Control Dropdown
|  |  | <1 HP | Single Phase < 460V | ECM | Variable Speed based on Temp
|  |  | >= 1 HP | Three Phase | >=70% Efficiency | Variable Speed based on Humidity
Reduce airflow ≥ 40 % for ≥ 75% of time when compressor is not running.
Refrigerated Warehouse/Space Condensers (Air-cooled, Water-cooled, Evaporative-cooled, Adiabatic)
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08
Name or Item Tag |  | Model # | Condenser Location | Temp Setpoint Controls | Variable Speed Control | Refrigerant Type | Efficiency (Btuh/W) | Condenser Compliance
Per NRCC | Fconair02_ComponentName Fconwater02_ComponentName Fconadia02_ComponentName | Always Grey | Fconair03_CondenserLocation Fconwater03_CondenserLocation | Fconair05_CondenserTempControls Fconwater05_CondenserTempControls Fconadia04_CondenserTempControls | Fconair04_VariableSpeedControl Fconwater04_VariableSpeedControl Fconadia03_VariableSpeedControl | Fconair07_RefrigerantType Fconair07_NotApplicableMessage Fconadia06_RefrigerantType | Fconair09_CondenserEfficiency Fconwater09_CondenserEfficiency Fconadia08_CondenserEfficiency
As-built |  |  | dropdown | dropdown | dropdown | dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  |  | Condenser Location Dropdown | Temp Setpoint Dropdown | Variable Speed Fans Dropdown | Efficiency Dropdown
|  |  | Indoor | Designed to <= 70 @ ambient db temp | Variable speed fan(s) provided | Ammonia
|  |  | Outdoor | NA: Transcritical CO2 refrigeration | NA: Transcritical CO2 refrigeration | Halocarbon
NA: Transcritical CO2 refrigeration
NA: Condensing Unit that are components of walk-in coolers or freezers within the scope of Appliance Efficiency regulations.
Refrigerated Warehouse/Space Compressors
01 |  | 02 | 03 | 04 |  | 05 |  | 06
Name or Item Tag |  | Model # | Condensing Temp | Variable Speed Control |  | Variable Volume Ratio |  | Compressor Compliance
Per NRCC | Fcom02_ComponentName | Always Grey | Fcom03_CompressorTemps | Fcom04_CompressorVariableSpeed |  | Fcom05_VariableVolRatioStatus
As-built |  |  | dropdown | dropdown |  | dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  |  | Condensing Temp Dropdown | VS Control Dropdown |  | VVR Dropdown
|  |  | Min condensing temp < 70 deg | Controls compressor speed in response to refrigeration load |  | Auto vary volume ratio in response to operating pressure
|  |  | Transcritical CO2 w SST < 30deg: Min condensing temp <= 60 deg | NA: Not new open-drive screw compressor w SST <= 28deg |  | NA: Not screw compressor w > 150 HP motor
NA: > 1 dedicated compressor per suction group
NA: > 20% for quick chilling/freezing or cooling another refrigerated space
Refrigerated Warehouse/Space Infiltration Barriers and Automatic Door Closers
01 | 02 |  |  |  | 03 |  | 04
Room ID/ Description | Infiltration Barrier |  |  |  | Door Closure |  | Infiltration Barrier Compliance
Fbar01_SpaceName | Fbar02_InfiltrationBarrierMethod |  |  |  | Fbar02_DoorClosureMethod
| Dropdown |  |  |  | Dropdown
1 FOOTNOTE: Infiltration barriers include strip curtains, automatically-closing door, or an air curtain designed by the manufacturer
2 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
| IB Dropdown |  |  |  | Door Closure Method Dropdown
| Passageway between freezers and non-refrigerated spaces include infiltration barriers |  |  |  | Passageway between freezers & higher temp. spaces/ coolers and non-refrigerated spaces shall include automatic door closures per §120.6(a)9
| NA: openings < 16ft2 |  |  |  | NA: Room doesn't include people passageways between freezers/ higher temp./coolers/non-refrigerated spaces
NA: Dock doorway for trailers
NA: Room doesn't include passageways between freezers and non-refrigerated spaces
Transcritical CO2 Fan-powered Gas Coolers
01 |  | 02 | 03 | 04 | 05 | 06
Name or Item Tag |  | Variable Speed Control | Gas Cooler Pressure Controls | Design Condensing Temperatures | Efficiency (Btuh/W) | Compliance
Per NRCC |  | Variable speed fan(s) provided controlled per §120.6(a)8D | Condensing temp reset per §120.6(a)4F and cooler pressure setpoint maximizes efficiency
As-built |  |  |  | Dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Design Temp dropdown
Min condensing temp <=60 deg
Transcritical CO2 w SST < 30deg: Min condensing temp <= 70 deg
Mandatory Pipe Insulation All Occupancies
1 |  | 2 |  |  |  | 3
System Name |  | Pipe Insulation Applications |  |  |  | Pipe Insulation Protection
Per NRCC |  | For systems serving nonresidential spaces, pipe insulation for the following applications is specified to comply with Table 120.3-A1 or or Table 120.3-A2 (see below) - Recirculating system piping, including supply and return piping of the water heater - The first 8 ft of hot and cold outlet piping, including between storage tank and heat trap, for a nonrecirculating storage system - Pipes that are externally heated |  |  |  | Pipe and appurtenance insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Protection shall include: - Insulation exposed to weather shall be installed with a cover suitable for outdoor service - Pipe insulation buried below grade must be installed in a water proof and non-crushable casing or sleeve. - Pipe insulation covering chilled water piping and refrigerant suction piping located outside the conditioned space shall include, or be protected by, a Class I or Class II vapor retarder. All penetrations and joints shall be sealed.
As-built
Note on H6: 10/7/22 If: All fields are not complete if not grey 07 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 03-06 per NRCC match 03-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: 03-06 per NRCC do not match 03-06 as-built 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A15: Ben Lalor: This table covers all the NRCC condensers sub-tables
Note on I18: 10/7/22 If: All fields not grey are not complete 08 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 03-07 per NRCC match 03-07 as-built 08 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: 07 per NRCC > 07 as-built OR 03 per NRCC does not match 03 as-built OR 06 per NRCC does not match 06 as-built 08 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" Else: 08 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on I31: 10/7/22 If: 02-05 fields are not complete if not grey 06 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 03-05 per NRCC match 03-05 as built 06 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 06 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on H46: 10/7/22 If: 02 and 03 is not complete 04 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED2" Else if: 02 and 03 per NRCC match 02 and 03 as built 04 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: 02 and 03 per NRCC does not match 02 and 03 as built 04 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on C62: Sally Blair: This & column 03 are just static text in this table.
Note on G62: 10/7/22 IF all fields aren't complete, this says "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else If: column 05 as-built < column 05 Per NRCC, this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" Else If: columns 04-05 as-built match columns 04-05 NRCC, THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: column 05as-built >= column 05 Per NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"

## NRCI F.Refrig Spaces Insulation
Refrigerated Warehouse/Space Exterior Surface Insulation
01 | ¨ | Exterior surfaces of refrigerated warehouses/spaces are insulated at least to the R-values in TABLE 120.6-A-1 (see below).
TABLE 120.6-A REFRIGERATED WAREHOUSE/SPACE INSULATION
02 |  | 03 | 04 | 05
Space |  | Surface | Minimum R-Value | Insulation Compliance
Freezers |  | Roof/ Ceiling | 40
|  | Wall | 36
|  | Floor | 35
|  | Floor with all heating from productive refrigeration capacity1 | 20
Coolers |  | Roof/ Ceiling | 28
|  | Wall | 28
1 FOOTNOTE: All underslab heating is provided by a heat exchanger that provides refrigerant subcooling or other means that result in productive refrigeration capacity on the associated refrigerated system.
Note on G6: Sally Blair: If: 01 does not equal "true" 05 = "INCOMPLETE" Else: 05 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## NRCI F.Refrig Spcs Undrslb Heat
Refrigerated Warehouse/Space Underslab Heating
01 |  | 02 | 03
Room ID/ Description |  | Compliance Method | Underslab Heating Compliance
Per NRCC | Fslab01_SpaceName | Fslab02_SlabHeatingType
As-built |  | Dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Method Dropdown
Using electric resistance with thermostatic control to be off during summer on-peak time periods.
NA: not using electric resistance heat for underslab heating
NA: no underslab heating
Note on F7: 10/7/22 If: 02 is not complete 03 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 02 per NRCC match 02 as-built 03 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: 02 per NRCC do not match 02 as-built 03 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## NRCI F. Comm Refrigeration
Condensers Serving Commercial Refrigeration System
The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
The project includes replacement condensers that meet the following conditions: - attached compressor system Total Heat of Rejection does not increase and; - less than 25 percent of both the attached compressors and the attached display cases are new. | [7 empty] | << triggers if NRCC/LMCC-PRC Table G Condensers 01 is checked
All equipment, appliances and components serving the refrigeration system have been certified by the Energy Commission as compliant with Title 20 and listed in the Modernized Appliance Efficiency Database System found at https://cacertappliances.energy.ca.gov/Pages/Search/AdvancedSearch.aspx. | [7 empty] | << triggers if NRCC/LMCC-PRC Table G Condensers 02 is checked
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | << triggers if BOTH NRCC/LMCC-PRC Table G Condensers 01 AND 02 are NOT checked
Name or Item Tag |  | Condenser Type | Variable Speed Control | Temp Setpoint Controls | Specific Efficiency (Btuh/W) | Fin Density | Condenser Compliance
Per NRCC | Gcon03_ComponentName | Gcon04_CondenserType | Gcon05_VariableSpeedControl | Gcon06_CondenserTempControls | Gcon09_CondenserEfficiency Gcon09_NotApplicableMessage | Gcon10_CondenserFins Gcon10_NotApplicableMessage
As-built |  | dropdown | dropdown | dropdown |  | dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  | Condenser Type Dropdown | VS Dropdown | Temp Setpoint Dropdown |  | Fin Density dropdown
|  | Air Cooled | Variable speed fan(s) provided | Air cooled: designed to <= 70 @ ambient db temp |  | <= 10 fins/in
|  | Evaporative Cooled |  | Evap cooled: designed to <= 70 @ ambient wb temp |  | NA: Using microchannel condenser
|  | Adiabatic |  | Adiabatic: designed to < 70 @ ambient db temp |  | NA: Existing condenser being reused
NA: Adiabatic in Climate Zone 16
NA: Transcritical CO2 refrigeration
Compressors and Condensing Units Serving Commercial Refrigeration System
01 |  | 02 |  |  |  | 03 | 04
Name or Item Tag |  | Saturation suction temperature control (SST) |  |  |  | Transcritical CO2 Min Condensing Temp. | Condenser Compliance
Per NRCC | Gcom02_ComponentName | Gcom03_CompressorTempControls
As-built |  | Dropdown |  |  |  | dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  | Saturation Suction Temperature Control |  |  |  | Condensing Temp Dropdown
|  | Floating suction pressure logic used to reset target SST |  |  |  | Min condensing temp <=60 deg
|  | NA: Single compressor system with no variable capacity capability |  |  |  | SST < 30deg: Min condensing temp <= 70 deg
|  | NA: Suction group with design SST >= 30°F |  |  |  | NA: Not Transcritical CO2
NA: Suction group comprises of the high stage of a two-stage or a cascade system
NA: Suction group serves the secondary cooling fluid chiller
Refrigerated Display Cases
01 | [5 empty] | 02
Lighting Controls for Refrigerated Display Cases & Illuminated Glass Doors of Walk-in Coolers/ Freezers | [5 empty] | Refrigerated Display Case Compliance
Per NRCC | Gcase02_RefrigCaseTimer
Gcase03_RefrigCaseSensor
As-built | o | Timeclock: Turn off lighting power automatically during non-business hours
| o | Motion Sensor: Reduce lighting power by at least 50% within 30 minutes after the nearby area is vacated
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Lighting Control checkboxes
Timeclock: Turn off lighting power automatically during non-business hours
Motion Sensor: Reduce lighting power by at least 50% within 30 minutes after the nearby area is vacated
Heat Recovery of Refrigeration System
Per NRCC | Gheat02_HeatRecoveryMethod Gheat02_NotApplicableMessage
As-built
Method Dropdown
Heat recovery provided using 25% or more of Total Heat of Rejection and will not increase HFC refrigerant charge more than 0.35 lb/kBtuh of heat recovery heating capacity per §120.6(b)4
NA: No individual refrigeration systems > 150kBtuh
NA: Located in CZ 15
NA: Stores where the design Total Heat of Rejection of all refrigeration systems is less than or equal to 500,000 Btu/h.
Transcritical CO2 Fan-powered Gas Coolers
01 |  | 02 | 03 | 04 | 05 | 06
Name or Item Tag |  | Variable Speed Control | Gas Cooler Pressure Controls | Design Condensing Temperatures | Efficiency (Btuh/W) | Compliance
Per NRCC |  | Variable speed fan(s) provided controlled per §120.6(b)5D | Condensing temp reset per §120.6(b)1A and cooler pressure setpoint maximizes efficiency
As-built |  |  |  | Dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Design Temp dropdown
Min condensing temp <=60 deg
Transcritical CO2 w SST < 30deg: Min condensing temp <= 70 deg
Mandatory Pipe Insulation All Occupancies
1 |  | 2 |  |  |  | 3
System Name |  | Pipe Insulation Applications |  |  |  | Pipe Insulation Protection
Per NRCC |  | For systems serving nonresidential spaces, pipe insulation for the following applications is specified to comply with Table 120.3-A1 or or Table 120.3-A2 (see below) - Recirculating system piping, including supply and return piping of the water heater - The first 8 ft of hot and cold outlet piping, including between storage tank and heat trap, for a nonrecirculating storage system - Pipes that are externally heated |  |  |  | Pipe and appurtenance insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Protection shall include: - Insulation exposed to weather shall be installed with a cover suitable for outdoor service - Pipe insulation buried below grade must be installed in a water proof and non-crushable casing or sleeve. - Pipe insulation covering chilled water piping and refrigerant suction piping located outside the conditioned space shall include, or be protected by, a Class I or Class II vapor retarder. All penetrations and joints shall be sealed.
As-built
Note on H10: 10/7/22 If: All fields not grey are not complete 07 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 02-06 per NRCC match 02-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 02 per NRCC does not match 02 as-built OR 05 per NRCC > 05 as-built 07 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" Else: 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on H26: 10/7/22 If: 02-03 is not complete 04 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 02-03 per NRCC match 02-03 as-built 04 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else : 04 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on G42: 10/7/22 If: 01 are not complete if not grey 02 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 01 per NRCC match 01 as-built 02 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else : 02 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on C70: Sally Blair: This & column 03 are just static text in this table.
Note on G70: 10/7/22 IF all fields aren't complete, this says "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else If: column 05 as-built < column 05 Per NRCC, this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" Else If: columns 04-05 as-built match columns 04-05 NRCC, THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: column 05as-built >= column 05 Per NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"

## F. Parking Garage Exhaust
|  |  | From NRCC |  | user Input | Calculated
Enclosed Parking Garage Exhaust Controls
| Per C of C | As-built | Exceptions
01 | ¨ | ¨ | Garage is expected to have vehicles with non-gasoline combustion engines for > 20% of the parked vehicles per Exception 1 to §120.6(c)
02 | ¨ | ¨ | Project scope includes an addition or alteration to an existing garage where < 10,000 cfm of new exhaust capacity is being added Exception 2 to §120.6(c)
Requirements
03 | ¨ | ¨ | Exhaust fan control modulates airflow rates <= 50% design capacity when contaminant levels are maintained per §120.6(c)1
04 | ¨ | ¨ | Fan control or device allows fan motor demand ≤ 30% design wattages at 50% of design airflow per §120.6(c)2
05 | ¨ | ¨ | Design includes monitoring CO with a sensor density >= 1 per 5,000 ft2 per §120.6(c)3
06 | ¨ | ¨ | CO sensors are located in the highest expected concentration locations, with at least two per proximity zone per §120.6(c)3
07 | ¨ | ¨ | Design CO sensor setpoint <= 25 ppm per §120.6(c)4
08 | ¨ | ¨ | Occupied garage design maintains negative pressurization per §120.6(c)6
09 | ¨ | ¨ | Designed occupied total ventilation rate >= 0.15 CFM/ ft2 §120.6(c)5
CO Sensors shall be:
A. Certified by the manufacturer to be accurate within plus or minus 5% of measurement. B. Factory calibrated C. Certified by the manufacturer to drift no more than 5% per year. D. Certified by the manufacturer to require calibration no more frequently than once a year. E. Monitored by a control system. The system shall have logic that automatically checks for sensor failure by the following means. Upon detection of a failure, the system shall reset to design ventilation rates and transmit an alarm to the facility operators. i. If any sensor has not been calibrated according to the manufacturer's recommendations within the specified calibration period, the sensor has failed. ii. During unoccupied periods the system compares the readings of all sensors, e.g., if any sensor is more than 15 ppm above or below the average of all sensors for longer than 4 hrs, the sensor has failed. iii. During unoccupied periods the system compares the readings of sensor in the same proximity zone, e.g. if the 30 minute rolling average for any sensor in a proximity zone is more than 15 ppm above or below the 30 minute rolling average for other sensor(s) in that proximity zone, the sensor has failed.
Enclosed Parking Garage Exhaust
01 |  | 02 | 03 | 04
Fan Name or Item Tag |  | Parking Garage Area (ft2) | Ventilation Fan Rate (CFM) | Exhaust Compliance
Per C of C | H10_FanName | H11_ParkingGarageArea | H12_FanFlowCapacity
As-built
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Note on C5: 7/27/21 If selected, the as-built rows for Exhuast 03-09 and 02-03 as-built exhuast table gray out - Compliance Logic is equal or better in this case
Note on C6: 7/27/21 If selected, the as-built rows for Exhuast 03-09 and 02-03 as-built exhuast table gray out - Compliance Logic is equal or better in this case
Note on A16: 4.12.22 This new fied is just static text for the report.
Note on E21: 10/7/22 If: 02-03 or Controls sub-table are not complete 04 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 02-03 and controls per NRCC match 02-03 and controls as-built 04 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else if: 03 as-built >= (02 as-built x 0.15) OR controls per NRCC don't match per controls as-built 04 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 04 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## NRCI F. Process Boilers
|  |  |  | From NRCC |  |  | user Input | Calculated
Process Boilers
01 |  | 02 | 03 | 04 | 05 | 06 | 07
Name or Item Tag |  | Model # | Rated Input Capacity per Boiler (Btu/h) | Fan Controls | Combustion Air Shutoff | Stack Design and Controls | Process Boiler Compliance
Per NRCC | I01_BoilerName | Always Gray | I02_ProcessBoilerInputRange | I04_BoilerFanControl | I03_CombustionAirShutOff I04_NotApplicableMessage | I05_BoilerStackControl I05_NotApplicableMessage
As-built |  |  | Dropdown | Dropdown | Dropdown | Dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  |  | Input Capacity | Fan Control | Combustion Air Shutoff | Control Type
|  |  | < 2.5 MMBtuh per boiler | Variable speed drive provided | Combustion air positive shut-off provided | Designed and controlled per §120.6(d)
|  |  | >= 2.5 to <5 MMBtuh per boiler | Controls limit fan motor demand to <= 30% of the total design wattage at 50% of design air volume provided | NA: combined rated input of all boilers per stack < 2.5 MMBtuh | NA: Steady state full-load combustion efficiency >= 90%
|  |  | >= 5 MMBtuh per boiler | NA: Combustion air fan < 10 HP
Note on H7: 10/7/22 If: 02-06 fields are not complete if not grey 07 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 03-06 per NRCC match 03-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## NRCI F. Compressed Air
Compressed Air Systems
01 |  | 02 | 03 | 04 | 05 | 06 | 07
System Name/ Description |  | Model # | Trim Compressor | Controls | Monitoring | Service Line Size1 | Compressed Air Compliance
Per NRCC | J01_SystemDescription | Always Gray | J02_CompressorTrimMethod | J03_CompressorControls | J04_CompressorMonitoring
As-built |  |  | Dropdown | Dropdown | Dropdown | Dropdown
1 FOOTNOTE: Service line piping are pipes that deliver compressed air from distribution piping to end uses.
2 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  |  | Trim Compressor Dropdown | Controls Dropdown | Monitoring Dropdown | Line Size Dropdown
|  |  | Variable Speed Drive Compressor provided | Design includes sensor/controllor capable of using most efficient combination of compressors to meet load | Includes monitoring, data logging/storage and display system for pressure, amps/power, airflow per §120.6(e)3. | Inner diameter >= 3/4 in
|  |  | Dedicated trim compressor provided | NA: Do not have > 3 compressors | NA: < 100 combined HP rating | NA: Adjoining length <= 50ft
|  |  | NA: Medical gas serving Healthcare facility | NA: < 100 combined HP rating
|  |  | NA: Alt. where total added/replaced compressor hp < avg. per compressor hp of all compressors in system | NA: Medical gas serving Healthcare facility
NA: Alt. where added/replaced compressors are VSD & system includes primary storage >= 1g/acfm of largest trim compressor
NA: Alt. of system that includes >= 1 centrifugal compressor
Note on H6: 10/7/22 If: 02-06 fields are not complete if not grey 07 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED2" Else if: 03-06 per NRCC match 03-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## F. Elevators
|  |  | From NRCC |  |  | user Input | Calculated
Elevator Lighting and Ventilation
Lighting
01 |  | 02 | 03 | 04 | 05 | 06
Elevator Name or Item Tag |  | Fixture Name or Item Tag | Number of Fixtures | Watts per Fixture | Total Power | Elevator Lighting Compliance
Per C of C | K01_ComponentName | K03_LuminaireName | K05_LuminaireCountByType | K04_LuminairePower | K06_LuminairePowerByType
As-built Conditions |  |  |  |  | equals 03 x 04
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Ventilation
07 |  | 08 | 09 | 10 | 11 | 12
Name or Item Tag |  | Fan Power (Watts) | Airflow (CFM) | Watts per CFM | Controls | Elevator Ventilation Compliance
Per C of C | K09_ComponentName | K11_ElevatorFanPower K11_NotApplicableMessage | K12_FanDeviceFlow K12_NotApplicableMessage | K13_FanPowerPerFlow K13_NotApplicableMessage | K15_OccupancySensorControl K15_NotApplicableMessage
As-built |  |  |  | equals 08/09 | Dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Controls
Occupancy sensors provided
Note on G8: 10/7/22 If: All required Elevator Lighting fields are not complete 06 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 03-05 per NRCC match 03-05 as-built 06 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else if: 03-04 per NRCC do not match 03-04 as-built AND 05 per NRCC >= 05 as-built 06 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 06 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"
Note on G16: 10/7/22 If: 08-11 fields are not complete if not grey 12 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else if: 08-11 per NRCC match 08-11 as-built 12 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else if: 10as-built <= 0.33 12 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 12 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## NRCI F. Escalators
Escalators and Moving Walkway Speed Controls
The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
Escalators and moving walkways located in airports, hotels, and transportation function areas shall automatically slow to the minimum permitted speed in accordance with ASME A17.1/CSA B44 when not conveying passengers. | << triggers if compliance method from L.01 from NRCC-PRC is selected (Not the NA: method)
Note on A3: Sally Blair: Triggers if Controls selected in Table B.

## NRCI F. Computer Room
|  | From NRCC | [6 empty] | user Input | Calculated
Computer Room Systems
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Computer Room Name/ID |  | Economizer | Reheat Controls | Humidification | Sensible Cooling Capacity (kBtuh) | Total Fan System Power (Watts) | Fan Controls | Containment | Computer Room Compliance
Per NRCC | M01_SpaceName | M02_ComputerRmEconomizer | M03_ComputerRmReheat | M04_ComputerRmHumidification | M05_FanSystemSensibleCooling | M06_FanPowerPerCooling | M08_ComputerRmFanControl | M09_ComputerRmAirBarrier
As-built |  | Dropdown | Dropdown | Dropdown |  |  | Dropdown | Dropdown
|  | Economizer Compliance Method | Reheat Dropdown | Humidification |  |  | Fan Controls | Containment
|  | NEW CONSTRUCTION: Integrated air economizer designed to partial cooling and provide 100% of cooling load @ OSA 65deg db and below 50deg wb and below & includes FDD per §120.2(i) | Zone controls provided to prevent reheat | None Provided |  |  | Variable airflow controls/ devices provided per §120.6(j)3 | Air barrier provided per §140.9(a) 3
|  | NEW CONSTRUCTION: Integrated water economizer designed to partial cooling and provide 100% of cooling load @ OSA 50deg db and 45deg wb and below |  | Adiabatic system (non-adiabatic not allowed) |  |  | NA: Not Unitary AC System > 60kBtuh or CHW Fan System | NA: Not air-cooled computers where ITE process design load > 10 kW per room
|  | ADDITION/ALTERATION: Integrated air economizer designed to partial cooling and provide 100% of cooling load @ OSA 55deg db and below 50deg wb and below & includes FDD per §120.2(i) | [5 empty] | NA: Expansion of existing computer rooms
|  | ADDITION/ALTERATION: Integrated water economizer designed to partial cooling and provide 100% of cooling load @ OSA 40deg db and 35deg wb and below | [5 empty] | NA: Computer racks with a design load less than 1 kW/rack
|  | NA: Computer room w/ITE design load < 5 tons & building HVAC does not have any existing economizers per Exception 1 to 140.9(a)1 or Exception 1 to 141.1(b)1 | [5 empty] | NA: Equivalent energy performance based on computational fluid dynamics or other analysis.
|  | NA: New cooling systems in existing building with ITE design load <=50 tons per Exception 2 to 141.1(b)1 serving an existing computer room in an existing building up to a total of 50 tons of new cooling equipment per building | [5 empty] | NA: Rm power density <= 20 W/ft2
NA: New cooling systems serving a new computer room in an existing building up to a total of 20 tons of new cooling equipment per building per Exception 3 to 141.1(b)1.
NA: A computer room being served by a fan system (not economizer) meeting the requirements of Exception 2 to §140.9(a)1. ITE design load <20 tons and served by economizer meeting Exception 2 to 140.9(a)1
NA: Rm power density <= 20 W/ft2
THIS ENTIRE SUBTABLE IS NEW FOR 2022
Computer Room Uniterruptible Power Supply (UPS)
01 |  | 02 | 03 | 04 | 05 | 06
Computer Room Name/ID |  | Alternating Current Output UPS Compliance Method | Type of UPS | UPS Rated Output Power (W) | Efficiency | Compliance
Per NRCC | bar: 02 to 06
As-built |  | 02: Dropdown; 03: Dropdown
|  | UPS Compliance Method | Type Dropdown
|  | Systems meet or exceed min efficiency per Table 140.9-B | Voltage & Frequency Dependent
|  | NA: Rm power density <= 20 W/ft2 | Voltage Independent
|  | NA: UPS utilizes standardized NEMA 1-15P or NEMA 5-15P input plug | Voltage & Frequency Independent
Note on J7: 4.20.21 If: 02-08 fields are not complete if not grey 09 = "INCOMPLETE" Else if: 02-08 per NRCC match 02-08 as-built 09 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 06 as-built <= (05 as-built x 27) 09 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 09 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"
Note on G26: 4.12.22 If: 02-05 fields are not complete if not grey 06 = "INCOMPLETE" Else if: 02-05 per NRCC match 02-05 as-built 06 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 04 as built <= 04 per NRCC and 05 as-built >= 05 per NRCC AND 03 per NRCC matches 03 as-built 06 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 06 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## F. Kitchen
|  | From NRCC |  | user Input |  |  |  |  | Calculated
Commercial Kitchen Exhaust & Ventilation
Kitchen Ventilation
The following ventilation requirements have been included on the permitted Certificate of Compliance to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
Providing replacement air directly to the hood(s) that does not exceed 10% of the hood(s) exhaust rate. | [7 empty] | << triggers if selected in N02 from NRCC/LMCC-PRC
Not providing replacement air directly to the hood(s). | [7 empty] | << triggers if selected in N02 from NRCC/LMCC-PRC
Mechanically cooled or heated makeup air delivered to any space with a kitchen hood does not exceed the supply flow required to meet the space heating and cooling load. | [7 empty] | << triggers if selected in N03 from NRCC/LMCC-PRC
Mechanically cooled or heated makeup air delivered to any space with a kitchen hood does not exceed the hood exhaust flow minus the available transfer air from adjacent spaces. | [7 empty] | << triggers if selected in N03 from NRCC/LMCC-PRC
The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and at least 50% of all replacement air is transferred air that would otherwise be exhausted. | [7 empty] | << triggers if selected in N05 from NRCC/LMCC-PRC
The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and demand ventilation system(s) on at least 75% of the exhaust air. | [7 empty] | << triggers if selected in N05 from NRCC/LMCC-PRC
The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and listed energy recovery devices with a sensible heat recovery effectiveness of > 40 on at least 50% of the total exhaust airflow. | [7 empty] | << triggers if selected in N05 from NRCC/LMCC-PRC
The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and a minimum of 75% of makeup air volume having a total of no more than 60°F and uncooled or cooled without the use of mechanical cooling. | [7 empty] | << triggers if selected in N05 from NRCC/LMCC-PRC
Kitchen Hood
01 |  | 02 | 03 | 04 | 05 | 06 | 07
Name or Item Tag |  | Hood Type | Hood Style | Equipment Duty | Hood Length (ft) | Hood Exhaust Rate (CFM) | Kitchen Exhaust Compliance
Per C of C | Ne02_ComponentName | Ne03_KitchenHoodType | Ne04_KitchenExhaustHoodStyle | Ne06_KitchenExhaustHoodDuty Ne06_NotApplicableMessage | Ne05_KitchenExhaustHoodLength Ne05_NotApplicableMessage | Ne07_KitchenExhaustHoodFlow
As-built |  | Dropdown | Dropdown | Dropdown
|  | Hood Type | Hood Style | Equipment Duty
|  | Type I | Wall-mounted Canopy | Light Duty
|  | Type II | Single Island | Medium Duty
|  |  | Double Island | Heavy Duty
|  |  | Eyebrow | Extra Heavy Duty
Backshelf / Passover
Electric Ready Commercial Kitchens
1 |  | 2 |  |  |  | 3
System Name |  | Dedicated Branch Wiring |  |  |  | Electrical Panel Sizing
Per NRCC |  | Includes a dedicated branch circuit wiring and outlet accessible to cookline appliances and meets the following requirements: a) The branch circuit conductors shall be rated at 50 amps minimum. b) The electrical service panel shall have a minimum capacity of 800 connected amps. |  |  |  | The electrical service panel shall be sized to accommodate an additional either 208v or 240v 50-amp breaker.
As-built
Note on H20: 3.9.22 If: 02-06 fields are not complete if not grey 07 = "INCOMPLETE" Else if: 02-06 per NRCC match 02-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else if: 02-04 per NRCC match 02-04 as-built AND 05 per NRCC >= 05 as-built AND 06 per NRCC >= 06 as-built 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else if: 03 per NRCC does not match 03 as-built OR 04 per NRCC does not match 04 as-built 07 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## NRCI F.Lab Factory
O. LABORATORY AND FACTORY EXHAUST AND FUME HOODS
01 | 02 | [5 empty] | 03 | 04 | 05 | 06 | 7
Zone/System or Item Tag | Airflow Reduction | [5 empty] | Transfer Air | Exhaust Fan Power | Hood Sash Closure | Reheat Limitation | Exhaust Air Heat Recovery
Per NRCC
As-built | Dropdown | [5 empty] | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
| Airflow Reduction Method Dropdown | [5 empty] | Transfer Air Method Dropdown | Fan Power Upper Dropdown | Hood Sash Dropdown | Reheat Limitation Dropdown | EAHR Dropdown
| Exhaust airflow capable of reducing exhaust and make-up air to occupied and unoccupied min exhaust airflow rates per §140.9(c)1 circulation/pressurization rate | [5 empty] | Conditioned supply air delivered to any space with mechanical exhaust is designed per §140.4(o) | System meets discharge requirements in ANSI Z9.5-20192022 Section 6.4 | Hood sash closure system design controlled per §140.9(c)4 | Air handler shall not cool air < 80 °F nor heat >50 °F per §140.9(c)5 | System includes sensible energy recovery (heat ≥45%/cool ≥25%); recovered heat ≥75% w/ability to disable; pressure drop ≤0.4"w.g.
| NA: Constant volume system required by AHJ or Environmental, Health & Safety | [5 empty] | NA: Laboratory is classified as biosafety level >= 3 | NA: Newly installed exhaust system <= 10,000 cfm | NA: Not VAV hood with vertical sashes in hood intensive lab | NA: < 20,000 cfm of lab exhaust | NA: < 10,000 cfm of lab exhaust
| NA: New zones on an existing constant volume system | [5 empty] | NA: Serving vivarium space |  |  | NA: Air Handler does not serve multiple laboratory zones | NA: Addition/alteration to existing system without exhaust air heat recovery
| NA: Systems designed for > 10 ACH | [5 empty] | NA: Space required to be at positive pressure |  |  | NA: Add/alt to existing AH serving zones with no heat/cool capacity per Exception 1 to 140.9(c)5 | NA: Total lab exhaust rate > 20 cfm/ft2 of roof area per Exception 2 to 140.9(c)6
[7 empty] | NA: Space required to be at negative pressure and where highest amount of transfer air used for make-up exceeds available transfer airflow rate |  |  | NA: Vivarium or space classified as biosafety level 3 or higher per Exception 3 to 140.9(c)5 | NA: CZ 6 or 7 where gas heating is allowed per Exception 3 to 140.9(c)6
[10 empty] | NA: Systems that meet dew point criteria, heat/cool at each zone, and do not cool per Exception 4 to 140.9(c)5 | NA: Exhaust air heat recovery & heat recovery chiller with >=40% heat recovery per Exception 4 to 140.9(c)6
NA: Exhaust system requiring wash down system per Exception 5 to 140.9(c)6
Fans
01 | 02 | 03 |  | 04 |  | 05
Name or Tag ID | Quantity | Fan Function | Compliance Pathway | Fan Electrical Input Power (kW) | Fan System Power (Watts/CFM) | System Compliance
Per C of C |  |  |  | this should be Allowance from NRCC
As-built Conditions |  | dropdown
O. Exhaust Systems 140.9(c)3D
This table includes all laboratory and factory exhaust and fume hoods within the scope of the permit application. The inputs within Table O are used to demonstrate compliance with the requirements within §140.9(c)3D.
01 | 04 |  | 05 |  | 06
Exhuast System Name or Item Tag | Exhaust Fan System Airflow (cfm) |  | Design Exhaust Fan System Power (watts) |  | Variable Speed Controls
Per C of C | From CC O04 |  | From CC O05 |  | From CC O06
As-built Conditions
Note on A18: Alexis Markstrum: Ben - double check this table has the appropriate information. Reference CEC comments. I added the fields from his comments
Note on E20: Alexis Markstrum: This is from CEC comments See their comments for direction
Note on G20: Alexis Markstrum: This is from CEC's comments. See their comments for direction
Note on D21: Alexis Markstrum: Ben - Not sure what field from the CC this is
Note on H21: 10/7/22 IF all fields aren't complete this says "INCOMPLETE" OR Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED2" IF column 04 as-built > column 04 NRCC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED C of C REVISED" OR If columns 02- 04 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" ELSE IF column 04 as-built <= column 04 NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED C of C"
Note on F22: Alexis Markstrum: See CEC comments on this
Note on A25: Alexis Markstrum: Ben - double check this table is correct Reference CEC comments

## NRCI F.CEH
THIS ENTIRE TABLE IS NEW FOR 2022
CONTROLLED ENVIRONMENT HORTICULTURE LIGHTING
01 |  | 02 | 03 | 04 | 05 | 06
Zone/System or Item Tag |  | Photosynthetic Photon Efficacy (PPE) | Timeswithch Lighting Controls | Multilevel Lighting Controls | Electrical System Monitoring | CEH Compliance
Per NRCC | O01_ComponentName |  |  |  | Electrical system capable of moning electrical energy usage of horticulture lighting load
As-built |  | Dropdown | Dropdown | Dropdown
|  | PPE Dropdown | Timeswitch | Multilevel
|  | System PPE ANSI/ASABE S640 rated for wavelengths 400-700 nanometers AND integrated, non-serviceable luminaire PPE >= 1.7 2.3 micromoles per joule | EMCS | Dimmer
|  | System PPE ANSI/ASABE S640 rated for wavelengths 400-700 nanometers AND serviceable lamp PPE >= 1.7 2.3 micromoles per joule | Autotimeswitch | Multilevel Switch
|  |  | Countdown timer | NA: System has < 40kW of aggregate horticulture lighting load
Space Conditioning for Plant Production
01 | 02 |  | 03
System Name/ Description | Dehumidification System for Indoor Grow CEH Compliance Method |  | CEH Compliance
Dropdown
Dehumid Compliance Method
Dehumidifiers regulated by Federal Appliance Standards
HVAC has onsite heat recovery for >=75% of dehumidification reheat
CHW system has onsite heat recovery for >=75% of dehumidification reheat
Dessicant dehumidification for dewpoint <= 50degF
NA: No dehumidification systems or greenhouse
NA: No Greenhouse
Greenhouse Envelope
01 |  | 02 | 03 | 04 | 05
Tag/Plan Detail ID |  | Assembly Type | Frame Type | Design U-factor | CEH Compliance
Per NRCC |  | From CC P02 | From CC P04 | From CC P06
As-built |  | Dropdown | Dropdown | Dropdown
Note on A3: 6/19/23 Required when CEC Lighting is checkd in Table B
Note on F6: Alexis Markstrum: I do not know these NRCC schema references
Note on G6: Sally Blair: Static text
Note on H6: 3.9.22 If: 02-04 fields are not complete if not grey 06 = "INCOMPLETE" Else if: 02-04 per NRCC match 02-04 as-built 06 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 06 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A14: 6/19/23 Required when CEH Space Conditioning is checked in Table B
Note on E18: 4.12.22 If: 02 fields are not complete if not grey 03 = "INCOMPLETE" Else if: 02 per NRCC match 02 as-built 03 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 03 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A31: 6/19/23 Required when CEC Lighting is checkd in Table B
Note on G34: 2/12/25 If: 03-04 fields are not complete if not grey this = "INCOMPLETE" Else if: 03-04 per NRCC match 03-04 as-built this = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: If 03cc == 03AsBuilt and 04cc>04AsBuilt this == Equal or Better Else this == May Not Comply

## NRCI F. Steam Trap
THIS ENTIRE TABLE IS NEW FOR 2022
STEAM TRAPS IN INDUSTRIAL FACILITIES
01 |  | 02 | 03 | 04
Fault Detection Diagnostics Monitoring |  |  | Strainer Installation | Steam Traps Compliance
Update Interval |  | Alarm Display
Per NRCC
As-built | Dropdown | Dropdown | Dropdown
| Interval Dropdown | Alarm Dropdown | Strainer Dropdown
| Status updates at <= 8 hr intervals | Alarm displays which steam trap has fault | Steam traps are equipped with an integral strainer and blow-off valve
| NA: Steam is diverted to a steam system of lower pressure for use when the steam trap fails open. | NA: Steam is diverted to a steam system of lower pressure for use when the steam trap fails open. | Steam traps are installed downstream within 3 ft of a strainer and blow-off valve
NA: Steam is diverted to a steam system of lower pressure for use when the steam trap fails open.
Note on D7: Alexis Markstrum: I do not know the NRCC schema references
Note on E7: 3.9.22 If: 01-03 fields are not complete if not grey 04 = "INCOMPLETE" Else if: 01-03 per NRCC match 02-06 as-built 04 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 04 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## F. PoolSpa
Removed for 2025
POOL & SPAS
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08
Pool/Spa Description |  | Efficiency | On/Off Control | Instructions & Covers | Electric Resistance Heating | Piping | Directional Inlets & Pump Control | Pool/Spa Compliance
Per C of C | R01_ComponentName | Equipment subject to State/federal appliance efficiency standards is in the CEC's directory of certified equipment | Includes on-off switch mounted on outside of heater allowing shutting off heater without adjusting thermostat
As-built |  |  |  | Dropdown | Dropdown | Dropdown | Dropdown
|  |  |  | Cover Dropdown | Elec Resistance Dropdown | Piping Dropdown | Inlet Dropdown
|  |  |  | Heated outdoor pools/spas must include cover and weatherproof instruction for proper care of when cover is used | No electric resistance heating used | >= 36 in of pipe installed between filter & heater or dedicated suction and return lines to allow for the future addition of solar heating equipment | Has directional inlets to mix the pool water & control mechanism to allow pumps to run only during off-peak electric demand period and for min time necessary
|  |  |  | NA: Pool/spa not heated | Listed package units with fully insulated enclosures, and with tight-fitting covers that are insulated to at least R-6 | Built-in/built-up connections installed to allow for future addition of solar heating equipment | NA: Spa only
Pools/spas where >= 60% of annual heating energy is from site solar energy or recovered energy
Additional Requirements for Pool/ Spa Serving One Tenant
All pump flow rates shall be calculated using H = C × F2 WHERE: H is the total system head in feet of water F is the flow rate in gallons per minute (gpm) C is a coefficient based on the volume of the pool (0.0167 for pools less than or equal to 17,000 gallons & 0.0082 for pools greater than 17,000 gallons)
Filtration pumps shall be sized, or if programmable, shall be programmed, so that the filtration flow rate is not greater than the rate needed to turn over the pool water volume in 6 hours or 36 gpm, whichever is greater.
Pump motors used for filtration shall meet the applicable federal standard in 10 CFR 431.465.
Each auxiliary pool load shall be served by either separate pumps or the system shall be served by a multispeed pump if pump hp >= 1. - Multispeed pumps shall have controls which default to the filtration flow rate when no auxiliary pool loads are operating; and - For multispeed pumps, the controls shall default to the filtration flow rate setting within 24 hours and shall have an override capability for servicing.
System Piping must meet the following requirements: - A length of straight pipe that is greater than or equal to at least 4 pipe diameters shall be installed before the pump; and - Pool piping shall be sized so that the velocity of the water at maximum flow for auxiliary pool loads does not exceed 8 feet per second in the return line and 6 feet per second in the suction line; and - All elbows shall be sweep elbows or of an elbow-type that has a pressure drop of less than the pressure drop of straight pipe with a length of 30 pipe diameters.
Filters shall be at least the size specified in NSF/ANSI 50 for public pool intended applications.
Minimum diameter of backwash valves shall be 2 inches or the diameter of the return pipe, whichever is greater.
Note on I6: 3.9.22 If: 04-07 fields are not complete if not grey 08 = "INCOMPLETE" Else if: 04-07 per C of C match 04-07 as-built 08 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else: 08 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## NRCA
G. Acceptance Tests and Field Verification
The following Acceptance Tests related to the systems or materials documented on this Certificate of Installation have been indicated on the permitted Certificate of Compliance as being required to comply with Title 24, Part 6. Process System Acceptance Tests are not required to be completed by a certified Acceptance Test Technician and may be completed by a field technician (which may be the installer). The Certificate of Acceptance forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
Form/Title | Systems to be Field Verified
NRCA-PRC-01-F Compressed Air Systems | Q01_SystemsToFieldVerify | Diane - It looks like there are two schema terms for the systems to be field verified? I made my best guess and used the concatenated list term here.
NRCA-PRC-02-F Kitchen Exhaust | Q02_SystemsToFieldVerify | < only trigger rows that are required by the project.
NRCA-PRC-03-F Garage Exhaust | Q03_SystemsToFieldVerify
NRCA-PRC-04-F Refrigerated Warehouses - Evaporator Fan Motor Controls | Q04_SystemsToFieldVerify
NRCA-PRC-05-F Refrigerated Warehouses - Evaporative Condenser Controls | Q05_SystemsToFieldVerify
NRCA-PRC-06-F-Refrigerated Warehouses - Air Cooled Condenser Controls | Q06_SystemsToFieldVerify
NRCA-PRC-16-F-Refrigerated Warehouses - Adiabatic Condenser Controls | Q07_SystemsToFieldVerify
NRCA-PRC-07-F-Refrigerated Warehouses - Variable Speed Compressor | Q08_SystemsToFieldVerify
NRCA-PRC-08-F Refrigerated Warehouses - Electric Resistance Underslab Heating System | Q09_SystemsToFieldVerify
NRCA-PRC-12-F Elevator Lighting & Ventilation Controls | Q10_SystemsToFieldVerify
NRCA-PRC-13-F Escalators & Moving Walkways Speed Controls | Q11_SystemsToFieldVerify
NRCA-PRC-14-F Lab Exhaust Ventilation Systems | Q12_SystemsToFieldVerify
NRCA-PRC-15-F Fume Hood Automatic Sash Closure Systems | Q13_SystemsToFieldVerify
NRCA-PRC-X-F Transcritical CO2 Refrigeration Systems
NRCA-PRC-X-F Steam Traps
There are no Acceptance Tests indicated on the permitted Certificate of Compliance related to the systems or materials documented on this Certificate of Installation. |  | << Excel row 17 is triggered if no other rows in this table are triggered.
A copy of this Certificate of Installation should be distributed to the Field Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A17: CEC, will there be a new NRCA form for Steam Traps? For transcritical CO2 systems?
Note on A20: Sally Blair: This is a static field that is always on this table.

## LMCA
G. Acceptance Tests and Field Verification
The following Acceptance Tests related to the systems or materials documented on this Certificate of Installation have been indicated on the permitted Certificate of Compliance as being required to comply with Title 24, Part 6. Process System Acceptance Tests are not required to be completed by a certified Acceptance Test Technician and may be completed by a field technician (which may be the installer). The Certificate of Acceptance forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
Form/Title | Systems to be Field Verified
NRCA-PRC-02-F Kitchen Exhaust | Q02_SystemsToFieldVerify | < only trigger rows that are required by the project.
NRCA-PRC-03-F Garage Exhaust | Q03_SystemsToFieldVerify
NRCA-PRC-12-F Elevator Lighting & Ventilation Controls | Q10_SystemsToFieldVerify
There are no Acceptance Tests indicated on the permitted Certificate of Compliance related to the systems or materials documented on this Certificate of Installation. |  | << Excel row 17 is triggered if no other rows in this table are triggered.
A copy of this Certificate of Installation should be distributed to the Field Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A8: Sally Blair: This is a static field that is always on this table.