## Change Log
Date | Table | Description of Change | Cell Color/Text Color
2025-03-10 | F. Allocated Zone | Added new columns 4-6 | yellow/red
2025-03-10 | F. PV | Added checkbox row for JA11 | yellow/red
2025-03-10 | F. Battery | Added checkbox row for JA12 | yellow/red
2025-03-10 | F. Battery | Revised columns 03 and 04, removed Column 06 | yellow/red
2025-03-10 | F. Battery | Column 07 changed to "Rated Single Charge-Discharge AC Efficiency" | yellow/red
2025-03-10 | F. ST and AEM | Revised static text | yellow/red

## NRCI Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | NRCI-SAB-E
This Certificate of Installation documents the installation of solar and battery features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | NRCI-SAB-E
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator

## LMCI Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | LMCI-SAB-E
This Certificate of Installation documents the installation of solar and battery features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for low-rise multifamily and low-rise mixed-use occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | LMCI-SAB-E
Project Name: | comes from LMCC | Report Page: | comes from report generator
Project Address: | comes from LMCC | Date Prepared: | comes from report generator

## Table A. General
A. GENERAL INFORMATION
01 | Project Location (city): | A01_ProjectCity | 05 | Authority Having Jurisdiction:
02 | Zip Code: | A02_Zipcode | 06 | Building Permit #:
03 | Date of Permit Set used for construction: |  | 07 | Date of As-built Set:
04 | Name of Permit Set used for construction: |  | 08 | Name of As-built Set:

## Table B. Scope
B. INSTALLER SCOPE
This table indicates construction systems and materials documented on this Certificate of Installation.
01
□ | Allocated Solar Zone | □ | Photovoltaics | □ | Solar Water Heater | □ | Smart Thermostat
□ | Home Automation System | □ | Greywater Irrigation | □ | Rainwater Catchment System | □ | Electric Vehicle Charging Space
□ | Energy Star Dishwasher and Energy Star Refrigerator | □ | Energy Star Dishwasher F w/Electronically Communicated Mower | □ | Battery Storage System
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing smart thermostat vs. Rainwater Catchment System, this will show what is being documented.

## Table C. Compliance
C. COMPLIANCE RESULTS
This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance. If the installation is not equal or better, Section 10-103(a)2B requires the Certificate of Compliance form to be revised accordingly to demonstrate compliance.
01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE
Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply.
The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly.
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Note on B4: 10/7/22 -IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INCOMPLETE", this says "FORM NOT COMPLETE" OR - IF cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" OR - IF ALL assemblies/equipment compliance columns in ALL subtables triggered say "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE", that is what is shown here. OR - IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED", that is what is shown here. ELSE - this field says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A5: Sally Blair: Excel Row 5 triggered if "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE" OR "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" is triggered in 01.
Note on A6: Sally Blair: Excel Row 6 triggered if "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" is triggered in 01.

## Table D Exceptional Conditions
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact requirements documented on the Certificate of Compliance.
Remarks below are triggered from other tables in the NRCI/LMCI Form and are not editable by the user.
No exceptional condition notes for NRCI/LMCI SRA

## Table E. Notes
E. INSTALLER NOTES
This table includes remarks made by the installer to the Authority Having Jurisdiction.

## Table F. Install Details
F. INSTALLATION DETAILS
The following tables indicate performance requirements as documented on the permitted Certificate of Compliance for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.
After this table heading, the appropriate Table F "Subtables" from the other tabs would appear based on what scope the installer is completing the form for.
Example, if they are completing the form for installing a solar PV system, subtable on the "F.PV" tab would appear here.

## F. Allocated Zone
[7 empty] | From NRCC | user Input | Calculated
Allocated Solar Zone on Roof for Future Use
01 |  | 02 | 03 | 04 | 05 | 06 | 04 07
Subarea Name |  | Building Plan Reference Showing Solar Zone | Solar Zone Free from Obstructions?1 | Location reserved for inverters and metering and a pathway reserved for routing of conduit from solar zone to point of interconnection? | Main electrical service panel has a minimum busbar rating of 200 amps? | Main electrical service panel has a reserved space for the installation of a circuit breaker for future solar electric installation that is labeled? | Solar Zone Compliance
Per C of C | F09_SolarZoneSubAreaID | F10_BuildingPlanName | F14_IsSolarZoneSubAreaObstructionsFree | dropdown | dropdown | dropdown
As-built Conditions |  |  | dropdown
1 FOOTNOTE: No obstructions, including but not limited to, vents, chimneys, architectural features, and roof mounted equipment, shall be located in the solar zone.
2 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
|  |  | Solar Zone Free of Obstructions dropdown | Interconnection pathways | Electrical panel rating | Electrical panel reserved and labeled
|  |  | Yes | Yes | Yes | Yes
Note on H8: 10/7/22 If: All fields are not complete 04 07= "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED2" Else if: 03 per NRCC match 03 as-built 04 07= "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C"

## F. PV
|  | From NRCC | [8 empty] | user Input | Calculated
Permanently Installed Solar Photovoltaic (PV) System
¨ | The system meets the installation requirements of Joint Appendix JA11.
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
PV Array ID or Name |  | Installed DC Power Rating (kW) | Module Type | Azimuth (deg) | Tilt Input (deg/pitch) | Angle/Tilt | Annual Solar Access (%) | Inverter Efficiency (%) | Array Type | Module Level Power Electronics
As-built Conditions
As-built Conditions
11 | Total As-built DC System Size (kW) | 04: 12; 05: Total DC System Size per C of C (kW); 08: 13; 09: PV Compliance
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Note on A9: 4.26.22: There is no Per C of C row in this table because this info isn't on the CC. If there is more than one Array, the As-built Conditions row will need to be duplicated for the second, third, etc. array. This is what it would look like.
Note on H10: 4.26.22: Use CC-SAB Table C col 04 for this field, but that is in Watts & this is in kW, so need to divide by 1000. Not sure the value from the CC-PRF and if it needs to be converted?
Note on K10: 10/7/22 If: All fields are not complete 13 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else If: 11 = 12 13 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: 11 > 12 13 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 11 < 12 13 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## F. Battery
|  |  | From NRCC | [6 empty] | user Input | Calculated
Battery Energy Storage System
¨ | The system meets the installation requirements of Joint Appendix JA12.
01 |  | 02 | 03 | 04 | 05 | 06 | 07 06 | 08 07 | 09 08
Manufacturer |  | Model # | Rated Usable Energy Capacity of BESS Battery (kWh) | Rated Power Capacity of BESS Battery (kWdc) | Control | Charging Efficiency (%) | Discharging Efficiency (%) Rated Single Charge-Discharge AC Efficiency | Battery System Certified by CEC? | Battery Compliance
Per C of C | NA | bar: 02 to 09 08
As-built Conditions |  | 08 07: Yes/No
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
Note on D8: 3.10.22: schema reference is NRCC-SAB Jtotal Energy (kWh) Capacity in Design OR LMCC-SAB J08.
Note on E8: 3.10.22: Schema referece is NRCC-SAB Jtotal Power (kW) Capacity in Design. This is not applicable to LMCC, so would be blank/grey.
Note on J8: 10/7/22 If: All fields are not complete if not grey 09 08 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else If: 03-04, 06 CofC = 03-04, 06 as-built 09 08= "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: 03-04, 06 CofC < 03-04, 06 as-built 09 08= "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 03-04, 06 CofC > 03-04, 06 as-built 09 08="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## F. SWH
[7 empty] | user Input | Calculated
Permanently Installed Solar Hot Water System
01 |  | 02 | 03 | 04 | 05 | 06
SRCC # or IAPMO File # |  | Certification Number | System Type | Solar Savings Fraction | Drainwater Heat Recovery | SHW Compliance
Per C of C | H01_SolarWaterHeatingCertificationAuthority | H02_SolarWaterSystemSRCC_CertificationNumber H02_SolarWaterSystemIAPMO_FileNumber | The SWH system is built-up and specifies collectors certified by the Solar Rating & Certification Company (SRCC) or the International Association of Plumbing & Mechanical Officials (IAPMO) as OG-100. | H03_SolarSavingsFractionOG100 H03_NotApplicableMessage H05_SolarSavingsFractionOG300 H05_NotApplicableMessage | H00c_IsDWHR_Installed
As-built Conditions | dropdown
1 The compliance tool used to document the Certificate of Compliance does not provide data to the Certificate of Installation. In these scenarios,certificate of installation compliance status will need to be determined manually by the AHJ.
SRCC # or IAPMO File # dropdown
SRCC #
IAPMO File #
OG-100 Certified Collectors Requirements
The installed system shall meet the following eligibility criteria:
- System is installed at the same orientation &tilt as modeled. - System shall have the same collectors, pumps, controls, storage tank and backup water heater fuel type as the rated condition. - The collectors are located in a position that is not shaded by adjacent buildings or trees. - Backup storage tanks are insulated with either an internal R-16 (labeled on tank) or external R-12. - All domestic hot water piping (including solar) shall be insulated.
Note on D7: 3.9.22 This is a static text field.
Note on F7: 3.9.22: If Drainwater heat recovery in NRCC/LMCC SAB Table H is true, the following static message populates here, otherwise this is blank and grey. "A drain water heat recovery system that is field verified by a HERS Rater as specified in the Title 24, Part 6 Reference Appendix RA3.6.9 is being used to lower the required Solar Savings Fraction and must be installed and HERS verified."
Note on G7: 10/7/22 If: All fields are not complete 06 = "INCOMPLETE" Else If: cc project data not available (no compliance ID) say "CC PROJECT DATA NOT AVAILABLE. COMPLIANCE CAN NOT BE AUTOMATICALLY DETERMINED1" Else If: 01-04 per NRCC match 01-04 as-built 06 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED C of C" Else If: 04 per NRCC <= 04 per as-built 06 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else if: 04 per NRCC > 04 per as-built 06 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"
Note on A16: 3.10.22: This is static text that shows up when this table is triggered. Note: this text came directly from CF2R-STH-01

## F. ST and AEM
|  |  | From NRCC | user Input | Calculated
Smart Thermostats and Additional Efficiency Measure in Multifamily Dwelling Units
The following requirements have been included on the permitted Certificate of Compliance to comply with Title 24, Part 6. Installations shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
All thermostats in each dwelling unit comply with the following requirements from Title 24, Part 6 §110.12(a) and all requirements in Joint Appendix 5: 1. All demand responsive controls shall be either: |  | << triggers if "Exception to Solar Ready Area: Smart Thermostat and Alternative Energy Efficiency Measure" true in NRCC/LMCC-SAB Table B
A. A certified OpenADR 2.0a or OpenADR 2.0b Virtual End Node (VEN), as specified under Clause 11, Conformance, in the applicable OpenADR 2.0 Specification; or a certified Baseline Profile Open ADR 3.0 Virtual End Node; or
B. Certified by the manufacturer to the Energy Commission as being capable of responding to a demand response signal from a certified OpenADR 2.0b or a certified Baseline Profile OpenADR 3.0 Virtual End Node by automatically implementing the control functions requested by the Virtual End Node for the equipment it controls.
2. All demand responsive controls shall be capable of communicating using one or more of the following: Wi-Fi, ZigBee, BACnet, Ethernet, or hard-wiring. 3. Demand responsive controls may incorporate and use additional protocols beyond those specified in Sections 110.12(a)1 and 2. 4. When communications are the demand response signal is disabled or unavailable, all demand responsive controls shall continue to perform all other control functions provided by the control.
Dwelling units include an ENERGY STAR dishwasher AND EITHER an ENERGY STAR refrigerator OR a whole house fan driven by an electronically commutated motor. |  | << triggers if "Energy Star Appliances and EC Motor" true in NRCC/LMCC-SAB Table I
Dwelling units include a home automation system that is capable of, at a minimum, controlling the appliances and lighting of the dwelling and responding to demand response signals. |  | << triggers if "Home Automation System" true in NRCC/LMCC-SAB Table I
Dwelling units include alternative plumbing piping to permit the discharge from the clothes washer and all showers and bathtubs to be used for an irrigation system in compliance with the California Plumbing Code and any applicable local ordinances. |  | << triggers if "Greywater Irrigation System" true in NRCC/LMCC-SAB Table I
Dwelling units include a rainwater catchment system designed to comply with the California Plumbing Code and any applicable local ordinances, and that uses rainwater flowing from at least 65% of the available roof area. |  | << triggers if "Rainwater Cachment System" true in NRCC/LMCC-SAB Table I
Project complies with Title 24, Part 11, §A4.106.8.2 requirements for electric vehicle charging spaces. |  | << triggers if "Part 11: Electric Vehicle Parking Space" true in NRCC/LMCC-SAB Table I