## Change Log
Date | Description of Change | Color
2022-09-20 | - There was a typo on the logic for 12_FanSystemPowerAllowance when System Zoning == DOAS <1.0 kW. - Fdoas05_RatingConditionDOAS should gray/blank in certain scenarios. This was not previously specified. It now is. | None
2022-09-22 | Added Exhaust System Base Allowance in Table H. | None
2022-10-17 | Removed the "-A" from the NRCA-MCH-04-A row in the NRCA table | red

## New Table Sequence
Label | Table Title | Trigger within:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | HVAC System Summary (Dry & Wet Systems) | Table B
Table G | Pumps | Table B
Table H | Fan Systems and Air Economizers | Table B
Table I | System Controls | Table B
Table J | Ventilation | Table B
Table K | Terminal Box Controls | Table B
Table L | Distribution (Ductwork & Piping) | Table B
Table M | Cooling Towers | Table B
Table N | Declaration of Required Certificates of Installation | ALWAYS
Table O | Declaration of Required Certificates of Acceptance | ALWAYS
Table P | Declaration of Required Certificates of Verification | ALWAYS
Table Q | Mandatory Measures Documentation Location | ALWAYS
| Signature Page | ALWAYS
Note on C17: 2019 Update: Added new NRCV table
Note on A18: 219 Update: Changed Table letter to Q.

## Hyperlinks
Section | Hyperlink
110.1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=99
110.12 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=134
110.2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=100
120.1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=138
120.2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=150
120.3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=155
120.4 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=158
120.9 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=175
140.4 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=212
140.4(e) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=215
110.2(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=100
110.2(b) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=100
110.2(d) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=101
110.2(e)1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=101
110.2(e)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=101
110.2(e)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=101
110.2(e)4 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=101
110.2(e)5 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=101
120.1(b)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=139
120.1(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=140
120.1(c)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=141
120.1(d)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=142
120.1(d)5 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=143
120.2(e) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=151
120.2(e)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=151
120.2(e)3B | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=151
120.2(g) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=152
120.3(b) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=155
120.3(c)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=155
120.4(a)-(f) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=158
140.3(a)1B | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=198
140.4(a&b) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=212
140.4(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=212
140.4(b) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=212
140.4(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=213
140.4(d) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=214
140.4(e) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=215
140.4(f) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=218
140.4(f) and (n) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=218
140.4(h)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=219
140.4(h)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=219
140.4(h)5 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=220
140.4(i) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=220
140.4(k) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=220
140.4(l) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=221
140.4(m) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=222
140.4(n) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=222
141.0(b)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=254
141.0(b)2E | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=258
Reference Nonresidential Appendix 2 (NA2) | https://www.energy.ca.gov/2018publications/CEC-400-2018-021/CEC-400-2018-021-CMF.pdf#page=357
Table 110.2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=102
Table 110.2-E | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=107
Table 140.4-B | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=214
Tbale 110.2-G | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=109
Title 20 | http://www.energy.ca.gov/appliances/database/
Table 120.3-A | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=155
130.1(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180

## LMCC Headers
| User input |  | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Mechanical Systems
LMCC-MCH-E |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-MCH-E
This document is used to demonstrate compliance for mechanical systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.0, §140.4, §170.2, §180.1 and §180.2 .
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  |  | Date Prepared:
The project name and date prepared is a user input on the first page, but will populate the heading on all other pages.
STATE OF CALIFORNIA
Mechanical Systems
NRCC-MCH-E (Created XX/XX) |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-MCH-E
Project Name: |  | Remove these fields from all but first page |  |  | Report Page: | Page 1 of ??
Project Address: |  | Remove these fields from all but first page |  |  | Date Prepared:
Footer on all pages:
CA Building Energy Efficiency Standards - 2022 Nonresidential & Multifamily Compliance: https://www.energy.ca.gov/programs-and-topics/programs/building-energy-efficiency-standards/2022-building-energy-efficiency
First Page Heading
Heading for all other pages
Note on A6: 2019 Update: Updated to remove "Table Instructions"
Note on B21: 2019 Update: Updated footer

## A. General Info (LMCC)
| User input |  | auto calculated |  |  | From another table |  |  |  |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 04 | Total Conditioned Floor Area
02 | Climate Zone |  |  | Dropdown |  | 05 | Total Unconditioned Floor Area
03 | Occupancy Types Within Project: |  |  |  |  | 06 | # of Stories (Habitable Above Grade)
• | Office | • | Retail | • | Warehouse | • | Hotel/Motel | • | School | • | Support Areas
• | Low-Rise Residential | • | Commercial | • | Healthcare Facility | • | Parking Garage | • | Theater | • | Sports Arena
• | Auditorium | • | Library | • | Relocatable School Building | • | Medical Clinic | • | Data Center | • | Convention Center
• | Classroom | • | Gymnasium | • | Grocery Store | • | Religious Facility | • | Financial Institution | • | All Others
• | Restaurant/Commercial Kitchen
CS Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16

## B. Project Scope
|  | User input |  |  | auto calculated |  | From another Table | From look up table
B. PROJECT SCOPE
[d:OnlyUI] Table Instructions: Include any mechanical systems that are within the scope of the permit application and are demonstrating compliance using the mandatory requirements in §110.2, §120.1, §120.2, §120.4, §120.5, §120.9 and prescriptive path outlined in §140.4, or §141.0(b)2 for alterations. [d:/OnlyUI] [d:OnlyRG] This table includes mechanical systems or components that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.4, 170.2(b) or §141.0(b)2 and 180.2(b)2 for alterations. [d:/OnlyRG]
My project consists of (check all that apply)
01 |  | 02 |  | 03
Air System(s) |  | Wet System Components |  | Dry System Components
¨ | Heating Air System | ¨ | Water Economizer | ¨ | Air Economizer | <<triggers Table H
¨ | Cooling Air System | ¨ | Pumps | ¨ | Electric Resistance Heat | << triggers "Electric Resistance" Section in Table F
Mechanical Controls |  | ¨ | System Piping | ¨ | Fan Systems | << triggers Table H
|  | ¨ | Cooling Towers | ¨ | Ductwork (existing to remain, altered or new) | << triggers "Ductwork" section in Table L
¨ | Mechanical Controls (existing to remain, altered or new) | ¨ | Chillers | ¨ | Ventilation | << triggers Table J.01-J.03 UNLESS "Healthcare" is the ONLY occupancy type checked in Table A column 03. If this is the case, trigger Alert below in row 15
|  | ¨ | Boilers | ¨ | Zonal Systems/ Terminal Boxes | << triggers Table K UNLESS "Healthcare" is the ONLY occupancy type checked in Table A column 03. If this is the case, trigger Alert below in row 16
ALERT! Healthcare facilities must be ventilated in accordance with Chapter 4 of the CMC as amended by OSHPD and do not need to show compliance with Title 24, Part 6 ventilation requirements in Table J.
ALERT! Healthcare facilities are not required to comply with space-conditioning zone controls from §140.4(d) and do not need to show compliance with the requirements in Table K.
Note on B9: Sally Blair/Gina: Triggers Controls Table I and Table F "Dry System Eq. Sizing"
Note on C9: Sally Blair: Triggers "Heat Rejection Eq." section in Table F.
Note on B10: Gina: Triggers Controls Table I and Table F "Dry System Eq. Sizing"
Note on C10: Sally Blair: Triggers Table G
Note on C11: Sally Blair: Triggers "Piping" Section in Table L
Note on F11: 3.25.22 When Fan Systems is selected, ventilation is automatically selected
Note on C12: Sally Blair: Triggers Table M & "Heat Rejection Eq." section in Table F.
Note on B13: Sally Blair/Gina: Triggers Controls Table I
Note on C13: Sally Blair: Triggers "Chiller Efficiency & Controls" section in Table F.
Note on F13: 3.25.22 When ventilation is selected, fan systems are automatically selected
Note on G13: 2019 Update: Exception for triggering Table J if Healthcare is checked in Table A was added.
Note on C14: Sally Blair: Triggers "Boiler Efficiency & Controls" section in Table F.
Note on G14: 2019 Update: Exception for triggering Table K if Healthcare is checked in Table A was added.
Note on A15: 2020 Clarification: Triggers when "Healthcare Facility" is checked in Table A AND "Ventilation" in Table B
Note on A16: 2020 Clarification: Triggers when "Healthcare Facility" is checked in Table A AND "Zonal Systems/Terminal Boxes" in Table B.

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Equipment in Table F indicates total heating output exceeds total heating load by more than 43%. Please explain the Exception to §140.4(a) used to oversize the heating equipment in Table E. Additional Remarks.
Equipment in Table F indicates total cooling output exceeds total cooling load by more than 21%. Please explain the Exception to §140.4(a) used to oversize the cooling equipment in Table E. Additional Remarks.
A filter pressure adjustment has been taken on at least one fan system. See table H for more detail.
If the user changes radio button in Table O, a note saying "Selections made in Table O have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination." should show up in Table D.
Transfer air is being used in at least one zone to meet minimum ventilation requirements. See Table J for detail. Transfer air must be designed per §120.1(g) for air classification and recircultaion limitations and be documented within construction documents.
The permit applicant has indicated on Table M that cooling tower Maximum Cycles of Concentration calculations have been attached or included elsewhere on the plans.
The permit applicant has indicated on Table J that ventilation calculations have been attached or included elsewhere on the plans.
The permit applicant has indicated on Table J that natural ventilation is being utilized to meet ventilation requirements. Additional documentation may be requested by the Authority Having Jurisdiction demonstrating compliance for natural ventilation design.
Table F indicates more than one boiler, however an exception for isolation valve has been indicated that only applies to plants with only one boiler. Please revise Table F. prior to permit application.
Table F indicates a boiler with rated capacity greater than 500kBtu/h, however an exception for temperature reset controls has been indicated that only applies to boilers < 500kBtu/h. Please revise Table F. prior to permit application.
Table F indicates more than one chiller, however an exception for isolation valve has been indicated that only applies to plants with only one chiller. Please revise Table F. prior to permit application.
An exception has been taken to allow electric resistance heating. See Table F. for details.
Table H indicates a Fan Power System Index that exceeds the maximum allowed per §140.4(c). Please revise to demonstrate compliance.
If the user changes radio button in Table P, a note saying "Selections made in Table P have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination." should show up in Table D.
If the user is using continuous ventilation to meet the HRR ventilation requirements (first checkbox in HRR ventilation table) AND J24 and J24 both have values greater than 0, Table D triggers a note stating: "Table J indicates continuous ventilation is being used as an alternative to a balanced system. However, Table J also indicates both supply and exhaust fans are being used. Please verify the same ventilation type is being used in all dwelling units within the building per 120.1(b)2Aivb”
The permit applicant has indicated there multifamily dwelling units does not contain a kitchen or bathroom. See Table J Multifamily Dwelling Unit Ventilation for details
Note on A9: 2019 Update: Ben, these two notes are triggered in Table F. See Table F. mock up for data fields.
Note on P9: 2019 Update: Removed these errors as they are no longer relevant.
Note on I11: 2109 Update: Ben, this is triggered in Table H column 08
Note on A13: Sally Blair: Triggered by Table J column 05 2019 Update: Updated column # that triggers note in Table J & updated note text.
Note on I21: 9/11/20 Triggers when: Table H "Total System Design (B)HP:" row > Table H "Maximum System Fan Power (B)HP:" row
Note on F22: 2019 Update: New for 2019 since Table P was added.
Note on A23: 9/11/20: New note as of 9/10/20 to support the alternative compliance path for HRR balanced system requirements

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## F. HVAC Systems (LMCC)
|  | User input |  |  | auto calculated | [6 empty] | From another Table |  | From look up table
F. HVAC SYSTEM SUMMARY (DRY & WET SYSTEMS)
[d:OnlyUI] Table Instructions: Complete the following equipment schedules to show compliance with mandatory requirements found in §110.1 and §110.2(a) and prescriptive requirements found in §140.4 (a), §140.4(b) and §140.4(k), §170.2(c)1, §170.2(c)3 or §141.0(b)2 and §180.2(b)2 for alterations. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance for mechanical equipment with mandatory requirements found in §110.1 and §110.2(a) and prescriptive requirements found in §140.4 (a), §140.4(b) and §170.2(c)1, §170.2(c)3, §140.4(k) or §141.0(b)2 and §180.2(b)2 for alterations. [d:/OnlyRG]
THIS TABLE IS BRAND NEW FOR 2022
Space Conditioning System Information
01 | 02 | 03 | 04 | 05 | 06 | 07
Name or Item Tag | Quantity | System Serving | System Status | Space Type | Utilizing Recovered Heat | Distrubution System Type
|  | Dropdown | Dropdown | Dropdown | ¨ | Dropdown
|  | System Serving Dropdown | Status Dropdown | Space Type Dropdown |  | Distrubution System Type Dropdown
|  | Single Zone | New/Addition | Retail |  | Ducted
|  | Multi-Zone | Alteratation | Grocery |  | Ductless
|  | Multiple Dwelling units |  | School |  | Piping
|  | Individual Dwelling Unit |  | Financial Institution |  | Radiant
Library
Office Space in Wearhouse
Office
NOTE - The sizing table below is not completed from left to right in the user interface. Sizing information is needed to determine if system type is restricted. This is ok since the form is just a reporting tool, not a user interface |  |  |  | Other
Dry System Equipment Sizing (includes air conditioners, condensers, heat pumps, VRF, furnaces, unit heaters and DOAS systems )
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Name or Item Tag | Equipment Category per Tables 110.2, §140.4(a)2 and 170.2(c)3ai | Equipment Type per Tables 110.2 & Title 20 | Smallest Size Available1 §140.4(a) & 170.2(c)1 | Equipment Sizing per Mechanical Schedule (kBtu/h) §140.4 (a&b), §170.2(c)1 & §170.2(c)2
|  |  |  | Heating Output2,3 |  |  | Cooling Output2,3 |  | Load Calculations3,4
|  |  |  | Per Design (kBtu/h) | Rated (kBtu/h) | Supp. Heating Output (kBtu/h) | Sensible Per Design (kBtu/h) | Rated (kBtu/h) | Total Heating Load (kBtu/h) | Total Sensible Cooling Load (kBtu/h)
auto-populated from table above | Dropdown | Dropdown | Dropdown
1 FOOTNOTES: Equipment shall be the smallest size, within the available options of the desired equipment line, necessary to meet the design heating and cooling loads of the building per §140.4(a) and §170.2(c)1. Healthcare facilities are excepted. | [9 empty] | Reset | Add Row | Remove Last
2 It is common practice to show rated output capacity on the equipment schedule. Sensible cooling output comes from specification sheet tables.
3 If equipment is heating only, leave cooling output and load blank. If equipment is cooling only, leave heating output and load blank.
4 Authority Having Jurisdiction may ask for load calculations used for compliance per §140.4(b) and §170.2(c)2. | [21 empty] | Customized Sizing drop downs for column 02 in Dry System Equipment Efficiency (other than Package Terminal Air Conditioners (PTAC) and Package Terminal Heat Pumps (PTHP)) Table
| Equipment Category Dropdown | Eq Type Dropdown | Smallest Size Dropdown | [10 empty] | Dropdown for Column 034 Eq Type
| Unitary AC/ Condensers | Ben, see column M. | Yes | [17 empty] | From Table 110.2-A >> | AC, water cooled | AC, evaporatively cooled | Condensing Units, air cooled | Condensing Units, water cooled | Condensing Units, evaporatively cooled
| Unitary AC/ Cond. (no elec. resistance) |  | NA: Standby Equip. | [18 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000 | > 135,000
| Unitary heat pumps |  | NA: Load Controls | [9 empty] | "Unitary AC/ Condensers" | AC, water cooled | << from Table 110.2-A | [6 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
| Unitary heat pumps (no elec. resistance) |  | NA: Altered per §141.0(b)2E & 180.2(b)2 | [18 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000
| PTAC/ PTHP |  | NA: System serves Healthcare | [10 empty] | AC, evaporatively cooled | << from Table 110.2-A | [6 empty] | > 760,000 | > 760,000
| SPVAC/ SPVHP |  | NA: DOAS system | [11 empty] | << from Table 110.2-A |  |  | Last updated Table B-2 on 4.3.2020 from Title 20 Section 1605.1
| Variable Refrigerant Flow | [12 empty] | Condensing units, air cooled | << from Table 110.2-A
| Furnace/ Unit heater | [12 empty] | Condensing units, water cooled | << from Table 110.2-A
| Ceiling Mounted Computer Rm AC | [12 empty] | Condensing units, evaporatively cooled | << from Table 110.2-A
Computer Room AC (not ceiling mounted)
Heat Pump + AC Sm. Commercial AC
Split Furnace + AC
Pkg Furnace + AC
Room AC/HP
Dual Fuel Heat Pump
Dedicated Outdoor Air System
Dry System Equipment Efficiency (other than Package Terminal Air Conditioners (PTAC), Package Terminal Heat Pumps (PTHP), DX-DOAS and Dual Fuel Heat Pumps) | [13 empty] | AC, air cooled, split (1 phase)
01 | 02 | 03 | 04 | 05 |  | 06 | 07 | 08 | 09 |  |  |  |  | AC, air cooled, split (3 phase)
Name or Item Tag | Size Category (Btu/h) | Heating Mode |  |  |  |  | Cooling Mode | [6 empty] | AC, air cooled, split, space constrained |  |  |  |  | BEN - PURPLE MEANS YOU NEED TO COME BACK AND TAKE A LOOK. MOST IF NOT ALL ARE TITLE 20 ISSUE. NEED TO MAKE SURE THOSE TABLES DIDN'T CHANGE ALSO.
|  | Rating Condition (oF) | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 |  | Design Efficiency | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency |  |  |  |  | AC, air cooled, package (1 phase)
From Eq Table above | Dropdown | Dropdown | Dropdown | Ben, values from Tables 110.2-A, B, C, E, H, I, J & T20 Tables |  |  | Unit from efficiency tables auto populates here based on size category (col 02) | Ben, values from Tables 110.2-A, B, C, E, H, I, J & T20 Tables | [5 empty] | AC, air cooled, package (3 phase) | [6 empty] | From Tables C-3, C-4 or 110.2-A, depending on size category >> | AC, air cooled, split (1 phase) | AC, air cooled, split (3 phase) | AC, air cooled, split, space constrained | AC, air cooled, package (1 phase) | AC, air cooled, package (3 phase) | AC, air cooled, package, space constrained | AC, air cooled, small duct, high velocity
[7 empty] | Unit from efficiency tables auto populates here based on size category (col 02) | Ben, values from Tables 110.2-A, B, C, E, H, I, J & T20 Tables | [5 empty] | AC, air cooled, package, space constrained | [7 empty] | < 45,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[14 empty] | AC, air cooled, small duct, high velocity | [7 empty] | >= 45,000 and < 65,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
| Size Category Dropdown | Rating Condition Dropdown | Unit Dropdown |  |  |  | Units for auto populating, depends on equipment & size | [5 empty] | Sm. Commercial AC | Air-cooled unitary AC/HP Split Sys (3Ph) | << from Table C-4 to the right | [6 empty] | >= 65,000 and < 135,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
| Ben, see tables in column AF of this tab for custom drop downs. Sorry! | See choices in notes in column AF rows 51 & 76 of this tab. | COP |  |  |  | EER | [6 empty] | Air-cooled unitary AC/HP Pkg (3Ph) | << from Table C-4 to the right | [6 empty] | >= 135,000 and < 240,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000
|  |  | AFUE |  |  |  | IEER | [5 empty] | "Unitary Heat Pumps" | Air cooled, split (1 phase) | [7 empty] | >= 240,000 and < 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000
|  |  | Et |  |  |  | SEER | [6 empty] | Air cooled, split (3 phase) | [7 empty] | >= 760,000
|  |  | Ec |  |  |  | COP | [6 empty] | Air cooled, split, space constrained
|  |  | HSPF |  |  |  | SCOP | [6 empty] | Air cooled, package (1 phase)
Air cooled, package (3 phase)
[14 empty] | Air cooled, package, space constrained | [6 empty] | From Table C-4 to the left >> | Air-cooled unitary AC+HP Split Sys (3Ph) | Air-cooled unitary AC+HP Pkg (3Ph)
[14 empty] | Aircooled, small duct, high velocity | [7 empty] | < 65,000 | < 65,000
[14 empty] | Water source | << from Table 110.2-B | [5 empty] | From Table 110.2-B >> | Water source | Groundwater source | Ground source | Water source water-to-water | Groundwater source water-to water | Ground source brine-to-water
[14 empty] | Groundwater source | << from Table 110.2-B | [6 empty] | <17,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000
Dry System Equipment Efficiency (Package Terminal Air Conditioners (PTAC) and Package Terminal Heat Pumps (PTHP) only) | [13 empty] | Ground source | << from Table 110.2-B | [6 empty] | =>17,000 and < 135,000
01 | 02 | 03 | 04 | 05 | 06 | 070 | [7 empty] | Water source water-to-water | << from Table 110.2-B | [6 empty] | > 135,000 and < 240,000
Name or Item Tag | Heating Mode |  |  | Cooling Mode | [9 empty] | Groundwater source water-to water | << from Table 110.2-B
| Rated Output Capacity (kBtu/h) | Minimum COP Required per Table 110.2-E | Design COP | Rated Output Capacity (kBtu/h) | Minimum EER Required per Table 110.2-E | Design EER | [7 empty] | Ground source brine-to-water | << from Table 110.2-B | [5 empty] | From Table C-3, C-4, 110.2-B or 110.2-C depending on size category>> | Air-cooled gas-engine heat pump | Air cooled, split (1 phase) | Air cooled, split (3 phase) | Air cooled, split, space constrained | Air cooled, package (1 phase) | Air cooled, package (3 phase) | Air cooled, package, space constrained | Air cooled, small duct, high velocity
[14 empty] | Air-cooled gas-engine heat pump | << from Table 110.2-C | [6 empty] | Grey out the cell for this selection | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
From Eq Table above | Comes from sizing table column 06 | From Table 110.2-E |  | Comes from sizing table column 09 | From Table 110.2-E | [17 empty] | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
[23 empty] | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
[13 empty] | "PTAC/PTHP" | PTAC newly constructed or newly conditioned | << from Table 110.2-E | [7 empty] | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000
[14 empty] | PTAC replacements | << from Table 110.2-E
[14 empty] | PTHP newly constructed or newly conditioned | << from Table 110.2-E
[14 empty] | PTHP replacements | << from Table 110.2-E
[13 empty] | "SPVAC/ SPVHP" | SPVAC | << from Table 110.2-E
NOTE - This table should act like the fan table with tiered levels. There can be mutiple Boiler systems and multiple boilers within each boiler system | [13 empty] | SPVAC nonweatherized space constrained | << from Table 110.2-E
Boiler Efficiency and Controls | [13 empty] | SPVHP | << from Table 110.2-E |  | Last updated Table C-3 on 4.3.2020 from Title 20 Section 1605.1 |  |  |  | From Table 110.2-E >> | SPVAC | SPVAC nonweatherized space constrained | SPVHP | SPVHP nonweatherized space constrained
Boiler System Serving: |  |  | User Input | [10 empty] | SPVHP nonweatherized space constrained | << from Table 110.2-E | [6 empty] | < 65,000 | < 30,000 | < 65,000 | < 30,000
01 | 02 |  | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | [11 empty] | > 65,000 and < 135,000 | > 30,000 and < 36,000 | > 65,000 and < 135,000 | > 30,000 and < 36,000
Boiler Name or Item Tag | Equipment Type1 |  | Qty | Rated Input Capacity (Btu/h)2, 3 | Rated Efficiency | Minimum Efficiency Required per §110.2 | Efficiency Unit | Boiler Controls per §140.4(k) & §170.2(c)Iiii |  | High Capacity Boiler Exceptions | [11 empty] | > 135,000 and < 240,000 |  | > 135,000 and < 240,000
[8 empty] | Isolation Valve | Temperature Reset
| Dropdown |  |  |  |  | Use table 110.2-J column after 1/10/23 | Units listed in Table 110.2-J | Dropdown | Dropdown | Dropdown
System Efficiency |  |  | User Input 05: Minimum System Efficiency for High Capacity Boilers per 140.4(k)8A; User Input 08: 90%
1 FOOTNOTES: Use NRCC-PLB to document compliance with domestic hot water and service water heating systems | bar: User Input 03 to User Input 04
2 Maximum capacity- minimum and maximum ratings per the certified unit capacity as provided for and allowed by the unit's controls |  |  | User Input 08: Isolation Dropdown; User Input 09: Temperature Reset Dropdown; User Input 10: HCB Exceptions Dropdown
3 Includes oil-fired (residual) |  |  | User Input 08: Yes; User Input 09: Yes; User Input 10: >=25% space heating provided by on-site renewable | [10 empty] | From Table 110.2-G >> | VRF air conditioners, air cooled
|  |  | User Input 08: NA: only 1 boiler in plant; User Input 09: NA: < 500,000 Btu/h; User Input 10: >=25% space heating provided by site recovered energy | [11 empty] | < 65,000
| Equipment Type Dropdown |  | User Input 09: NA: Variable Flow Controls; User Input 10: >=25% space heating provided heat recovery chillers |  |  | "VRF" | VRF air conditioners, air cooled | << from Table 110.2-G | [6 empty] | > 65,000 and < 135,000
| Hot water: Gas-Fired |  | User Input 09: NA: System serves Healthcare; User Input 10: Installed in individual dwelling unit |  |  |  | VRF heat pump, air cooled | << from Table 110.2-H | [6 empty] | > 135,000 and < 240,000
| Hot water: Oil-Fired |  | User Input 10: >=50% heating served by perimeter convective/radiant ceiling panels |  |  |  | VRF water source | << from Table 110.2-H | [6 empty] | > 240,000
| Steam: Gas-Fired, not natural draft |  | User Input 10: Serving Multifamily Occupancy |  |  |  | VRF groundwater source | << from Table 110.2-H
| Steam: Gas-Fired, natural draft |  | User Input 10: No Exceptions Apply |  |  |  | VRF ground source | << from Table 110.2-H | [5 empty] | From Table 110.2-H >> | VRF heat pump, air cooled | VRF water source | VRF groundwater source | VRF ground source
| Steam: Oil-Fired | [11 empty] | "Furnace/ Unit Heater" | Warm-air central furnace, gas-fired | << from Table 110.2-I | [6 empty] | < 65,000 | < 65,000 | < 135,000 | < 135,000
[13 empty] | "Furnace/ Unit Heater" | Warm-air duct furnace, gas-fired | << from Table 110.2-I | [6 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000
[14 empty] | Warm-air unit heaters, gas-fired | << from Table 110.2-I | [6 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
[13 empty] | "Furnace/ Unit Heater" | Weatherized gas central furnace w single phase supply | << from Table 4-1 to the right | [6 empty] | > 240,000 | >=240,000
[14 empty] | Non-weatherized gas central furnace w single phase supply | << from Table 4-1 to the right |  | Last updated Table C-4 on 4.3.2020 from Title 20 Section 1605.1.. Larger size HP are covered in T24 110.2 Tables.
[13 empty] | "Furnace/ Unit Heater" | Wall furnace, fan | << from Table 4-2 to the right | [5 empty] | From Table 110.2-I >> | Warm-air central furnace, gas-fired | Warm-air duct furnace, gas-fired | Warm-air unit heaters, gas-fired
[14 empty] | Wall furnace, gravity | << from Table 4-2 to the right | [6 empty] | < 225,000 | Grey out the cell for this selection | Grey out the cell for this selection
[14 empty] | Floor furnace | << from Table 4-2 to the right | [6 empty] | > 225,000
[14 empty] | Room Heater | << from Table 4-2 to the right
[13 empty] | "Computer Rm AC (not ceiling mounted) | CRAC, air-cooled, downflow | << from Table C-7 to the right | [5 empty] | From Title 20 Table E-6 to the left >> | Weatherized gas central furnace w single phase supply | Non-weatherized gas central furnace w single phase supply
[14 empty] | CRAC, air-cooled, upflow | << from Table C-7 to the right | [6 empty] | < 225,000 | < 225,000
[14 empty] | CRAC, water-cooled, downflow | << from Table C-7 to the right
[14 empty] | CRAC, water-cooled, upflow | << from Table C-7 to the right | [5 empty] | From Table E-2 to the left >> | Wall furnace, fan | Wall furnace, gravity | Floor furnace | Room Heater
[14 empty] | CRAC, water-cooled w econ, downflow | << from Table C-7 to the right | [6 empty] | < 42,000 | < 27,000 | < 37,000 | < 20,000
[14 empty] | CRAC, water-cooled w econ,upflow | << from Table C-7 to the right | [6 empty] | > 42,000 | > 27,000 and < 46,000 | > 37,000 | > 20,000 and < 27,000
[14 empty] | CRAC, Glycol-cooled, downflow | << from Table C-7 to the right | [7 empty] | > 46,000 |  | > 27,000 and < 46,000
[14 empty] | CRAC, Glycol-cooled, upflow | << from Table C-7 to the right | [9 empty] | > 46,000
[14 empty] | CRAC, Glycol-cooled w econ, downflow | << from Table C-7 to the right | Last updated Table C-7 on 4.3.2020 from Title 20 Section 1605.1
[14 empty] | CRAC, Glycol-cooled w econ, upflow | << from Table C-7 to the right | [5 empty] | From Table C-7 to the left >> | CRAC, air-cooled, downflow | CRAC, air-cooled, upflow | CRAC, water-cooled, downflow | CRAC, water-cooled, upflow | CRAC, water-cooled w econ, downflow | CRAC, water-cooled w econ, upflow | CRAC, Glycol-cooled, downflow | CRAC, Glycol-cooled, upflow | CRAC, Glycol-cooled w econ, downflow | CRAC, Glycol-cooled w econ, upflow
[13 empty] | Room AC/HP | Room AC, louvered sides | << from Table B-2 to the right | [6 empty] | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[14 empty] | Room AC, no louvers | << from Table B-2 to the right | [6 empty] | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000
[14 empty] | Room AC, casement only | << from Table B-2 to the right | [6 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000
[14 empty] | Slider Room AC, casement | << from Table B-2 to the right
[14 empty] | Room AC Heat Pump, louvered sides | << from Table B-2 to the right
[14 empty] | Room AC Heat Pump, no louvers | << from Table B-2 to the right
[13 empty] | Furnace + AC | AC, air cooled, split + warm-air central furnace, gas-fired
AC, air cooled, split + weatherized gas central furnace
[14 empty] | AC, air cooled, single pkg + weatherized gas central furnace, 1 phase supply | [6 empty] | From Table 110.2-A & T20 C-3 (cooling) & 110.2-I & Table E-6 to the left (heating) >>> | AC, air cooled, split/ single package + Warm-air central furnace, gas-fired | AC, air cooled, split+ weatherized gas central furnace w single phase supply |  | From Table 110.2-A & T20 C-3 (cooling) & 110.2-I & Table E-6 to the left (heating) >>> | AC, air cooled, split/ single package + Weatherized gas central furnace w single phase supply | AC, air cooled, split/ single package + Warm-air central furnace, gas-fired
[14 empty] | AC, air cooled, single pkg + warm-air central furnace, gas-fired | [7 empty] | <45kBtuh cooling/ <225kBtuh heating | <45kBtuh cooling/ <225kBtuh heating
[13 empty] | Unitary AC/ Cond. (no elec. resistance) | AC, water cooled | [7 empty] | <45kBtuh cooling/ >225kBtuh heating | <45kBtuh cooling/ >225kBtuh heating |  |  | <65kBtuh cooling/ <225kBtuh heating | <65kBtuh cooling/ <225kBtuh heating
Chiller Efficiency and Controls | [13 empty] | AC, evaporatively cooled | [7 empty] | >45kBtuh cooling/ <225kBtuh heating | >45kBtuh cooling/ <225kBtuh heating |  |  | <65kBtuh cooling/ >225kBtuh heating | <65kBtuh cooling/ >225kBtuh heating
01 |  | 02 | 03 | 04 | 05 |  |  | 06 | 07 | 08 | 09 | 10
Name or Item Tag |  | Equipment Type | Qty | Size Category1 (Tons) | Chiller Efficiency "Path B" Exception per §140.4(i) & §170.2(c)g |  |  | Rated Efficiencies | Minimum Efficiencies Required per §110.22 | Efficiency Unit | Controls per §140.4(k) & §170.2(c)I | [10 empty] | >45kBtuh cooling/ >225kBtuh heating | >45kBtuh cooling/ >225kBtuh heating |  |  | >65kBtuh cooling/ <225kBtuh heating | >65kBtuh cooling/ <225kBtuh heating
[11 empty] | Isolation Valve | Temperature Reset |  | Condensing units, air cooled | [7 empty] | >65kBtuh cooling/ <225kBtuh heating | >65kBtuh cooling/ <225kBtuh heating |  |  | >65kBtuh cooling/ >225kBtuh heating | >65kBtuh cooling/ >225kBtuh heating | bar: User Input 05 to User Input 07
|  | Dropdown to match Table 110.2-D | User Input 04: Dropdown; User Input 05: Dropdown; User Input 09: Ben, "Path B" value from Table 110.2-D; User Input 10: Ben, "Path B" units from Table 110.2-D | Dropdown | Dropdown |  | Condensing units, water cooled | [5 empty] | EVEN THE YELLOW ONES NEED TO BE REVISITED AGAIN. THEY HAVE ONLY BE UPDATED FOR COOLING EFFICIENCY |  | >65kBtuh cooling/ >225kBtuh heating | >65kBtuh cooling/ >225kBtuh heating |  |  | >135kBtuh cooling/ <225kBtuh heating | >135kBtuh cooling/ <225kBtuh heating
|  |  | User Input 09: Ben, "Path B" value from Table 110.2-D; User Input 10: Ben, "Path B" units from Table 110.2-D |  |  |  | Condensing units, evaporatively cooled |  | Last updated Table E-6 on 4.3.2020 from Title 20 Section 1605.1 | [5 empty] | >135kBtuh cooling/ <225kBtuh heating | >135kBtuh cooling/ <225kBtuh heating |  |  | >135kBtuh cooling/ >225kBtuh heating | >135kBtuh cooling/ >225kBtuh heating
|  |  | User Input 10: Reset | Add Row | Remove Last |  | AC, air cooled, split (1 phase) | [7 empty] | >135kBtuh cooling/ >225kBtuh heating | >135kBtuh cooling/ >225kBtuh heating |  |  | >240kBtuh cooling/ <225kBtuh heating | >240kBtuh cooling/ <225kBtuh heating
1 FOOTNOTES: Chilled water plants shall not have more than 300 tons provided by air-cooled chillers. Exceptions may apply per §140.4(j). | [13 empty] | AC, air cooled, split (3 phase) | [7 empty] | >240kBtuh cooling/ <225kBtuh heating | >240kBtuh cooling/ <225kBtuh heating |  |  | >240kBtuh cooling/ >225kBtuh heating | >240kBtuh cooling/ >225kBtuh heating
2 Efficiency required is a minimum when "EER" or "COP" is the Efficiency Unit in column 08. It is also a minimum when "IPLV" is the unit for air-cooled, absorption, and water cooled gas engine chillers. Efficiency required is a maximum when "kW/ton" is the Efficiency Unit and when "IPLV" is the unit for water cooled electrically operated chillers. | [10 empty] | Isolation Dropdown | Temp Reset Dropdown |  | AC, air cooled, split, space constrained | [7 empty] | >240kBtuh cooling/ >225kBtuh heating | >240kBtuh cooling/ >225kBtuh heating |  |  | >760kBtuh cooling/ <225kBtuh heating | >760kBtuh cooling/ <225kBtuh heating
|  | Equipment Type Dropdown | User Input 04: Size Category Dropdown; User Input 05: Efficiency Exception Dropdown | Yes | Yes |  | AC, air cooled, package (1 phase) | [7 empty] | >760kBtuh cooling/ <225kBtuh heating | >760kBtuh cooling/ <225kBtuh heating |  |  | >760kBtuh cooling/ >225kBtuh heating | >760kBtuh cooling/ >225kBtuh heating
|  | Air Cooled: Condenser elec. operated | User Input 04: < 75; User Input 05: No exception taken | NA: only 1 chiller in plant | NA: ≤ 500 kBtu/hr (41.67 tons) |  | AC, air cooled, package (3 phase) | [7 empty] | >760kBtuh cooling/ >225kBtuh heating | >760kBtuh cooling/ >225kBtuh heating
|  | Air Cooled: w/o condenser elec. operated | User Input 04: ≥ 75 and < 150; User Input 05: 1. Electrical service > 600V | NA: chillers in series | NA: Variable Flow Controls |  | AC, air cooled, package, space constrained
|  | Water Cooled: Reciprocating | User Input 04: ≥ 150 and < 300; User Input 05: 2. Heat recovery w/ design capacity > 40% of the design chiller cooling capacity |  | NA: System serves Healthcare |  | AC, air cooled, small duct, high velocity
|  | Water Cooled: Positive displacement | User Input 04: ≥ 300 and < 400; User Input 05: 3. Charging energy storage systems w/ charging temperature < 40oF |  |  | Unitary heat pumps (no elec. resistance) | Air cooled, split (1 phase)
|  | Water Cooled: Centrifugal | User Input 04: ≥ 400 and < 600; User Input 05: 4. 4th (or more) chiller in this building |  |  |  | Air cooled, split (3 phase)
|  | Air Cooled: Absorption, single effect | User Input 04: ≥ 600 |  |  |  | Air cooled, split, space constrained |  | Last updated Table E-2 on 4.3.2020 from Title 20 Section 1605.1 |  |  |  |  | From Table B-2 >>> | Room AC, louvered sides | Room AC, no louvers | Room AC, casement only | Room AC, slider & casement | Room AC Heat Pump, louvered sides | Room AC Heat Pump, no louvers
|  | Water Cooled: Absorption, single effect | [11 empty] | Air cooled, package (1 phase) | [7 empty] | < 8,000 | < 8,000 | Grey out the cell for this selection | Grey out the cell for this selection | < 20,000 | < 14,000
|  | Absorption: Double effect, indirect-fired | [11 empty] | Air cooled, package (3 phase) | [7 empty] | >= 8,000 and < 14,000 | >= 8,000 and < 11,000 |  |  | >= 20,000 | >= 14,000
|  | Absorption: Double effect, direct-fired | [11 empty] | Air cooled, package, space constrained | [7 empty] | >= 14,000 and < 20,000 | >= 11,000 and < 14,000
|  | Water Cooled: Gas engine | [11 empty] | Aircooled, small duct, high velocity | [7 empty] | >= 20,000 and < 28,000 | >= 14,000 and < 20,000
[14 empty] | Water source | [7 empty] | >= 28,000 | >= 20,000
Groundwater source
Note - This table is brand new | [13 empty] | Ground source
[14 empty] | Water source water-to-water | [6 empty] | From Table 110.2-A >> | AC, water cooled | AC, evaporatively cooled | Condensing Units, air cooled | Condensing Units, water cooled | Condensing Units, evaporatively cooled
DX-DOAS Efficiency | [13 empty] | Groundwater source water-to water | [7 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000 | > 135,000
01 |  | 02 | 03 | 04 | 05 |  | 06 | 07 | 08 |  |  |  |  | Ground source brine-to-water | [7 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
Name or Item Tag |  | Equipment Type | Qty | Energy Recovery | Rating Condition |  | Rated Efficiencies | Efficiency Unit | Minimum Efficiency |  |  |  |  | Air-cooled gas-engine heat pump | [7 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000
[13 empty] | DOAS | DOAS | [7 empty] | > 760,000 | > 760,000
From sizing table above |  | Dropdown to match Table 110.2-K | User Input 04: Dropdown; User Input 05: Dropdown; User Input 08: ISMRE |  |  |  | DX-DOAS
|  |  | User Input 08: ISCOP |  |  | Computer Rm AC Ceiling Mounted
[21 empty] | From Tables C-3, C-4 or 110.2-A, depending on size category >> | AC, air cooled, split (1 phase) | AC, air cooled, split (3 phase) | AC, air cooled, split, space constrained | AC, air cooled, package (1 phase) | AC, air cooled, package (3 phase) | AC, air cooled, package, space constrained | AC, air cooled, small duct, high velocity
[22 empty] | < 45,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[22 empty] | >= 45,000 and < 65,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
[22 empty] | >= 65,000 and < 135,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
|  | Equipment Type Dropdown | User Input 04: Energy Recovery Dropdown; User Input 05: Rating Condition Dropdown | [11 empty] | >= 135,000 and < 240,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000
|  | Air Cooled | User Input 04: Yes; User Input 05: Cooling Tower Condenser Water | [11 empty] | >= 240,000 and < 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000
|  | Air Source Heat Pump | User Input 04: No; User Input 05: Chilled Water | [11 empty] | >= 760,000
Water Cooled
|  | Water Source Heat Pump | User Input 05: Rating Condition Dropdown | [11 empty] | Water source | Groundwater source | Ground source | Water source water-to-water | Groundwater source water-to water | Ground source brine-to-water
|  |  | User Input 05: Ground Source Closed Loop | [11 empty] | > 65,000 and < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000
|  |  | User Input 05: Ground Water Source | [11 empty] | > 135,000 and < 240,000
Water Source
Note - This table is brand new
[22 empty] | Air-cooled gas-engine heat pump | Air cooled, split (1 phase) | Air cooled, split (3 phase) | Air cooled, split, space constrained | Air cooled, package (1 phase) | Air cooled, package (3 phase) | Air cooled, package, space constrained | Air cooled, small duct, high velocity
[22 empty] | Grey out the cell for this selection | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
Dual Fuel Heat Pump | [22 empty] | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | [12 empty] | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
Name or Item Tag | Equipment Category | Equipment Type | User Input 03: Size Category (Btu/h); User Input 04: Heating Mode; User Input 08: Cooling Mode | [12 empty] | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000
|  |  |  | Rating Condition (oF) | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency
From Eq Table above | Dropdown | Dropdown | Dropdown | Dropdown | Lookup based on heat pump system type selected | Always appropriate HP values |  | Unit from efficiency tables auto populates here based on size category (col 02) | Values from Tables 110.2-A, B, C, E, H, I, J & T20 Tables | [12 empty] | Air Cooled with free air discharge condenser, ducted | Air Cooled with free air discharge condenser, nonducted | Air Cooled with free air discharge condenser with fluid economizer, ducted | Air Cooled with free air discharge condenser with fluid economizer, nonducted | Air cooled with ducted condenser, ducted | Air cooled with ducted condenser, nonducted | Air cooled with fluid economizer and ducted condenser, ducted | Air cooled with fluid economizer and ducted condenser, nonducted
|  |  | User Input 08: Unit from efficiency tables auto populates here based on size category (col 02); User Input 09: Values from Tables 110.2-A, B, C, E, H, I, J & T20 Tables | [11 empty] | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h
| Always = Furnace/Unit Heater | Dropdown | Dropdown | Always Blank/Gray | Dropdown | Always appropriate furnace value |  | Always Blank/Gray | Always Blank/Gray | Always Blank/Gray | [11 empty] | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h
[22 empty] | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h
| HP Equipment Category Dropdown | Equipment Type Dropdown | User Input 03: Size Category Dropdown; User Input 04: Rating Condition Dropdown; User Input 05: Unit Dropdown | [11 empty] | Water Cooled, Ducted | Water Cooled, nonducted | Water cooled with fluid economizer, ducted | Water cooled with fluid economizer, nonducted | Glycol cooled, ducted | Glycol cooled, nonducted | Glycol cooled with fluid economizer, ducted | Glycol cooled with fluid economizer, nonducted
| Unitary Heat Pump | Provide the appropriate equipment type dropdowns based on the equipment category chosen in 02. | User Input 03: See tables in column AF of this tab for custom drop downs.; User Input 04: See choices in notes in column AF rows 51 & 76 of this tab.; User Input 05: COP | [11 empty] | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h
| Unitary Heat Pump (no elec resistance) |  | User Input 05: AFUE | [11 empty] | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h
[22 empty] | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | bar: User Input 05
Ec
HSPF
Heat Rejection Equipment (Cooling Towers, Condensers, Waterside Economizers) Efficiency and Controls
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12
Name or Item Tag | Equipment Type1 | Qty | Rating Condition (oF) | Rated Performance | Minimum Required Performance per Table 110.2-F, §140.4(h)5 & §170.2(c)fv | Performance Unit | Fan Speed Control §140.4(h)1 | Tower Flow Turndown §140.4(h)2 | Fan Control in Multiple Cell Equipment §140.4(h)4 | Economizer Controls §140.4(e) | Condenser Water Temp Reset Controls
| Dropdown to match Table 110.2-G |  | Dropdown |  | Value from table |  | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
1 FOOTNOTES: Centrifugal fan open-circuit towers are not allowed for rated capacities > 900 gpm at 95oF condenser water return, 85oF condenser water supply and 75oF outdoor wet-bulb temperature. Exceptions may apply per §140.4(h)4. | [12 empty] | Link to 2022 Table 110.2-F
| Equipment Type Dropdown |  | User Input 07: Fan Speed Control Dropdown; User Input 08: Tower Flow Turndown Dropdown; User Input 09: Fan Control Dropdown; User Input 10: Economizer Control Dropdown | Cond. Water Temp Reset Controls Dropdown |  | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1102mandatoryrequirementsforspaceconditioningequipment.htm#table1102fperformancerequirementsforheatrejectionequipment.htm
| Axial fan open-circuit tower, CW loop in CHW plant >= 900gpm |  | Rating Condition Dropdown |  |  |  | Yes | Yes | Yes | Designed per §140.4(e) | Yes
| Replacement axial fan open-circuit tower, CW loop in CHW plant >= 900gpm |  | User Input 03: 165oF entering gas temp 105oF condensing temp 75oF entering air wb"; User Input 07: NA: Fan motor < 7.5hp (5.6kW); User Input 08: NA: Single condenser water pump; User Input 09: NA: Not multiple cell | No
| Propeller/ axial fan open-circuit cooling tower |  | User Input 03: 140oF entering gas temp 96.3oF condensing temp 75oF entering air wb"; User Input 07: NA: Integral to other equip.; User Input 08: NA: Not open-circuit tower; User Input 09: NA: No variable speed drives
| Propeller/ axial fan closed-circuit cooling tower |  | User Input 07: NA: Cond. fans serving > 1 refrigerant circuits
| Centrifugal fan open-circuit cooling tower |  | User Input 07: NA: Cond. fans serving flooded cond.
| Centrifugal fan closed-circuit cooling tower |  | User Input 07: NA: Mult. fans & lead fans meet req.
Propeller/ axial fan evaporative condensers
Centrifugal fan evaporative condensers
Air cooled condensers
Waterside Economizer
Electric Resistance Heating
01 |  | 02 | User Input 03: 03; User Input 04: 04
Name or Item Tag |  | Equipment Description | User Input 03: Output Capacity (kW); User Input 04: Applicable Exception to §140.4(g) Allowing Electric Resistance Heating
|  | dropdown | User Input 04: dropdown
Elec Resistance Dropdown
|  | Dropdown | User Input 04: Exception 1: Supplement to a heating system in which at least 60% of the annual energy requirement is supplied by site-solar or recovered energy.
|  | Baseboard | User Input 04: Exception 2: Supplement to a heat pump heating system and the heating capacity of the heat pump is more than 75% of the design heating load calculated in accordance with §140.4.
|  | Under-mat | User Input 04: Exception 3: Total capacity of electric-resistance heating systems serving the entire building is less than 10% of the total design output capacity of all heating equipment serving the entire building.
|  | Other | User Input 04: Exception 4: Total capacity of electric-resistance heating systems serving the entire building, excluding those allowed under Exception 2, is no more than 3 kW.
Exception 5: Serving an entire building that is not high-rise residential or hotel/motel and has a conditioned floor area no greater than 5,000 ft2, has no mechanical cooling and is in an area without natural gas access.
NA: Alteration, replacement of existing electric resistance heating system.
Note on F11: 6.29.21 If selected, ignore the custom dropdown options for Equipment Category 02 and Equipment Type 03
Note on G13: 7.5.22 This is needed for downstream CF2Rs, this does not trigger other fields or affect compliance logic.
Note on C15: 3.3.22 If Multi-zone or Dwelling unit is selected, 03-06 are gray/blank
Note on D15: 3.3.22 If Alteration is selected, 04-07 blank/grayed out
Note on E21: Ben Lalor: If other is selected 06 blank/grayed out
Note on E27: 2020 Update: F.05, F.06, and F.07 should Trigger when: F.02 = - Sm. Commercal AC - Unitary Heat Pump - Furnace/Unit Heater - Furnace + AC OR F.03 = - PTHP newly constructed or newly conditioned - PTHP replacements - SPVHP - SPVHP nonweatherized space constrained - VRF heat pump, air cooled - VRF water source - VRF groundwater source - VRF ground source OTHERWISE F.05, F.06, F.07 should be grayed out
Note on H27: 2020 UPDATE: F.08 and F.09 should trigger when: F.02 = - Unitary AC/Condenser - Heatpump + AC - Unitary Heat Pump - Computer Room AC - Room AC/HP - Furnace + AC - PTAC/PTHP - SPVAC/SPVHP - VRF OTHERWISE F.08 and F.09 should be grayed out
Note on J28: October 2019 Updates Added units to F.10 and F.11
Note on B29: 6.6.21 If 03 above = Multi-zone, 04 =alteration or 06 has been selected, then user has the options to select any of the equipment categories in the full list below. ELSE: If F.03 Table Above = "Individual Dwelling unit" AND A.02 = 1-15 Equipment Category 02 limited to - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) If F.03 Table Above = "Individual Dwelling unit"" AND A.02 = 16 Equipment Type 03 limited to - Unitary Heat Pump - DUAL FUEL HEAT PUMP F.03 = Single Zone AND If A.02 = 2-15 AND space type = retail OR grocery AND rated cooling capacity 09 <=240 Then equipment type 03 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) F.06 = Single Zone AND If A.02 = 1 OR 16 AND space type = retail OR grocery AND rated cooling capacity 09 <=65 Then equipment type 03 limited to the following options: - Furnace + AC F.06 = Single Zone AND If A.02 = 1 OR 16 AND space type = retail OR grocery AND rated cooling capacity 09 >65 AND <240 Then equipment type 03 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP F.06 = Single Zone AND If climate zone = 2-15 AND space type = school AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) F.06 = Single Zone AND If climate zone = 1 OR 16 AND space type = school AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP F.06 = Single Zone AND If climate zone = 1-15 AND space type = office OR financial institution OR library AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) F.06 = Single Zone AND If climate zone = 16 AND space type = office OR financial institution OR library AND rated cooling capacity 09 <=65 Then equipment type 02 limited to the following options: - Furnace + AC - Unitary Heat Pumps F.06 = Single Zone AND If climate zone = 16 AND space type = office OR financial institution OR library AND rated cooling capacity 09 > 65 AND <=225 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP*************************** F.06 = Single Zone AND If space type = office spaces in warehouses AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) ELSE choose from the full list of equipment categories
Note on E29: 2019 Update: If this value is > 1.43x column10, Table D needs to return the Row 9 error on the Table D tab.
Note on H29: 2019 Update: If this value is > 1.21x column11, Table D needs to return the Row 10 error on the Table D tab.
Note on C35: 2019 Update: Changes were made to these custom dropdowns for 2019
Note on B36: 6.10.20: Added category
Note on AH36: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.1" in the upper row & "13.9" in the lower row
Note on AI36: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.1" in the upper row & "12.3" in the lower row
Note on AJ36: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.5" in the upper row & "11.8" in the lower row
Note on AK36: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AL36: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AH37: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.5" in the upper row & "13.9" in the lower row
Note on AI37: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.0" in the upper row & "12.2" in the lower row
Note on B38: 6.10.20: Added category
Note on D38: Sally Blair: Greys out columns 05, 07, 08 2019 Update: This should no longer gray out 05, 06, or 08
Note on AH38: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.4" in the upper row & "13.6" in the lower row
Note on AI38: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "12.1" in the lower row
Note on D39: 2019 Update: Added new NA choice for new exception for Healthcare facilities.
Note on AH39: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.2" in the upper row & "13.5" in the lower row
Note on AI39: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.7" in the upper row & "11.9" in the lower row
Note on B45: THIS NEEDS TO BE UPDATED IN FORM AND SCHEMA Rename this "Sm. Commercial AC"
Note on B46: 2020 Update: Remove "Split" from this dropdown choice.
Note on B47: 2019 Update: Remove this choice from dropdown and add "Room AC/HP"
Note on B49: 3.14.22 When DFHP is selected, gray equipment type 03 and transfer system to DFHP efficiency table. They still need to complete 04-11
Note on A52: Sally Blair: This table only shows up if any of the equip. categories OTHER THAN "PTAC/PTHP" is selected in Eq Sizing Table above. Otherwise, user shouldn't see this at all (including title).
Note on D53: October 2019 Update: Change Trigger for F.04/5/6.They used to trigger based on F.10 but they should trigger if F.05 >=1, otherwise they are gray
Note on H53: October 2019 Update: Change Trigger for F.07/8/9. They used to trigger based on F.11 but they should trigger if F.05 >=1 , otherwise they are gray
Note on A56: 6.3.22 Anything designated as one of the follwing does not transfer to this table. Everything else does. PTAC/PTHP DX-DOAS Dual Fuel Heat Pump
Note on C56: Sally Blair: This is only a dropdown if column 03 in Dry System Equipment Sixing table is "VRF heat pump, air cooled" OR "Air cooled split/single package". Otherwise this cell greys out. 2019 Update: We got rid of "Air cooled split/ single package" as a dropdown choice in column 03. We need to add the following to take it's place: - "Air cooled, split" - "Air cooled, split, space constrained" - "Air cooled, packaged" - "Air cooled, packaged, space constrained"
Note on E56: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on G56: Sally Blair: If nothing is entered in Column 10 above in the Sizing Table, columns 03-06 here grey out.
Note on J56: Sally Blair: If nothing is entered in Column 11 above in the Sizing Table, columns 07-09 here grey out.
Note on AH57: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "12.2" in the lower row. From Table C-3
Note on AI57: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AJ57: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AK57: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.0" in the lower row. From Table C-3
Note on AL57: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AM57: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AN57: NEEDS TO BE UPDATED IN FORM AND SCHEMA If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AH58: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.7" in the lower row. From Table C-3
Note on AI58: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AJ58: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AK58: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AL58: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AM58: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on D59: Sally Blair: This needs to be a custom dropdown which only includes the unit relevant to the equipment type chosen. There's only one instance where they get to choose- Warm Air Central Furnace, Gas fired.
Note on AH59: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AI59: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AJ59: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AK59: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AL59: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AM59: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on B60: 2019 Update: Changes were made to these sizing dropdowns for 2019.
Note on AH60: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AI60: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AJ60: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AK60: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AL60: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AM60: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AH61: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AI61: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AJ61: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AK61: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AL61: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AM61: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AH62: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on H64: 2019 Update: Added new unit to dropdown for CRACs
Note on AH67: NEED TO UPDATE IN FORM AND SCHEMA Column 07 upper should be SEER & Column 08 upper should be "14.0" & column 04 should be HSPF & column 05 should be "8.2" From Table C-4
Note on AI67: NEED TO UPDATE IN FORM AND SCHEMA Column 07 upper should be SEER & Column 08 upper should be "14.0" & column 04 should be HSPF & column 05 should be "8.0" From Table C-4
Note on AH70: 7/30/20 - New Size Category Cooling Mode Efficiency = 12.2 EER Heating Mode Efficiency = 4.3 COP
Note on AI70: Sally Blair: this would result in the Cooling Mode eff. Of 18.0 EER & the heating mode eff. Of 3.7 COP.
Note on AJ70: Sally Blair: this would result in the Cooling Mode eff. Of 14.1 EER & the heating mode eff. Of 3.2 COP.
Note on AK70: Sally Blair: this would result in the Cooling Mode eff. Of 10.6 EER & the heating mode eff. Of 3.7 COP.
Note on AL70: Sally Blair: this would result in the Cooling Mode eff. Of 16.3 EER & the heating mode eff. Of 3.1 COP.
Note on AM70: Sally Blair: this would result in the Cooling Mode eff. Of 12.1 EER & the heating mode eff. Of 2.5 COP.
Note on A71: Sally Blair: Ben, this table only shows up if "PTAC/PTHP" is selected in Eq Sizing Table above. Otherwise, user shouldn't see this at all (including title).
Note on AH71: 7/30/20: SIZE RANGE CHANGE ON 7/30 Ben, in Table 110.2-B, this would result in the Cooling Mode eff. Of 13.0 EER & the heating mode eff. Of 4.3 COP.
Note on AH72: Sally Blair: Ben, in Table 110.2-B, this would result in NO Cooling Mode eff. (ie, so grey that column out) & the heating mode eff. Of 2.90 COP.
Note on B74: October 2019 Update: Changed the units to kbtu/h
Note on E74: October 2019 Update: Changed the units to kbtu/h
Note on AF75: 2019 Update: For heating mode only, the dropdown choices in light purple would trigger two choices in the drop down for rating condition in column 03 of the Dry System Equipment Efficiency (other than PTAC and PTHP) subtable: - 47oFdb/43oFwb OSA - 17oFdb/15oFwb OSA Otherwise, column 03 stays grey & blank
Note on AH75: 2019 Update: For all sizes, if selected column 04 dropdown is "COP" and column 05 is "0.72" and column 07 is "COP" in the upper row and blank in the lower row & column 08 is "0.60" in the upper row & blank in the lower row.
Note on AI75: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Tabe C-3.
Note on AJ75: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AK75: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AL75: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-3
Note on AM75: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AN75: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AO75: NEEDS TO BE UPDATED IN FORM & SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "7.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. Table C-3
Note on A76: Sally Blair: Ben, anything designated as "PTAC/PTHP" transfers to this table. Everything else does not.
Note on C76: October 2019 Updates: Calculated field: PTHP: Newly constructed or newly conditioned- if column 02 < 7 = 3.3 if column 02 >=7 and <= 15 = 3.7 - (0.052 x column02) if column 02 > 15 = 2.9 PTHP: replacement- if column 02 < 7 = 2.7 if column 02 >=7 and <= 15 = 2.9 - (0.026 x column02) if column 02 > 15 = 2.5
Note on D76: Sally Blair: If nothing is entered in Column 10 above in the Sizing Table, columns 02-04 here grey out.
Note on F76: Ocotber 2019 Updates: Calculated field: PTHP: Newly constructed or newly conditioned- if column 05 < 7 = 11.9 if column 05 >=7 and <= 15 = 14 - (0.3 x column05) if column 05 > 15 = 9.5 PTHP: replacement- if column 05 < 7 = 9.3 if column 05 >=7 and <= 15 = 10.8 - (0.213 x column05) if column 05 > 15 = 7.6 PTAC: Newly constructed or newly conditioned- if column 05 < 7 = 11.9 if column 05 >=7 and <= 15 = 14 - (0.3 x column05) if column 05 > 15 = 9.5 PTAC: replacement- if column 05 < 7 = 9.4 if column 05 >=7 and <= 15 = 10.9 - (0.213 x column05) if column 05 > 15 = 7.7
Note on G76: Sally Blair: If nothing is entered in Column 11 above in the Sizing Table, columns 05-07 here grey out.
Note on AI76: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AJ76: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AK76: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AL76: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AM76: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AN76: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AI77: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AJ77: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AK77: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AL77: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AM77: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AN77: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AI78: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AJ78: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AK78: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AL78: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AM78: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AN78: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AI86: 6.29.21 Remove this option for 2022
Note on AK86: 6.29.21 Remove this option for 2022
Note on AH87: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.0"
Note on AJ87: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.0" & column 04 should be COP & column 05 should be "3.3"
Note on AH88: Sally Blair: Column 07 upper should be EER & Column 08 upper should be "10.0"
Note on AJ88: Sally Blair: Column 07 upper should be EER & Column 08 upper should be "10.0" & column 04 should be COP & column 05 should be "3.0"
Note on AH89: Sally Blair: Column 07 upper should be EER & Column 08 upper should be "10.0"
Note on AJ89: Sally Blair: Column 07 upper should be EER & Column 08 upper should be "10.0" & column 04 should be COP & column 05 should be "3.0"
Note on K91: 6.3.22 If anything other than "No Exceptions Apply" is selected, Minimum System Efficiency.. Is blank/gray
Note on D92: 12/2/21 if sum of rated input capacity >=1,000,000 excluding individual boilers < 300,000 System Efficiency = (sum (Rated Efficiency x input capacity))/ total input capacity of boilers > between 1million and 10 million btu/h else = gray/blank
Note on I92: 6.8.22 = 90% if sum of rated input capacity >=1,000,000 excluding individual boilers < 300,000 Else gray/blank
Note on I96: Sally Blair: If NA selected AND Col 03 Qty is greater than 1, Table D needs to return the Row 17 error on the Table D tab.
Note on J96: Sally Blair: If "NA: ≤ 500,000 Btu/h" selected AND rated capacity is EITHER >500,000 to 2,500,000 OR > 2,500,000 in Col 04, Table D needs to return the Row 18 error on the Table D tab.
Note on AH96: Sally Blair: Column 07 upper should be SEER & Column 08 upper should be "13.0"
Note on AH97: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.2" Column 07 lower should be IEER & Column 08 lower should be "15.5"
Note on AH98: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.0" Column 07 lower should be IEER & Column 08 lower should be "14.9"
Note on AH99: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "10.0" Column 07 lower should be IEER & Column 08 lower should be "13.9"
Note on AH101: Sally Blair: For heating mode only, the 3 selections highlighted in pink would trigger two choices in the drop down for rating condition: - 47oFdb/43oFwb OSA - 17oFdb/15oFwb OSA
Note on AH102: Sally Blair: If chosen, column 07 upper is "SEER" and column 07 lower is blank. Column 08 upper is "13.0" and column 08 lower is blank. AND column 04 is "HSPF" dropdown choice and column 05 is "7.7"
Note on AI102: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "12.0" and column 08 lower is "16.0". AND column 04 is "COP" dropdown choice and column 05 is "4.3"
Note on AJ102: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "16.2" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.6"
Note on AK102: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "13.4" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.1"
Note on AH103: 2019 Update: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "11.0" and column 08 lower is "14.6". AND column 04 is "COP" dropdown choice and column 05 is: "3.3" if column 02 is "47oFdb/43oFwb OSA" "2.25" if column 02 is "17oFdb/15oFwb OSA"
Note on AI103: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "12.0" and column 08 lower is "16.0". AND column 04 is "COP" dropdown choice and column 05 is "4.3"
Note on AJ103: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "13.8" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.3"
Note on AK103: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "11.0" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "2.8"
Note on AH104: 2019 Update: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.6" and column 08 lower is "13.9". AND column 04 is "COP" dropdown choice and column 05 is: "3.2" if column 02 is "47oFdb/43oFwb OSA" "2.05" if column 02 is "17oFdb/15oFwb OSA"
Note on AI104: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.0" and column 08 lower is "14.0". AND column 04 is "COP" dropdown choice and column 05 is "4.0"
Note on N105: 2019 Update: Remove these two dropdown choices from "Furnace + AC" & only use with "Furnace/ Unit heater"
Note on AH105: 2019 Update: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "9.5" and column 08 lower is "12.7". AND column 04 is "COP" dropdown choice and column 05 is: "3.2" if column 02 is "47oFdb/43oFwb OSA" "2.05" if column 02 is "17oFdb/15oFwb OSA"
Note on AI105: 2019 Update: New size category for 2019. If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.0" and column 08 lower is "12.0". AND column column 04 is "COP" dropdown choice and column 05 is "3.9"
Note on AH108: 6.29.21 This is the only instance where the "Efficiency Unit" under heating mode needs to be a dropdown. The two choices are: - AFUE - Et If "AFUE" chosen, column 05 is "0.78" If "Et" chosen, column 05 is "0.81"
Note on AI108: Sally Blair: If chosen, column 04 is "Ec" dropdown choice and column 05 is "0.80"
Note on AJ108: Sally Blair: If chosen, column 04 is "Ec" dropdown choice and column 05 is "0.80"
Note on AH109: 6.29.21 If chosen, column 04 is "Et" dropdown choice and column 05 is "0.82"
Note on AH112: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.81"
Note on AI112: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.80"
Note on AH115: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.75"
Note on AI115: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.65"
Note on AJ115: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.57"
Note on AK115: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.61"
Note on AH116: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.76"
Note on AI116: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.66"
Note on AJ116: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.58"
Note on AK116: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.66"
Note on AI117: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.67"
Note on AK117: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.67"
Note on AK118: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.68"
Note on AH120: 2019 Update: Divided all of these choices into "downflow" and "upflow"
Note on AH121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.2" in the upper row & blank in the lower row.
Note on AI121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.09" in the upper row & blank in the lower row.
Note on AJ121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.6" in the upper row & blank in the lower row.
Note on AK121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.49" in the upper row & blank in the lower row.
Note on AL121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.55" in the upper row & blank in the lower row.
Note on AM121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.44" in the upper row & blank in the lower row.
Note on AN121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.5" in the upper row & blank in the lower row.
Note on AO121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.39" in the upper row & blank in the lower row.
Note on AP121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.45" in the upper row & blank in the lower row.
Note on AQ121: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.34" in the upper row & blank in the lower row.
Note on AH122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.1" in the upper row & blank in the lower row.
Note on AI122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AJ122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.5" in the upper row & blank in the lower row.
Note on AK122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.39" in the upper row & blank in the lower row.
Note on AL122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.45" in the upper row & blank in the lower row.
Note on AM122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.34" in the upper row & blank in the lower row.
Note on AN122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.15" in the upper row & blank in the lower row.
Note on AO122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.04" in the upper row & blank in the lower row.
Note on AP122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.10" in the upper row & blank in the lower row.
Note on AQ122: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AH123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.9" in the upper row & blank in the lower row.
Note on AI123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.79" in the upper row & blank in the lower row.
Note on AJ123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.4" in the upper row & blank in the lower row.
Note on AK123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.29" in the upper row & blank in the lower row.
Note on AL123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.35" in the upper row & blank in the lower row.
Note on AM123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.24" in the upper row & blank in the lower row.
Note on AN123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.10" in the upper row & blank in the lower row.
Note on AO123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AP123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.05" in the upper row & blank in the lower row.
Note on AQ123: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.94" in the upper row & blank in the lower row.
Note on AH129: 2019 Update: Taking "/single package" out of this choice
Note on AI129: 01.09.20 Update: Completely new set of dropdowns and efficiencies.
Note on AM129: 2019 Update: Taking out "split/" in both of these choices.
Note on AH130: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AI130: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AH131: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AI131: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AL131: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AM131: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AH132: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AI132: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AL132: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AM132: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AH134: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AI134: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AM134: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AH135: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI135: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AM135: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11.2" F.08 Lower Row = "14.8"
Note on F136: Sally Blair: If the user chooses one of the exceptions (1-4) here, use "Path A" values/ units in cells 07/08.
Note on J136: Sally Blair: Sally Blair: Ben, if Path B says "NA", then lets use Path A values to document MM.
Note on AH136: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AI136: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AL136: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AM136: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on I137: Sally Blair: If there is only one value required by Table 110.2-D (ex. COP), then these three cells in 06/07/08 grey out.
Note on AH137: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI137: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AL137: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11" F.08 Lower Row = "14.2"
Note on AM137: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11" F.08 Lower Row = "14.2"
Note on AH138: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AI138: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AL138: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AM138: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AH139: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI139: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AL139: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "10" F.08 Lower Row = "13.2"
Note on AM139: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "10" F.08 Lower Row = "13.2"
Note on AH140: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AI140: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AL140: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AM140: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AH141: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI141: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AL141: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "9.7" F.08 Lower Row = "12.5"
Note on L142: Sally Blair: If NA selected AND Col 03 Qty is greater than 1, Table D needs to return the Row 19 error on the Table D tab.
Note on AH142: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AI142: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on M144: 2019 Update: Added new NA choice for new exception for Healthcare facilities.
Note on AH147: 2019 Update: These are new categories.
Note on AH148: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "11.0" in the upper row & blank in the lower row.
Note on AI148: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.0" in the upper row & blank in the lower row.
Note on AJ148: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.5" in the upper row & blank in the lower row.
Note on AK148: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.4" in the upper row & blank in the lower row.
Note on AL148: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.8" in the upper row & blank in the lower row.
Note on AM148: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AH149: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.9" in the upper row & blank in the lower row.
Note on AI149: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.6" in the upper row & blank in the lower row.
Note on AL149: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AM149: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "8.7" in the upper row & blank in the lower row.
Note on AH150: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.7" in the upper row & blank in the lower row.
Note on AI150: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.5" in the upper row & blank in the lower row.
Note on AH151: 2019 UPdate: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.4" in the upper row & blank in the lower row.
Note on AI151: 2019 UPdate: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AH152: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.0" in the upper row & blank in the lower row.
Note on AI152: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.4" in the upper row & blank in the lower row.
Note on AH156: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "13.7" in the lower row
Note on AI156: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "12.1" in the lower row
Note on AJ156: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.5" in the upper row & "11.8" in the lower row
Note on AK156: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AL156: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AH157: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.3" in the upper row & "13.7" in the lower row
Note on AI157: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.8" in the upper row & "12.0" in the lower row
Note on AH158: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.2" in the upper row & "13.4" in the lower row
Note on AI158: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.7" in the upper row & "11.9" in the lower row
Note on O159: 3.24.22 If DOAS is selectedd 04-11 gray out and no efficiency table is triggered.
Note on AH159: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.0" in the upper row & "13.3" in the lower row
Note on AI159: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.5" in the upper row & "11.7" in the lower row
Note on J160: 3.14.22 Lookup based on Table 110.2-K
Note on O160: 3.24.22 If DX-DOAS is selected the DX-DOAS table is triggered
Note on AH162: 2019 Update: These are all new categories for "Unitary AC/ Condensers" so these sizing dropdowns need to be added.
Note on AH163: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "12.2" in the lower row. From Table C-3
Note on AI163: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AJ163: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AK163: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.0" in the lower row. From Table C-3
Note on AL163: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AM163: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AN163: NEEDS TO BE UPDATED IN FORM AND SCHEMA If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AH164: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.7" in the lower row. From Table C-3
Note on AI164: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AJ164: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AK164: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AL164: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AM164: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AH165: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AI165: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AJ165: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AK165: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AL165: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AM165: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on F166: 3.14.22 Custom Dropdown when 02=Water Cooled
Note on AH166: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AI166: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AJ166: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AK166: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AL166: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AM166: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AH167: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AI167: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AJ167: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AK167: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AL167: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AM167: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AH168: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on F170: 3.14.22 Custom Dropdown when 02=Water Source Heat Pump
Note on AH171: Added 6/15/20: Ben, in Table 110.2-B, this would result in the Cooling Mode eff. Of 12.8 EER & the heating mode eff. Of 4.3 COP.
Note on AI171: Sally Blair: this would result in the Cooling Mode eff. Of 17.8 EER & the heating mode eff. Of 3.7 COP.
Note on AJ171: Added 6/15/20: this would result in the Cooling Mode eff. Of 13.9 EER & the heating mode eff. Of 3.2 COP.
Note on AK171: Added 6/15/20: this would result in the Cooling Mode eff. Of 10.4 EER & the heating mode eff. Of 3.7 COP.
Note on AL171: Added 6/15/20: this would result in the Cooling Mode eff. Of 16.1 EER & the heating mode eff. Of 3.1 COP.
Note on AM171: Added 6/15/20: this would result in the Cooling Mode eff. Of 11.9 EER & the heating mode eff. Of 2.5 COP.
Note on AH172: Sally Blair: Ben, in Table 110.2-B, this would result in NO Cooling Mode eff. (ie, so grey that column out) & the heating mode eff. Of 2.90 COP.
Note on AH176: 2019 Update: For all sizes, if selected column 04 dropdown is "COP" and column 05 is "0.72" and column 07 is "COP" in the upper row and blank in the lower row & column 08 is "0.60" in the upper row & blank in the lower row.
Note on AI176: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Tabe C-3.
Note on AJ176: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AK176: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AL176: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-3
Note on AM176: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AN176: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AO176: NEEDS TO BE UPDATED IN FORM & SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "7.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. Table C-3
Note on A177: 3.14.22 This table is triggered when Dual Fuel Heat Pump is selected in System Sizing Table above
Note on AI177: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AJ177: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AK177: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AL177: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AM177: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AN177: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AI178: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AJ178: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AK178: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AL178: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AM178: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AN178: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AI179: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AJ179: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AK179: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AL179: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AM179: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AN179: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on A181: 3.14.22 Bring in system name for DFHP systems
Note on E181: Sally Blair: This is only a dropdown if column 03 in Dry System Equipment Sizing table is any of the following: - "VRF heat pump, air cooled" - "Air cooled, split" - "Air cooled, split, space constrained" - "Air cooled, packaged" - "Air cooled, packaged, space constrained" Otherwise this cell greys out.
Note on G181: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on AH182: 6.3.22 Blank/Gray
Note on AI182: 6.3.22 2.08 COP
Note on AJ182: 6.3.22 2.01 COP
Note on AK182: 6.3.22 2.04 COP
Note on AL182: 6.3.22 1.86 COP
Note on AM182: 6.3.22 1.89 COP
Note on AN182: 6.3.22 1.82 COP
Note on AO182: 6.3.22 1.85 COP
Note on G183: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on AH183: 6.3.22 2.02 COP
Note on AI183: 6.3.22 2.05 COP
Note on AJ183: 6.3.22 1.97 COP
Note on AK183: 6.3.22 2.00 COP
Note on AL183: 6.3.22 1.83 COP
Note on AM183: 6.3.22 1.86 COP
Note on AN183: 6.3.22 1.78 COP
Note on AO183: 6.3.22 1.81 COP
Note on AH184: 6.3.22 1.92 COP
Note on AI184: 6.3.22 1.94 COP
Note on AJ184: 6.3.22 1.87 COP
Note on AK184: 6.3.22 1.89 COP
Note on AL184: 6.3.22 1.73 COP
Note on AM184: 6.3.22 1.75 COP
Note on AN184: 6.3.22 1.68 COP
Note on AO184: 6.3.22 1.70 COP
Note on F186: Sally Blair: This needs to be a custom dropdown which only includes the unit relevant to the equipment type chosen. There's only one instance where they get to choose- Warm Air Central Furnace, Gas fired.
Note on AH187: 6.3.22 2.38 COP
Note on AI187: 6.3.22 2.41 COP
Note on AJ187: 6.3.22 2.33 COP
Note on AK187: 6.3.22 2.36 COP
Note on AL187: 6.3.22 1.97 COP
Note on AM187: 6.3.22 2.00 COP
Note on AN187: 6.3.22 1.92 COP
Note on AO187: 6.3.22 1.95 COP
Note on AH188: 6.3.22 2.38 COP
Note on AI188: 6.3.22 2.31 COP
Note on AJ188: 6.3.22 2.23 COP
Note on AK188: 6.3.22 2.26 COP
Note on AL188: 6.3.22 1.93 COP
Note on AM188: 6.3.22 1.98 COP
Note on AN188: 6.3.22 1.88 COP
Note on AO188: 6.3.22 1.93 COP
Note on AH189: 6.3.22 2.18 COP
Note on AI189: 6.3.22 2.20 COP
Note on AJ189: 6.3.22 2.13 COP
Note on AK189: 6.3.22 2.16 COP
Note on AL189: 6.3.22 1.78 COP
Note on AM189: 6.3.22 1.81 COP
Note on AN189: 6.3.22 1.73 COP
Note on AO189: 6.3.22 1.76 COP
Note on H209: Update 9.29.20: Updated code reference numbers for 08-10
Note on I211: Sally Blair: Grey out if anything other than open-circuit towers is selected in 02.
Note on K211: Sally Blair: Grey out if anything other than open-circuit towers is selected in 02.
Note on L211: Sally Blair: grey out if "Air cooled condenser" is selected in column 02
Note on B214: 2019 Update: two new options added for 2019
Note on B223: Updated 9.29.20: If Waterside Economizer chosen, grey and blank columns 03-10.
Note on E228: Sally Blair: If any choice is selected, Table D needs to return the Row 20 error on the Table D tab.

## G. Pumps
| User input |  |  | auto calculated |  |  | From another Table | From look up table
G. PUMPS
[d:OnlyUI] Table Instructions: Complete the following pump schedule to show compliance with Prescriptive hydronic system requirements found in §140.4(k)& §170.2(c)4I applicable to pumps < 5hp. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with Prescriptive hydronic system requirements found in §140.4(k) & §170.2(c)4I applicable to pumps < 5hp. [d:/OnlyRG]
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Name or Item Tag | Equipment Type | Qty | HP | Controls per §140.4(k) & §170.2(c)4I
|  |  |  | Variable Flow | Hydronic Heat Pump Isolation | VSD on Pumps > 5HP | Differential Pressure Sensor
| Dropdown |  |  | Dropdown | Dropdown | Dropdown | Says "Required" if 07 says "Yes"
|  |  |  | Reset | Add Row | Remove Last
Equipment Type
| Primary chilled water |  |  | VF Dropdown | WLHP Dropdown | VSD Dropdown
| Secondary chilled water |  |  | Yes | Yes | Yes
| Primary heating hot water |  |  | NA: < 3 control valves | NA: Not connected to common water loop | NA: Not serving variable flow system
| Secondary heating hot water |  |  | NA: pump system < 1.5 hp | NA: No hydronic heat pump | NA: Condenser water serving only water-cooled chillers
Tertiary heating hot water
Condenser water
Note on E8: Sally Blair: Grey out if user selects "condenser" in column 02 because this only applies to CHW and HHW
Note on F8: Sally Blair: Grey out user chooses either CHW or HHW in column 02.
Note on G8: Sally Blair: grey out if < 5 hp in column 04 OR if HHW selected in column 02

## H. Fan Systems (LMCC)
Note - THIS WHOLE TABLE IS NEW FOR 2022 |  |  |  | Note - This table is showing two fans as an example. You can have multiple fans per fan system, and you can have multiple fan systems within the table.
H. FAN SYSTEMS & AIR ECONOMIZERS
[d:OnlyUI] Table Instructions: Complete the following Table for fan systems to demonstrate compliance with prescriptive requirements found in §140.4(c), §140.4(e) §140.4(m) §170.2(c)3 & §170.2(c)4A. Fans serving covered process systems such as computer rooms are exempt. First document the system details, then add fans within that system to document compliance with fan power requirements. Fan systems serving healthcare facilities, or those serving only process loads, are exempt from these requirements and do not need to be included in Table H. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with prescriptive requirements found in §140.4(c), §140.4(e) §140.4(m), §170.2(c)3 & §170.2(c)4A for fan systems. Fan systems serving only process loads are exempt from these requirements and do not need to be included in Table H. [d:/OnlyRG]
System Name: |  | Quantity |  | Fan System Status: | Dropdown | System Zoning | Dropdown | Serving Dwelling Units | Dropdown | Fan System Airflow |  | Site Elevation |  | Economizer | Dropdown
01 | 02 | 03 | 04 | [5 empty] | 05 | 06 | 07 | 08 | 09 | 10 | 11
|  | Qty | Components | [5 empty] | Airflow Through Component (%) | Water Gauge (w.g) | Allowance |  | Design
Fan Name or Item Tag | Fan Type | [9 empty] | Component Allowance | Fan Allowance(watt/cfm)3 | Design Electrical Input Power Method | Motor Nameplate Horsepower | Design Electrical Input Power (kW)
(fan 1) | dropdown |  | Dropdown (component 1) | [7 empty] | component 1 allowance | Fan Allowance | Dropdown | Dropdown
|  |  | (component2) | [7 empty] | component 2 allowance
(fan 2) | dropdown |  | Dropdown (component 1) | [7 empty] | component 1 allowance | Fan Allowance | Dropdown | Dropdown
|  |  | (component2) | [7 empty] | component 2 allowance
[9 empty] | Fan System Allowance(kW)3 |  |  |  | Fan System Electrical Input Power (kW)
1 Fans serving spaces with design background noise goals below NC35
2 Low-turndown single-zone VAV fan system must be capable of and configured to reduce airflow to 50 percent of design airflow and use no more than 30 percent of the design wattage at that airflow. No more than 10 percent of the design load served by the equipment shall have fixed loads.
3 Fan system allowance includes fan system base allowance
4 Filter pressure loss can only be counted once per fan system
5 Complex Fan System means a fan system that combines a signle cabinet fan system with other supply fans, exhaust fans, or both
6 FOOTNOTE: Computer room economizers must meet requirements of §140.9(a) and will be documented on the NRCC-PRC-E document. | [7 empty] | Serving Dwelling Units | [5 empty] | Economizer Dropdown
| Fan Type |  |  | Fan System Status |  | System Zoning |  | Serving Individual Dwelling Unit | [5 empty] | Fixed Temperature
| supply |  |  | New |  | DOAS <1.0 kW |  | Serving Multiple Dwelling Unit | [5 empty] | Fixed Enthalpy
| relief |  |  | Altered |  | multizone VAV systems |  | Not Serving Dwelling Units | [5 empty] | Differential Temperature
| exhaust |  |  |  |  | all other systems | [7 empty] | Differential Enthalpy
| return | [12 empty] | Waterside Economizer (See Tbl. F)
| transfer | [12 empty] | NA: < 33 kBtu/h cooling
|  |  |  | Components Dropdown (Status = New) |  |  |  |  | Use Tables 140.4-A and 140.4-B | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1404prescriptiverequirementsforspaceconditioningsystems.htm#cfansystems1.htm |  |  |  | NA: Special OA filtration
|  |  |  | System serving spaces ≤ 6 floors away |  |  |  |  | Options for Supply Fan in H.02 |  |  |  |  | NA: Multifamily
|  |  |  | System serving spaces > 6 floors away | [9 empty] | NA: Efficiency per Table 140.4-D
|  |  |  | MERV 13 to MERV 16 Filter upstream of thermal conditioning equipment | [9 empty] | NA: System operates @ 100% OSA
|  |  |  | MERV 13 to MERV 16 Filter downstream of thermal conditioning equipment | [9 empty] | NA: DOAS with EAHR
|  |  |  | Filtration allowance for > MERV 16 or HEPA Filter | [9 empty] | See NRCC-PRC for details6
|  |  |  | Central Hydronic heating coil | [9 empty] | NA: Altered other than packaged AC or HP< 54kBty/h
|  |  |  | Electric heat | [9 empty] | NA: Controlled Environment Horticulture
Gas heat
|  |  |  | Hydronic/DX cooling coil or heat pump coil | [6 empty] | Method Dropdown | Nameplate
|  |  |  | Solid or liquid Desiccant system allowance | [6 empty] | default per Table 140.4-D Variable Speed Drive | ≥1 and <1.5
|  |  |  | Reheat Coil for Dehumidification | [6 empty] | default per Table 140.4-D | ≥1.5 and <2
|  |  |  | Evaporative humidifier/cooler in series with a cooling coil | [6 empty] | manufacturer provided | ≥2 and <3
|  |  |  | 100% outdoor air system | [7 empty] | ≥3 and <5
|  |  |  | Energy recovery 0.50 <= ERR < 0.55 | [7 empty] | ≥5 and <7.5
|  |  |  | Energy recovery 0.55 ≤ ERR <0.60 | [7 empty] | ≥7.5 and <10
|  |  |  | Energy recovery 0.60 ≤ ERR <0.65 | [7 empty] | ≥10 and <15
|  |  |  | Energy recovery 0.65 ≤ ERR <0.70 | [7 empty] | ≥15 and <20
|  |  |  | Energy recovery 0.70 ≤ ERR <0.75 | [7 empty] | ≥20 and <25
|  |  |  | Energy recovery ERR ≥ 0.80 | [7 empty] | ≥25 and <30
|  |  |  | Runaround Loop | [7 empty] | ≥30 and <40
|  |  |  | Gas phase filtration | [7 empty] | ≥40 and <50
|  |  |  | Economizer Return Damper | [7 empty] | ≥50 and <60
|  |  |  | Air blender | [7 empty] | ≥60 and <75
|  |  |  | Sound attenuation section1 | [7 empty] | ≥75 and ≤100
System feeds a terminal unit with a fan with electrical input power < 1kW
Low-turndown single-zone VAV fan systems2
|  |  |  | Filter (any MERV value)4 |  |  |  |  | Options for Exhaust, Return, Relief, Transfer in H.02
Energy Recovery 0.50 ≤ ERR <0.55
Energy Recovery 0.55 ≤ ERR <0.60
Energy Recovery 0.60 ≤ ERR <0.65
Energy recovery 0.65 ≤ ERR <0.70
Energy Recovery 0.70 ≤ ERR <0.75
Energy Recovery 0.75 ≤ ERR <0.80
Energy Recovery >= 0.80
Coil Runaround Loop
Fully Ducted, or Systems that maintain air pressure differential between rooms
Airflow control devices required for space pressurization control
Laboratory and vivarium exhaust system with vertical ducts > 75 ft2
Biosaftey Cabinet
Filters, scrubber or other exhaust treatment
Sound attenuation section
|  |  |  | Additional Component for replacement Fan Systems (this list should be added to the one above used for new systems |  |  |  |  | Use table 141.0-D | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1410additionsalterationsandrepairstoexistingnonresidentia.htm#table1410dadditionalfanpowerallowances.htm
|  |  |  | Supply Fan System |  |  |  |  | Options for Supply Fan in H.02
Supply Fan In-Unit with Adapter Curb
|  |  |  | Exhaust/Relief/Return/Transfer Fan System |  |  |  |  | Options for Exhaust, Return, Relief, Transfer in H.02
Exhaust/Relief/Return/Transfer In-Unit with Adapter Curb
Note - THIS TABLE IS BRAND NEW FOR 2022
H. DWELLING UNIT FAN EFFICACY & ENERGY/HEAT RECOVERY 170.2(c)3B
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Fan System Name or Item Tag | Qty | Serving Dwelling Units | Forced Air System | System Airflow (cfm) | Design Power (kW) | Design Watts/CFM §170.2(c)3b | Maximum Watts/CFM §170.2(c)3b | 1ERV/HRV 170.2(c)3biv | Design Sensible Recovery/Effectiveness | 1Required Senisble Recovery/Effectiveness §170.2(c)3biv
Transfers from Fan And Air Economizer Table | autopopulated from Table H Fan System Quantity | Transfers from Fan And Air Economizer Table (Serving Dwelling Units) | dropdown |  |  |  |  | dropdown
1 CFI = Central Fan Integrated Dwelling Unit
|  |  | System Type Dropdown |  |  |  |  | ERV/HRV Dropdown
|  |  | Gas Furnace Air Handling Units |  |  |  |  | ERV Provided
|  |  | All Other Air Handling Units |  |  |  |  | HRV Provided
|  |  | Not Central Forced AHU |  |  |  |  | NA: CZ 3-10
NA: Continuously operating supply/exhuast
Note - THIS TABLE IS BRAND NEW FOR 2022
H. EXHAUST AIR HEAT RECOVERY 140.4(q), 170.2(c)4o
01 | 02 | 03 | 04 | 05 | 06 | 07 |  | 08 | 09 | 10 | 11
Fan System Name | Qty | Hours of Operation Per Year | Design Supply Airflow Rate | Outdoor Airflow | % Outdoor Air at Full Design Airflow | Exemptions to Exhaust Air Heat Recovery Requirement per §140.4(q) & §170.2(c)4o |  | Exhuast Air Heat Recovery §140.4(q) & §170.2(c)4o | Type Of Heat Recovery Rating | Required Recovery Ratio | Energy Recovery Bypass
Populated from Table H Fan System Name | Autopopulated from Fan System Quantity | Dropdown | [6 empty] | Dropdown | "60%" or "50%" | Dropdown
Hours of Operation Dropdown
|  | >= 8,000 |  |  |  | Exemptions Dropdown |  |  | Type Dropdown |  | Bypass Dropdown
|  | <8,000 |  |  |  | No Exemptions Apply |  |  | Sensible Energy Recovery Ratio |  | Energy Recovery Bypass or similar control Installed per 140.4(q)2
[6 empty] | NA: Process system serving laboratory and/or factory exhaust |  |  | Enthalpy Recovery Ratio |  | NA: DOAS unit with shut-off capabilities per 140.4(q)2
NA: Serving space not cooled and heated to <60F
NA: >60% outdoor air heating energy provided by site recovered energy in CZ 16
NA: Total airflow exhuasted and relieved within 20ft < 75% per Exception 6 to 140.4(q)
NA: Operating < 20 hours/week
Note - THIS TABLE IS BRAND NEW FOR 2022
Dedicated Outdoor Air System (DOAS)
01 |  | 03 | 04 | 05 | 06
System Name | Quantity | Delivered Directly To The Space | DOAS Fan Control | Multi-Zone DOAS with Cooling §140.4(p)4 & §170.2(c)4N | MF DOAS
|  | Dropdown | Dropdown | Dropdown | DOAS
|  | Delivery Dropdown | Fan Control Dropdown | Multi-zone DOAS dropdown | DOAS Dropdown
|  | Yes | >=3 speeds | No heating or heat recovery to warm supply air > 60F when majority of zones require cooling | Not Serving Multifamily Common Use Space
|  | NA: Active Chilled Beam System |  | NA: No Mechanical cooling and heating | Option 1 - 170.2(c)Nia
|  | Exception 2 per 140.4(p)2/170.2(c)4N |  | NA: Single Zone | Option 3 - 170.2(c)Nib
|  | NA: Exception 3 per 140.4(p)2/170.2(c)4N |  |  | Option 3 - 170.2(c)Nic
H. Fan Energy Index (FEI)
01 | 2 |  | 3
Name or Item Tag | FEI Exception |  | FEI
FEI Dropdown
None Applies
Embedded Fan Regulated under 110.2 or 110.1
Computer Room Air Conditioners
DX-DOAS Unit
Embedded Fan < 5HP or < 4.1 kW
Circulating Fan, Ceiling Fan, Air Curtain
Operates Only During Emergencies
Note on A5: April 2020 Update: Language in the last sentence has been revised to remove language about healthcare.
Note on J6: 4/6/22 If this = "Serving Individual"OR "Serving Multiple" THEN H.01-H.12 AND Fan System Airflow, Site Elevation and Economizer = gray/blank out AND System Name transfers to H.01 of the Dwelling Unit Fan Efficacy
Note on N6: 3.25.22 If >=3,000 feet use the correction factors of Table 140.4C
Note on K11: 8/3/21 Grays out unless H.04= any of the following: - "Evaporative humidfier/cooler in a series…." - "Gas Phase filtration" - Laboratory or Vivarium - Biosaftey Cabinet - Filters, scrubber or other exhaust treatment
Note on L11: 8.3.21 NOTE - One of the allowances in Table 170.2-C is only for highrise and should not be included in the logic here. I have removed it from the components list to the left. = allowance from either Table 140.4-A & 140.4-B. Table and column determined by H.02 Fan Type, H.03 System Zoning and System Airflow Use Equation 140.4-A if H.05 is not "100" If H.07 is not gray,H.08 = the value from H.05 * H.07
Note on M11: 8.3.21 = sum for fan all components (H.05 x H.07)
Note on O11: 8.3.21 Gray unless H.09 = default per 140.4-D
Note on P11: 8/3/21 User input if H.09 Method = "manufacturer provided", ELSE automatically calculated based on H.10 selections using Table 140.4-D
Note on L13: 2019 Update: Add Pressure Adj Device duplicates coulumns 07 & 08 (but blank). Remove Last Pressure Adj Device removes the last row added.
Note on L19: 6.20.22 If fan system electrical input power < 1.0 then Fan System Allowance = blank/grayed out Else = total of fan allowances * their quantity * Fan System Airflow / 1,000 AND If elevation in Table A > 3,000. Multiply * correction factor in Table 140.4-C NOTE: Healthcare facilities have an additional allowance in Table 140.4-B that should be added automatically if Table A includes Healthcare Facility. User will not select this allowance in H.05 ALSO - Base allowances can only be selected once per fan system Base allowances are the first tow options "serving spaces <= or > 6 floors..."
Note on P19: 8.3.21 - sum of design electrical input powers * their quantity
Note on G27: 4/26/22 If selected, 02, 04, 05, 06 07 08 grey out and fan system allowance = fan system allowance/1000
Note on R27: April 2020 Update: When the user selects 'NA: System Servers Healthcare Facility H.01 - H.08 for that system type should gray out.The questions in row 5 of the mock-up should all stay ungrayed as normal.
Note on E28: 3.30.22 If altered is selected the components dropdown also includes the replacement components and allowances in addition to the new components/allowances.
Note on E32: 10/13/21 User can select all that apply
Note on A82: Ben Lalor: Triggers when B.03 = Fan Systems AND A.03 = Multifamily
Note on G86: 11/30/21 =(06/ 1,000) /05
Note on H86: 6.8.22 System Zoning = "multiple dwelling units" AND A.02 = 4-10 AND ERV/HRV= "NA" = 0.4 if H.03 = "Individual.." AND A.02 = 1, 2, or 11-16 AND H.04 ="Not Central Forced Air.." AND ERV/HRV="Provided" = 0.60 If H.03 = "Individual..." AND H.04 = "All Others" = .58 If H.03 = "Indivudual..." AND H.04 = "Gas Furnace" = .45 Else , H.05, H.06, H.07 adn H.08= blank/grayed out
Note on K86: 4.6.22 = 67% if 09 = Provided Else = blank/grayed out
Note on A102: 6.29.21 Doesn't trigger for Climate Zones 6 and 7, otherwise triggers when Fan Systems are selected in Table B
Note on C106: 8/2/21 Determines which table should be used - 140.4-J or 140.4-K
Note on F106: 3.25.22 = 05 / 06
Note on G106: 7/30/21 If any of the exemptions here are selected, 07 says "Not Required" and 02, 03, 08 09 10 gray out EXCEPT if they use CZ exception special text shows in 08. See logic there.
Note on I106: 6/8/22 Use Table 140.4-H or 140.4-I to determine if EAHR is required or not. Exemptions in H.07 override the tables. If required and heating or cooling exemption not used in H.07, show the appropriate option below. Either: - "Required for both heating and cooling design conditions" - "Not Required" Used this text for heating or cooling exemption in H.07 - "Required for heating design conditions" - "Required for cooling design conditions"
Note on K106: 8/2/21 60% if H.08 = "Sensible" 50% if H.08 = "Enthalpy"
Note on L106: 4/6/22 "60%" if H.09 = Sensiible "50%" if H.09 = Enthalpy
Note on A124: 3.4.22 Triggers when DOAS is selected in Table F
Note on A128: Ben Lalor:
Note on A146: Ben Lalor: Transferred from H.01 Fan and Air Economizer
Note on D146: 5/3/22 This grays out if anything but "None Applies" is selected in column 2.

## I. Sys Controls (LMCC)
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
I. SYSTEM CONTROLS
[d:OnlyUI] Table Instructions: Complete the following Table to demonstrate compliance with mandatory controls in §110.2 and §120.2 and prescriptive controls in §140.4(f) §140.4(n) §170.2(c)4D, & §170.2(c)4L or requirements in §141.0(b)2E & §180.2(b)2 for altered space conditioning systems. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory controls in §110.2 and §120.2 and prescriptive controls in §140.4(f) and (n) or requirements in §141.0(b)2E for altered space conditioning systems. [d:/OnlyRG]
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
System Name | System Zoning | Conditioned Floor Area Being Served (ft2) | Thermostats §110.2(b), (c)1, §120.2(a), §160.3(a)2a or §141.0(b)2E & §180.2(b)2 | Shut-Off Controls §120.2€ & §160.3(a)2d | Isolation Zone Controls §120.2(g) & §160.3(a)2f | Demand Response §110.12, §120.2(b) & §160.3(a)2b | Supply Air Temp. Reset §140.4(f) & §170.2(c)4d | Window Interlocks per §140.4(n) & §170.2(c)4d | Direct Digital Control (DDC) per 110.12
| See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown
1 FOOTNOTES: Gravity gas wall heaters, gravity floor heaters, gravity room heaters, non-central electric heaters, fireplaces or decorative gas appliances, wood stoves are not required to have setback thermostats.
* NOTES: Controls with a * require a note in the space below explaining how compliance is achieved.
[6 empty] | Reset | Add System | Remove Last
| System Zoning Dropdown | CFA dropdown | Thermostat Dropdown | Shut Off Dropdown | Isolation Zone Dropdown | Demand Response Dropdown | SA Temp Reset Dropdown | Window Interlock Dropdown | DDC Dropdown
| single zone | < 25,000 ft2 | Setback Thermostat | Auto Timeswitch | Auto Timeswitch | EMCS | Included | Provided | Provided
| multi-zone | > 25,000 ft2 | EMCS | Occ. Sensor | Occ. Sensor | DR Tstat per §110.12 | NA: Alteration | NA: Auto-closing doors | NA: Single Zone
| multi-zone w/ DDC to zone | NA: Altered per §141.0(b)2E | Setback + DR Tstat per §110.12 | 4 Hour Timer | 4 Hour Timer | Other* | NA: Single Zone | NA: No thermostatic control
|  |  | NA: Room AC/ heat pump | EMCS | EMCS | NA: PTAC, PTHP, Rm AC, HP | NA: Healthcare only | NA: Alteration project
|  |  | NA: Eq. type per §110.2(c) exception1 | Card Key (hotel/motel) | Other* | NA: Healthcare only | Exempt* | NA: No operable windows
|  |  |  | Other* | NA: Continuous Heat/Cool | NA: Serves temp. sensitive process | NA: Would increase energy use | NA: Healthcare only
|  |  |  | NA: 7 day per §120.2(e)1 | NA: Altered per §141.0(b)2E |  | NA: Serves humidity sensitive process | NA: HRR dwelling unit
|  |  |  | NA: Altered per §141.0(b)2E | NA: Single Zone |  | NA: Controls prevent reheat/recool/simultaneous
|  |  |  | NA: Healthcare only | NA: Serves < 25k ft2 |  | NA: dwelling unit
|  |  |  | NA: HRR dwelling unit | NA: dwelling unit
Note on D6: 2019 Update: Added S120.2(a)
Note on G6: 2019 UPDATE: Changed section reference to S110.12 & S120.2(b)
Note on G17: Usability Update: Changed wording
Note on D18: 2019 UPDATE: Removed JA5 choice & NA: Rm AC/HP, added NA: Eq. type option.
Note on G18: Sally Blair: Remove as part of 2022 update. Replace with new NA choices in pink
Note on G19: Usability Update: changed wording
Note on H19: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on F20: Sally Blair: Remove as part of 2022 update. Don't need to replace with any other NA: choices.
Note on G20: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on H20: Sally Blair: Remove as part of 2022 update. Replace with new NA choices in pink
Note on E21: Sally Blair: Remove as part of 2022 update. Don't need to replace with any other NA: choices.
Note on I21: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on E22: Usability Update: Changed wording
Note on I22: 2019 UPDATE: Added exemption for HRR
Note on E24: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on H24: Usability Update: Added new "NA" choice
Note on E25: Usability Update: Added new "NA" choice
Note on F25: Usability Update: Added new "NA" choice

## J. Ventilation (LMCC)
|  | User input |  | auto calculated |  |  |  | From another Table |  |  | From look up table
J. VENTILATION AND INDOOR AIR QUALITY
[d:OnlyUI] Table Instructions: Complete the following Table to demonstrate compliance with mandatory and prescriptive ventilation requirements in §120.1, §120.2(e)3B, 140.4(p) and 140.4(q) for all nonresidential and 160.2, 160.3(a)3D, 170.2(a)4N, 170.2(a)4O for high-rise residential occupancies. For alterations, only ventilation systems being altered within the scope of the permit application need to be documented in this table. In lieu of this table, the required outdoor ventilation rates and airflows may be shown on the plans or the calculations can be presented in a spreadsheet. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory ventilation requirements in §120.1 and §120.2(e)3B for all nonresidential, high-rise residential and hotel/motel occupancies. For alterations, only ventilation systems being altered within the scope of the permit application need to be documented in this table. In lieu of this table, the required outdoor ventilation rates and airflows may be shown on the plans or the calculations can be presented in a spreadsheet. [d:/OnlyRG]
01 | ¨ | Check the box if the project is showing ventilation calculations on the plans, or attaching the calculations instead of completing this table.
02 | ¨ | Check this box if the project includes Nonresidenital, Hotel/Motel spaces or Multifamily Common Use Spaces |  |  |  | Check this box if the project includes new or altered high-rise residential multifamily dwelling units |  |  |  | ¨
03 | ¨ | Check the box if the project is using natural ventilation in any nonresidential spaces to meet required ventilation rates per §120.1(c)2.
Nonresidential Hotel/ Motel and Multifamily Common Use Ventilation Systems
04 |  |  | 05 |  |  | 06 |  |  | 07
System Name: |  |  | System Design OA CFM Air Flow1 |  |  | System Design Transfer Air CFM |  |  | Air Filtration per §120.1(c), §141.0(b)2, 160.2(c)1 and 2
See dropdown
08 | 09 |  | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  | CHECK FIGURES | WARNINGS
Space Name or Item Tag | Mechanical Ventilation Required per §120.1(c)33 & §160.2(c)3 | [5 empty] | Exh. Vent. per §120.1(c)4 & §160.2(c)4 |  | DCV or Occupant Sensor Controls per §120.1(d)3, §120.1(d)5 & §120.2(e)36, §160.2(c)5d, §160.2(c)5e & §160.2(c)diii
| Occupancy Type4 |  | Conditioned Floor Area (ft2) | # of showerheads/ toilets | # of people5 | Required Min OA CFM | Required Minimum CFM | Provided per Design CFM
| See dropdown | [7 empty] | DCV | See dropdown
[9 empty] | Occ Sensor | See dropdown
[8 empty] | Reset | Add Occupancy Type | Remove Last
17 | Total System Required Min OA CFM |  |  |  |  | sum of col 13 for all spaces in system | 18 | Ventilation for this System Complies? |  | "Yes"/ "No"
1 FOOTNOTES: System CFM should include both mechanical and natural ventilation for the zone/system. | [7 empty] | Reset | Add System | Remove Last
2 Air filtration requirements apply to the following three system types per §120.1(c)1A: space conditioning systems utilizing ducts to supply air to occupiable space; supply-only ventilation systems providing outside air to occupiable space; supply side of balanced ventilation systems including heat recovery and energy recovery ventilation systems providing outside air to occupiable space.
3 Uniform Mechanical Code may have more stringent ventilation requirements; the most stringent code requirement takes precedence.
4 See Standards Tables 120.1-A and 120.1-B.
5 For lecture halls with fixed seating, the expected number of occupants shall be determined in accordance with the California Building Code.
6 §120.2(e)3 requires systems serving rooms that are required by §130.1(c) to have lighting occupancy sensing controls to also have occupancy sensing zone controls for ventilation. Examples of spaces which require lighting occupancy sensors include offices 250ft2 or smaller, multipurpose rooms less than 1,000ft2, classrooms, conference rooms, restrooms, aisles and open areas in warehouses, library book stack aisles, corridors, stairwells, parking garages, and loading and unloading zones, unless excepted by §130.1(c).
Multifamily Dwelling Unit Ventilation Systems
¨ | Check the box if the system is using continuous ventilation to meet the ventiliation requirements per §120.1(b)2Aivb & §160.2(b)2Aivb2
19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 |  | 27
Space Name or Item Tag | Mechanical Ventilation Required per §120.1(b)2 & §160.2(b)2 |  |  |  | Ventilation per Design |  | Local Exhaust |  | Air Filtration per §120.1(b)3 120.1(c) & §160.2(b)1
| Conditioned Floor Area (ft2) | # bedrooms | # dwelling units | Required Min OA CFM 1 | Supply Air CFM | Exhaust CFM
[7 empty] | ¨ | Bathroom/Kitchen IAQ | See dropdown
[7 empty] | ¨ | Bathroom/Kitchen IAQ & Vent.
[7 empty] | ¨ | Kitchen Range Hood 2
| 125 | 5 | 10 | 487.5 |  |  | ¨ | Bathroom/Ktichen IAQ | See dropdown
[7 empty] | ¨ | Bathroom/Ktichen IAQ & Vent.
[7 empty] | ¨ | Kitchen Range Hood 2
28 | Is this a balanced system? 4 |  |  | Yes/No | 29 | Meeting Outside Air Requirements? |  |  |  | Yes/ No
1 FOOTNOTES: Uniform Mechanical Code may have more stringent ventilation requirements; the most stringent code requirement takes precedence. | [7 empty] | Reset | Add Space | Remove Last
2 Kitchen range hood will be verified per NA7.18.1 to confirm model is rated by HVI or AHAM.
3 Air filtration requirements apply to the following three system types per §120.1(b)1A: space conditioning systems utilizing ducts to supply air to occupiable space; supply-only ventilation systems providing outside air to occupiable space; supply side of balanced ventilation systems including heat recovery and energy recovery ventilation systems providing outside air to occupiable space.
4 A balanced ventiltion system provides ventilation airflow to each dwelling-unit at a rate equal to or greater than the required minimum rate, but not more than twenty percent greater.
|  | Column 09- Occupancy Type Dropdown | cfm/ft2 for column 13 calc | cfm/ft2 for column 14 calc | cfm/ft2 for column 13 calc DCV |  |  |  | Column 07- Air filtration dropdown
|  | All others | 0.15 | #NAME? |  |  |  |  | Provided per §120.1(c) (NR & Hotel/Motel)
|  | Art Classroom | 0.15 | 0.7 |  |  |  |  | Provided per §141.0(b)2c (alteration)
|  | Assembly- multiuse | 0.5 | [5 empty] | NA: Not system type specified in Table J footnote 2
|  | Auditorium seating | 1.07 |  | 0.15
|  | Auto-repair room | 0.15 | 1.5 | [5 empty] | Coulmn 16- DCV Dropdown
|  | Bank or bank lobby | 0.15 | [6 empty] | Provided per §120.1(d)4
|  | Bank Vault/safe deposit | 0.15 | [6 empty] | NA: Not required per §120.1(d)3
|  | Bar/ cocktail lounge | 0.5 |  | 0.2 |  |  |  |  | NA: Continously occupied and high density; healthcare/medical facility/social services building
|  | Barbershop | 0.4 | 0.5 | [5 empty] | NA: Space exhaust is > design ventilation rate exception
|  | Barracks sleeping area | 0.15 | [6 empty] | NA: Processes that generate dust, fumes, etc.& no local exhaust
|  | Beauty/ nail salon | 0.4 | 0.6 | [5 empty] | NA: Area <150 ft2 or design occupancy < 10 people
|  | Bedroom/Living room (hotel/motel/dorm) | 0.15 | [6 empty] | NA: Area <1,500 ft2 +Occ Sensor provided
|  | Bowling alley (seating) | 1.07 |  | 0.15
|  | Break room | 0.5 |  | 0.15 |  |  |  |  | Column 16- Occ Sens Dropdown
|  | Cafeteria/ fast-food dining | 0.5 |  | 0.15 |  |  |  |  | Provided per §120.1(d)5
|  | Cells with toilet | 0.15 | 1 | [5 empty] | NA: Continously operated per §120.2(e)3 exception
|  | Classroom (age 5-18) | 0.38 |  | 0.15 |  |  |  |  | NA: System < 2kW demand + manual shutoff per §120.2(e)3 exception
|  | Coffee station | 0.5 |  | 0.15 |  |  |  |  | NA: Hotel/ motel + manual shutoff per §120.2(e)3 exception
|  | Coin-operated Laundry | 0.3 | [6 empty] | NA: DCV provided
|  | Computer (not printing) | 0.15 | [6 empty] | NA: Not required space type
|  | Computer Lab | 0.15
|  | Conference/ meeting | 0.5 |  | 0.15
|  | Copy/ printing room | 0.15 | 0.5
|  | Corridor | 0.15 | [6 empty] | Column 27- Air filtration dropdown
|  | Courtroom | 0.19 |  | 0.15 |  |  |  |  | Provided per §120.1(b)
|  | Darkroom | 0.15 | 1 | [5 empty] | Provided per §141.0(b)2c (alteration)
|  | Daycare (through age 4) | 0.21 |  | 0.15 |  |  |  |  | NA: Evaporative Cooler
|  | Daycare Sickroom | 0.15
|  | Disco/ dance floor | 1.5 |  | 0.15
|  | Gambling casino | 0.68 |  | 0.15
|  | Game arcade | 0.68 |  | 0.15
|  | General Manufacturing- non chemical | 0.15
|  | Gym/ sports arena (play area) | 0.5 | 0.5 | 0.15
|  | Health club/ aerobics | 0.15
|  | Health club/ weight room | 0.15
|  | Janitor closet | 0.15 | 1
|  | Kitchen (cooking) | 0.15 | 0.7
|  | Kitchenettes | 0.15 | 0.3
|  | Laundry (soiled storage) | 0.15 | 1
|  | Laundry room (central) | 0.15
|  | Laundry room (dwelling unit) | 0.15
|  | Lecture Hall (fixed seats) |  |  | 0.15
|  | Lecture/ postsecondary classroom | 0.38 |  | 0.15
|  | Legislative chamber | 0.19 |  | 0.15
|  | Library- reading room/stacks | 0.15
|  | Lobbies | 0.5 |  | 0.15
|  | Locker room (all others) | 0.15 | 0.25
|  | Locker room (athletic facility) | 0.15 | 0.5
|  | Main Entry Lobby | 0.5 |  | 0.115
|  | Mall common area | 0.25 |  | 0.15
|  | Media Center | 0.15
|  | Multipurpose assembly | 0.5
|  | Multiuse assembly | 0.5 |  | 0.15
|  | Museum (children's) | 0.25 |  | 0.15
|  | Museum/gallery | 0.25 |  | 0.15
|  | Music/theater/dance | 1.07 |  | 0.15
|  | Occupiable storage for dry materials | 0.15
|  | Occupiable storage for liquids/gels | 0.15 | 1.5
|  | Office space | 0.15
|  | Parking Garage | 0.15 | 0.75
|  | Pet shop (animal area) | 0.25 | 0.9 | 0.15
|  | Pharmacy prep | 0.15
|  | Photo studio | 0.15
|  | Places of religious worship | 1.07 |  | 0.15
|  | Reception area | 0.15
|  | Restaurant Dining Rooms | 0.5 |  | 0.15
|  | Retail sales | 0.25 |  | 0.2
|  | Science Laboratories | 0.15 | 1
|  | Shipping/ receiving | 0.15
|  | Shower room | 0.15 | 50
|  | Shower room- cont. exh. | 0.15 | 20
|  | Sorting/packing/ light assembly | 0.15
|  | Spectator area (sports) | 0.5 | 0.5 | 0.15
|  | Stages, studios | 0.5 |  | 0.15
|  | Supermarket | 0.25 |  | 0.2
|  | Swimming deck | 0.5 |  | 0.15
|  | Swimming pool | 0.15
|  | Telephone closet | 0.15
|  | Telephone/ data entry | 0.15
|  | Toilet (private) | 0.15 | 50
|  | Toilet (private)- cont. exh. | 0.15 | 25
|  | Toilet (public) | 0.15 | 70
|  | Toilet (public)- cont. ehx. | 0.15 | 50
|  | Transportation waiting | 0.5 |  | 0.15
|  | Trash/ recycling | 0.15 | 1
|  | University/College Laboratory | 0.15 | 1
|  | Warehouse | 0.15
|  | Wood/ Metal shop | 0.15 | 0.5
Note on B6: 2019 Update: If this box checks, columns 02-18 grey out. Note in Table D row 15 about attached calcs.
Note on B7: 2019: If this box checks, Nonresidential and Hotel/Motel ventilation systems subtable below opens for user input.
Note on K7: Usability Update: If this box checks, High-Rise Residential Dwelling Unit Systems subtable below opens for user input.
Note on B8: Sally Blair: If this box is checked, Note in Table D row 16 about natural ventilation being used to meet ventilation rates.
Note on A9: 2019 Update: New Heading Row
Note on J10: 2019 Update: Because columns have been added for 2019, subsequent column numbers have all changed. Need to recheck calc logic uses the correct columns for all calcs in table.
Note on I11: 2019 Update: Any number entered > 0 should trigger note in Table D row 13.
Note on E16: 2019 Update: This greys out unless column 09 is "Shower room" or "Toilet…"
Note on F16: 6.6.22 Always user input
Note on G16: 09/03/20 J.13 = the greater of: J.10 * J.09 OR J.12 * 15.0 REMEMBER: J.09 rate is determined by J.16 DCV row. If DCV row = "Provided", then J.09 should use the DCV rate shown below. If J.16 DV row = anything other than "Provided", then J.09 rate should be "cfm/ft2 for column 13 calc" seen below.
Note on H16: 2019 Update: If 09 is anything OTHER THAN - Shower rooms - Toilets col 14 = col 10 x col 09 (cfm/ft2) If 09 is Shower rooms or Toilets: col 14 = col 11 x col 09 (cfm/unit) If no value in col 09 designated for col 14 calc, then col 14 & 15 greys out.
Note on J18: Sally Blair: Adds new (blank) row for user entry same as row 16/17. (under this system). Remove last removes this added row. Reset clears all entries for this system.
Note on K19: 2019 Update: Says "Yes" if column 05+column 06 > column 17 AND col 15 > col 14 if not grey, otherwise "No" Make sure it is EQUAL or greater is yes
Note on J20: Sally Blair: Add System button duplicates Rows 10-19, but blank. Remove Last removes that entire system. Reset clears entire table.
Note on A29: 09/11/20: If the box is checked, J28 grays out
Note on B29: 2019 Update: If this box checks, columns J28 grey out. Note in Table D row 15 about attached calcs.
Note on H30: 3/29/22 If neither bathroom/Kitchen IAQ or Bathroom/Kitchen IAQ & Vent is selected, trigger note in Table D row 24
Note on E33: 2019 Update: = column 22 x ((0.03 x column 20) + (7.5 x (column 21 + 1)))
Note on H33: 2019 Update: If checked, moves NRCV-MCH-32 form from "No" to "Yes" in Table P.
Note on H34: 2019 Update: If checked, moves NRCV-MCH 27 AND NRCV-MCH-32 forms from "No" to "Yes" in Table P.
Note on H35: 2019 Update: If checked, moves NRCV-MCH-32 form from "No" to "Yes" in Table P.
Note on E39: J.29 = "Yes" if ((column 24-column 25)/column 24) <= 0.2 for all rows in subtable, J.29 = Grayed out if continuous ventilation has been selected otherwise says "No"
Note on K39: 2019 Update: Says "Yes" if either of the conditions below are met for all rows in subtable: - column 23 <= column 24 OR - column 23 <= column 25, otherwise says "No"
Note on J40: 2019 Update: Excel rows 35-36 are example of what happens with this button is clicked. Same logic as rows 32-34 apply to this new space.
Note on C87: 2019 Update: This selection changes the formula in column 13
Note on C116: 2019 Update: These two selections changes the formula in column 14
Note on C126: 2019 Update: These four selections change the formula in column 14

## K. VAV Controls
| User input |  | auto calculated | [7 empty] | From another Table | From look up table | 2019 Changes
K. TERMINAL BOX CONTROLS
[d:OnlyUI] Table Instructions: Complete the following Table to demonstrate compliance with prescriptive zone control requirements in §140.4(d) & §170.2(c)4B. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with prescriptive zone control requirements in §140.4(d) & §170.2(c)4B. [d:/OnlyRG]
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12
Zone/System/VAV Box Name or Item Tag | Zonal Control Strategy per §140.4(d) | Design |  |  | Deadband Compliance |  |  |  | Reheated, Recooled, Mixed Air Compliance |  | Complies
|  | Peak Primary Airflow CFM | Primary Air in Deadband CFM | Reheated Recooled Mixed Airflow CFM | Outside Air CFM | 30% of Peak Primary Airflow CFM | Max Deadband Airflow CFM | 50% of Peak Primary Airflow | 1st Stage Modulates <95oF and Maintains DB Rate? | 2nd Stage Modulates from DB Flow to Heating Max Flow?
| See dropdown | [7 empty] | See dropdown | See dropdown | "Yes"/ "No"
[9 empty] | Reset | Add Row | Remove Last
Zonal Ctrl Strategy dropdown
| No Reheat, Recool, Mixing | [7 empty] | 1st Stage Dropdown | 2nd Stage Dropdown
| VAV w DDC @ zone | [7 empty] | Yes | Yes
VAV w/o DDC @ zone
NA: Pressurization control
NA: Reheat via site/solar source
NA: Humidity control
NA: Peak SA < 300 CFM
NA: Healthcare Facility
Note on G9: 11.11.21 = (0.3 x 03) if 02 is VAV w/o DDC Else blank/gray
Note on H9: 11/11/21 If K.02 = "VAV w DDC @ Zone", K.08 = K.06 If K.02 = "VAV w/o DDC @ Zone", K.08 = max of K.06 and K.07
Note on I9: Mart-Laptop: 0.5 X Col-03
Note on L9: 11.11.21 Ben, says "Yes" if column 02 selection is ANY of the following - No Reheat, Recool, Mixing - NA: Pressurization Control - NA: Reheat via site/solar source - NA: Humidity Control - NA: Peak SA < 300 CFM - NA: Healthcare Facility OR says "Yes" if column 02 says "VAV w/o DDC@zone" AND 05<08 OR says "Yes" if column 02 says "VAV w DDC@zone" AND 05<MAX(09 AND 06) AND 04<08 AND both columns 10 & 11 say "Yes".
Note on B11: Sally Blair: Selection of VAV w DDC opens 03-11. Selection of VAV w/o DDC opens 03, 05,06,07,08.
Note on B19: 2019 Update: Added exception fro HCF

## L. Distribution
| User input |  |  | auto calculated |  |  | From another Table |  | From look up table
L. DISTRIBUTION (DUCTWORK and PIPING)
[d:OnlyUI] Table Instructions: Complete the following tables to show compliance with mandatory pipe insulation requirements found in §120.3 and mandatory requirements found in §120.4 and 160.3(b) for duct sealing. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory pipe insulation requirements found in §120.3 and mandatory requirements found in §120.4(g) for duct sealing. [d:/OnlyRG]
Mandatory Pipe Insulation
01 | ¨ | Insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Insulation exposed to weather shall be installed with a cover suitable for outdoor service. Insulation covering chilled water piping and refrigerant suction piping located outside the conditioned space shall have a Class I or Class II vapor retarder. All penetrations and joints of which shall be sealed.
02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 10a
System Type | Nominal Pipe Diameter (in) | Fluid Temperature Range (oF) | Conductivity Range (Btu-in per hr per ft2 per oF) | Insulation Mean Rating Temp. (oF) | Min. Insulation Thickness Required per Table 120.3-A (in) | Min. Insulation Thickness Required per §120.3(c)2 & §160.3(c)1dii (in) | Insulation Thickness per Design (in) | Exception to §120.3 & §160.3(c) (if applicable) | Serving Res or NR Space?
Dropdown | Dropdown | Dropdown | Dropdown | Value from Table 120.3-A based on column 04 | Value from Table 120.3-A based on columns 03/04 |  |  | Dropdown | Dropdown
Duct Leakage Testing
The answers to the questions below apply to the following duct system(s): |  |  |  |  | NR/Common Use: Duct leakage testing shall not exceed X% per NA7.5.3 required for these systems?
Dwelling Units: Total duct leakage of duct system shall not exceed 12% or duct leakage system to outside shall not exceed 6% per RA3.1.4 required for these systems?
Duct leakage testing per CMC Section 603.10.1 required for these systems?
11 | Dropdown | The scope of the project includes only duct systems serving healthcare facilites.
12 | Dropdown | Duct system provides conditioned air to an occupiable space for a constant volume, single zone, space-conditioning system.
13 | Dropdown | The space conditioning system serves less than 5,000 ft2 of conditioned floor area.
14 | Dropdown | The combined surface area of the ducts located outdoors or in unconditioned spaces in the following locations is more than 25% of the total surface area of the entire duct system:
|  | ¨ | Outdoors
|  | ¨ | In a space directly under a roof that has a U-factor greater than the U-factor of the ceiling, or if the roof does not meet the requirements of §140.3(a)1B or if the roof has fixed vents or openings to the outside/ unconditioned spaces
|  | ¨ | In an unconditioned crawlspace
|  | ¨ | In other unconditioned spaces
15 | Dropdown | The scope of the project includes extending an existing duct system, which is constructed, insulated or sealed with asbestos.
16 | Dropdown | The scope of the project includes an existing duct system that is documented to have been previously sealed as confirmed through field verification and diagnostic testing in accordance with procedures in the Reference Nonresidential Appendix NA2.
17 | Dropdown | Duct system shall be sealed in accordance with the California Mechanical Code.
17 | Dropdown | All Ductwork and plenums with pressure class ratings shall be constructed to Seal Class A
18 | Dropdown | All ductwork is an extension of an existing duct system
19 | Dropdown | Ductwork serving individual dwelling unit
20 | Dropdown | < 25 ft of new or replacement space conditioning ducts installed
21 | Dropdown | Duct Insulation R-Value
System Type Dropdown | Pipe Dia Dropdown | Fluid Temp Range Dropdown if Space Heating in 02 | Conductivity Range Dropdown |  | Duct Insulation R Value Dropdown |  |  | Applicable Exception Dropdown | Space Dropdown
Space heating | < 1 | Above 350 | 0.32 - 0.34 |  | R0 |  |  | No exception taken | Residential
Space cooling | 1 to <1.5 | 251-350 | Other |  | R2.1 |  |  | Factory installed piping within certified equip. | Nonresidential
| 1.5 to <4 | 201-250 | Conductivity Range Dropdown |  | R4.2 |  |  | Fluid design operating temp. 60-105oF
| 4 to <8 | 141-200 | 0.29 - 0.32 |  | R6 |  |  | Gas/condensate/roof/vents/waste piping
| 8+ | 105-140 | Other |  | R8 |  |  | Lack of insulation will not increase energy use
|  |  | Conductivity Range Dropdown |  | R10
|  | Fluid Temp Range Dropdown if Space Cooling in 02 | 0.27 - 0.30 |  | R12
|  | 40-60 | Other |  | Rvalue Verified Duct System
|  | Below 40 | Conductivity Range Dropdown
| Duct Leakage Sealing Dropdowns (11/12/13/14/15/16/18/19/20) |  | 0.25 - 0.29
| Yes |  | Other
| No |  | Conductivity Range Dropdown
0.22 - 0.28
Other
| Duct Leakage Sealing Dropdowns (17) |  | Conductivity Range Dropdown
| Yes |  | 0.21 - 0.27
| Exposed Ductwork located in occupied space |  | Other
Conductivity Range Dropdown
0.20 - 0.26
Other
Note on E9: Sally Blair: 06 & 07 blank and grey out if "Other" selected in 05.
Note on G9: Sally Blair: Starts as grey unless user selects "Other" in column 05
Note on F12: 6.16.22 DYNAMIC TEXT IN RED If 17 = No X = 6 If 17 = Yes X = 15
Note on J12: 6.16.22 Yes if 12-14 are Yes and 11, 15, 116 are No. Otherwise, "No"
Note on J13: 6.16.22 if L.18 = Yes AND L17 = "No" = "Yes" and duct system = "12%" and outside = "6%" if L18 = "Yes" and AND L19 = "No" = "Yes and duct system = 15% and outside = 10% Otherwise = "No"
Note on J14: 11/30/21 = Yes if Duct Leakage Testign per NA7.5.3 = "No" AND Duct Leakage Testing per RA3.1.4.3 = "No"
Note on A15: Ben Lalor: Numbers of rows have been updated by shifting down one number
Note on B15: 6.16.22 If row 11 = "Yes" rows 12-20 grey out
Note on C19: Sally Blair: User can select more than one.
Note on B29: 6.16.22 This is blank/gray unless 18 = "Yes"
Note on B30: 6.16.22 This is blank/gray unless 18 = "Yes"
Note on D32: Ben Lalor: Custom Dropdown when column 04 = Above 350
Note on F32: 7.5.22 This is needed for downstream CF2R and does not trigger other fields or affect compliance logic
Note on D34: Sally Blair: If the user selects "Other", columns 06 & 07 blank and grey out & column 08 opens for user input.
Note on D35: Ben Lalor: Custom Dropdown when column 04 = 251-350
Note on I36: 2019 Update: Get rid of this option
Note on D38: Ben Lalor: Custom Dropdown when column 04 = 201-250
Note on D41: Ben Lalor: Custom Dropdown when column 04 = 141 - 200
Note on D44: Ben Lalor: Custom Dropdown when column 04 = 105 - 140
Note on D47: Sally Blair: Custom Dropdown when column 04 = 40-60
Note on D50: Sally Blair: Custom Dropdown when column 04 = Below 40

## M.Cooling Tower
| user entered |  |  |  | auto calculated |  |  |  |  | From another Table | From look up table
M. COOLING TOWERS
[d:OnlyUI] Table Instructions: Complete the following Table for open and closed circuit cooling towers with a rated capacity > 150 tons to demonstrate compliance with mandatory requirements in §110.2(e)2. This Table calculates the Maximum Cycles of Concentration using the Langelier Saturation Index (LSI) calculations per §110.2(e)2. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory requirements in §110.2(e)2 for cooling towers with a rated capacity > 150 tons. This Table calculates the Maximum Cycles of Concentration using the Langelier Saturation Index (LSI) calculations per §110.2(e)2. [d:/OnlyRG]
01 | ¨ | Check the box if the project is showing calculations on the plans, or attaching the calculations instead of completing this Table.
02 | 03 | 04 | 06 | 05 | 06 | 07 | 08 | 09 | 10 | 11 |  | gfd
Name or Item Tag | Design Conditions |  | Economizer Conditions | Rated Conditions | Maximum Skin Temp (◦F) | Conductivity | M-Alkalinity | Calcium Hardness | Magnesium Hardness | Target Tower Cycles
| Design GPM | Min Flow GPM | GPM | GPM/HP
[7 empty] | 12 | 13 | 14 | 15
[7 empty] | Calculated pH @ Target Cycles | pH Saturation @ Target Cycles | Tower LSI Based on Calculated pH | Complies
[6 empty] | 0 | #NUM! | #NUM! | #NUM! | #NUM!
[6 empty] | 0 | #NUM! | #NUM! | #NUM! | #NUM!
[8 empty] | Reset | Add Row | Remove Last
1 Open-circuit cooling tower is defined as an open, or direct contact, cooling tower which exposes water directly to the cooling atmosphere, thereby transferring the source heat load from the water directly to the air by a combination of heat and mass transfer.
2 Closed-circuit cooling tower is defined as a cooling tower that utilizes indirect contact between a heated fluid, typically water or glycol, and the cooling atmosphere to transfer the source heat load through sensible heat, latent heat, and mass transfer indirectly to the air, essentially combining a heat exchanger and cooling tower into an integrated and relatively compact device.
Climate Zone Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on B5: Sally Blair: If checked, grey out columns 02-15 & Trigger the note in row 14 on Table D.
Note on K10: Sally Blair: This row appears if the user hit "Add Row" button
Note on G14: Sally Blair: Name/item tag copied down from column 02
Note on K14: Sally Blair: "Yes" if column 14 is < 2.5. "No" if column 14 is > 2.5.
Note on K15: Sally Blair: This row appears if the user hit "Add Row" button

## N. LMCI (LMCC)
| User input |  |  | auto calculated | From another Table | From look up table
N. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ [d:/OnlyRG]
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | LMCI-MCH-01-E - Must be submitted for all buildings. | o | o
● | m | LMCI-MCH-20-H Duct Leakage Diagnostic Test | o | o
● | m | LMCI-MCH-21-H Duct Location Verification | o | o
● | m | LMCI-MCH-22-H Fan Efficacy | o | o
● | m | LMCI-MCH-23-H Airflow Rate | o | o
● | m | LMCI-MCH-24-H Building Envelope Air Leakage Worksheet | o | o
● | m | LMCI-MCH-25 Refrigerant Charge Verification | o | o
● | m | LMCI-MCH-26-H Rated Space Conditioning System Equipment Verification | o | o
● | m | LMCI-MCH-27b-H Indoor Air Quality and Mechanical Ventilation | o | o
● | m | LMCI-MCH-28-H Return Duct Design and Air Filter Grille Device Sizing | o | o
● | m | LMCI-MCH-29-H Duct Surface Area Reduction; Buried Ducts Compliance Credit | o | o
● | m | LMCI-MCH-32-H Local Mechanical Exhaust | o | o
● | m | LMCI-MCH-33-H Variable Capacity Heat Pump Compliance Credit | o | o
Note on A4: 2019 Update: Updated hyperlink
Note on A7: Sally Blair: Ben, this defaults to "Yes" and can’t be moved to "No"
Note on A8: 5/3/22 Triggers "Yes" if Table L Duct Leakage Testing, Dwelling Units = "Yes". Otherwise = "No"
Note on A9: 6.6.22 Default = No
Note on A10: 5/3/22 If Table H Serving Dwelling Units = "Serving Individual Dwelling Units". Otherwise = "No"
Note on A11: 5/3/22 If Table H Serving Dwelling Units = "Serving Individual Dwelling Units". Otherwise = "No"
Note on A12: 6.6.22 Triggers yes if J.28 = gray/blank. Otherwise = No
Note on A13: 6.6.22 If "Individual Dwelling Unit" is selected in Table F System Information and Table 170.2-K requires Refrigerant charge verification based on climate zone in Table A, this = Yes Otherwise = No
Note on A14: 6.6.22 = Yes if "Unitary Heat Pump", "Unitary Heat Pump (no elec resistance)" or "Dual Fuel Heat Pump" has been selected in Table F Otherwise = No
Note on A15: 6.6.22 Triggers based for new construction and additions greater than 1,000 sf, may need to add this question to the UI (not reported) because we don't ask for this information currently
Note on A16: 6.6.22 Default = No
Note on A17: 6.6.22 Default = No
Note on A18: 6.20.22 = Yes if Kitchen Range hood is selected in J26. Otherwise = No
Note on A19: 6.20.22 = default = "no"

## O. NRCA
O. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCA/. [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and any with "-A" in the form name must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html
YES | NO | Form/Title | Systems To Be Field Verified | Field Inspector |  | Trigger |  | Ben, this is the logic that moves the selection from "No" to "Yes"
|  |  |  | Pass | Fail |  | Logic
m | m | NRCA-MCH-02-A Outdoor Air must be submitted for all newly installed HVAC units. Note: MCH-02-A can be performed in conjunction with MCH-07-A Supply Fan VFD Acceptance (if applicable) since testing activities overlap. |  | o | o | Newly installed HVAC unit. (CFM is listed somwhere in this form…) | PROJECT SCOPE 01 = New Construction OR Altered Mechanical System 04 = Ventilation | Table B. Project Scope 03 = Ventilation
m | m | NRCA-MCH-03-A Constant Volume Single Zone HVAC NOTE: This form does not automatically move to "Yes". If Constant Volume Single Zone HVAC Systems are included in the scope, permit applicant should move this form to "Yes". |  | o | o | Newly installed Unitary Unit | PROJECT SCOPE 01 = New Construction OR Altered Mechanical System 04 = Unitary (Packaged/Split) | No automatic trigger to move to "Yes"
m | m | NRCA-MCH-04-A Air Distribution Duct Leakage |  | o | o | New Duct System Altered Space Conditioning System - Air Handler changeout - Condensing unit of Split System - Cooling coil changeout Altered Duct System <75% new Low Leakage Air-Handling Unit | PROJECT SCOPE 01 = New Construction OR Altered Mechanical System AND 04 = Fan Systems AND/ OR Unitary (Packaged/Split) AND/OR Zonal Systems/ Terminal Boxes AND/OR Ductwork | Table L: If ANY systems shows "Yes" for "Duct leakage testing triggered for these systems?"
m | m | NRCV-MCH-04-H Duct Leakage Test NOTE: Must be completed by a HERS Rater |  | o | o
m | m | NRCA-MCH-05-A Air Economizer Controls |  | o | o | New or Altered Air Economizer | FAN SYSTEMS If Economizer Dropdown Selection ≠ NA | FAN SYSTEMS If Economizer Dropdown Selection = "Fixed Temp., Fixed Enthalpy, Diff Temp., OR Diff Enthalpy"
m | m | NRCA-MCH-06-A Demand Control Ventilation Systems Acceptance must be submitted for all systems required to employ demand controlled ventilation (refer to §120.1(c)3) can vary outside ventilation flow rates based on maintaining interior carbon dioxide (CO2) concentration setpoints. |  | o | o | Have an air side economizer AND Occupant density ≥ 25 people/ 1000sf AND Single zone systems with any controls OR Multizone system with DDC to the zone level. | I. FAN SYSTEMS If Economizer Dropdown Selection "Fixed Temp. - Diff Enthalpy" AND Occupant Density ≥ 25 people/ 1000sf J. SYSTEM CONTROLS 02 = Single Zone OR multi-zone w/DDC to zone | Table J col 16 (top row) says "Provided per §120.1(d)4" for DCV dropdown.
m | m | NRCA-MCH-07-A Supply Fan Variable Flow Controls |  | o | o | VAV Supply Fan | I. FAN SYSTEMS Fan Function Dropdown = Supply Fan Type Dropdown = Variable Air Volume | FAN SYSTEMS Fan Type = Supply System Zoning = multizone VAV systems
m | m | NRCA-MCH-08-A Valve Leakage Test |  | o | o | New Construction | H. PUMPS 05 Variable Flow Dropdown = Yes | PUMPS 05 Variable Flow Dropdown = Yes
m | m | NRCA-MCH-09-A Supply Water Temperature Reset Controls |  | o | o | New or Replaced Chiller or Boiler | G. HVAC SYSTEMS Boiler Efficiency and Controls 09 Tempterature Reset Dropdown = Yes AND/OR Chiller Efficiency and Controls 10 Temperature Reset Dropdown = Yes | F. HVAC SYSTEMS Boiler Efficiency and Controls 09 Tempterature Reset Dropdown = Yes AND/OR Chiller Efficiency and Controls 10 Temperature Reset Dropdown = Yes
m | m | NRCA-MCH-10-A Hydronic System Variable Flow Controls |  | o | o |  | H. PUMPS 05 Variable Flow Dropdown = Yes | PUMPS 05 Variable Flow Dropdown = Yes
m | m | NRCA-MCH-11-A Automatic Demand Shed Controls |  | o | o |  | DDC to zone level | SYS CONTROLS 02 = "multi-zone w/ DDC to zone"
m | m | NRCA-MCH-12-A FDD for Packaged Direct Expansion Units |  | o | o |  | PROJECT SCOPE New Mechanical Systems OR Altered Mechanical System HVAC SYSTEMS 02 = Unitary AC/ Condensers OR Packaged AC/ Heat | If NRCA-MCH-05-A moves to "Yes" AND Table F. HVAC SYSTEMS 02 = Unitary AC/ Condensers OR Packaged AC/ Heat
m | m | NRCA-MCH-13-A Automatic FDD for Air Handling Units and Zone Terminal Units Acceptance |  | o | o |  |  | If NRCA-MCH-05-A moves to "Yes" AND Table F. HVAC SYSTEMS 02 = "Unitary Heat Pump", "PTAC/PTHP", "SPVAC/SPVHP", "Heat Pump + AC", OR "Furnace + AC"
m | m | NRCA-MCH-14-A Distributed Energy Storage DX AC Systems Acceptance NOTE: This form does not automatically move to "Yes". If Distributed Energy Storage DX AC Systems are included in the scope, permit applicant should move this form to "Yes". |  | o | o
m | m | NRCA-MCH-15-A Thermal Energy Storage (TES) System Acceptance NOTE: This form does not automatically move to "Yes". If Chilled Water Storage, Ice-on-Coil Internal Melt, Ice-on-Coil External Melt, Ice Harvester, Brine, Ice-Slurry, Eutectic Salt, Clathrate Hydrate Slurry (CHS), Cryogenic or Encapulated (Ice Ball) Systems are included in the scope, permit applicant should move this form to "Yes". |  | o | o |  |  | No automatic trigger to move to "Yes"
m | m | NRCA-MCH-16-A Supply Air Temperature Reset Controls |  | o | o |  | J. SYSTEM CONTROLS 08 = Included | Moves to Yes if I08 says "Included"
m | m | NRCA-MCH-17-A Condenser Water Temperature Reset Controls |  | o | o |  |  | HVAC SYSTEM Heat Rejection Equipment 12 Condenser Water Temp Reset Controls = Yes
m | m | NRCA-MCH-18 Energy Management Control Systems |  | o | o |  |  | Moves to Yes if I04, I05, I06 OR I07 has an "EMCS" selection.
m | m | NRCA-MCH-19 Occupancy Sensor Controls |  | o | o |  |  | Moves to "Yes" if EITHER I05 is "Occ. Sensor" OR J16 (bottom row) is "Provided per §120.1(d)5"
m | m | NRCA-MCH-20 Multi-Family Ventilation |  | o | o |  |  | Moves to "Yes" if "Ventilation" is checked in Table B AND High-rise Res is selected in Table A
m | m | NRCA-MCH-21 Multi-Family Envelope Leakage |  | o | o |  |  | Moves to "Yes" Balanced Ventilation System row in Table J says "No"
m | m | NRCA-MCH-22-A MF Duct Leakage |  | o | o |  |  | Moves to "Yes" if Table L Duct Leakage Testing, Dwelling Units = "Yes". Otherwise = "No"
m | m | NRCA-MCH-23-A MF HRV/ERV Verification |  | o | o |  |  | Moves to "Yes if Table H Dwelling Unit Fan Efficacy & Energy/Heat Recovery Column 9 = "…provided". Otherwise = "No"
Note on A1: 2019 Update: Removed "AND VERIFICATION" because NRCVs were moved to Table P. Modified instructions too.
Note on B3: Sally Blair: Form will select based on user input in other Tables. User can edit, but if they do a note will show up in Table D. See Table D row 12 for note.
Note on D3: 9/11/20: This is a user entry column where users would list the systems that require each form.
Note on C7: 10/17/22 It's hard to see, but the "-A" is struck-through. We want to remove it for 2022
Note on C8: 2019 Update: Moved to Table P.
Note on G10: Katie Gustafson: What does "single zone systems with any conrols" mean? Basically anything? Does this impact the DR dropdown.

## P. LMCV (LMCC)
| User input |  |  |  | auto calculated |  |  |  | From another Table | From look up table
P. DECLARATION OF REQUIRED CERTIFICATES OF VERIFICATION
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ [d:/OnlyRG]
YES | NO | Form/Title | Systems To Be Field Verified | Field Inspector |  | Trigger |  | Ben, this is the logic that moves the selection from "No" to "Yes"
|  |  |  | Pass | Fail |  | Logic
m | m | LMCV-MCH-04-H Duct Leakage Test NOTE: Must be completed by a HERS Rater |  | o | o |  |  | Moves to Yes if NRCA-MCH-04-A moves to Yes
m | m | LMCV-MCH-24 Enclosure Air Leakage Worksheet NOTE: Must be completed by a HERS Rater |  | o | o |  |  | Moves to "Yes" if A03 = "High-rise Residential" AND "Ventilation" in B03 is checked.
m | m | LMCV-MCH-27 Indoor Air Quality and Mechanical Ventilation NOTE: Must be completed by a HERS Rater |  | o | o |  |  | Moves to "Yes" if "Bathroom IAQ & Vent." is checked in J26.
m | m | LMCV-MCH-32 Local Mechanical Exhaust NOTE: Must be completed by a HERS Rater |  | o | o |  |  | Moves to "Yes" if any of the three boxes are checked in J26.
Table Tip:
[d:OnlyUI] In addition to the Certificates of Compliance, the Standards may also require Certificates of Verification to be submitted to the authority having jurisdiction. This section of the compliance documentation serves as an acknowledgement of, and a declaration that Certificates of Verification are required to be submitted for compliance. The boxes must be checked for every Certificate of Verification that applies to the job. [d:/OnlyUI]
Note on A4: 2019 Update: This whole table is new for 2019
Note on B6: 2019 Update: Form will select based on user input in other Tables. User can edit, but if they do a note will show up in Table D. See Table D row 22 for note.
Note on C8: 2019 Update: Moved from NRCA Table O.
Note on D8: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on C9: 2019 Update: These last 3 are new for 2019.
Note on I9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This should be low and high rise and is only reuqired if balanced ventilation not used, so not sure about this trigger
Note on I10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: low and high rise
Note on A14: UI ONly: Table tip only applies to UI, does not apply to report generator.

## Q. Mand Measures
| User input |  |  | auto calculated | From another Table | From look up table
Q. MANDATORY MEASURES DOCUMENTATION LOCATION
[d:OnlyUI] Table Instructions: Indicate where mandatory measures are documented in the plan set or construction documentation. For any mandatory measures that do not apply, mark the plan sheet or construction document location as "N/A", any active cells that are left blank will result in non-compliance in Table C. [d:/OnlyUI] [d:OnlyRG] This table is used to indicate where mandatory measures are documented in the plan set or construction documentation. [d:/OnlyRG]
01 |  |  | 02
Compliance with Mandatory Measures documented through MCH Mandatory Measures Note Block: |  | Dropdown | Plan sheet or construction document location
03 |  |  | 04
Mandatory Measure |  |  | Plan sheet or construction document location
Heating Equipment Efficiency per §110.1
Cooling Equipment Efficiency per §110.1
Furnace Standby Loss Control per §110.2(d)
Duct Insulation per §120.4
Heating Hot Water Equipment Efficiency per §110.1
Cooling Chilled and Condenser Water Equipment Efficiency per §110.1
Open and Closed Circuit Cooling Towers conductivity of flow-based controls per §110.2(e)1
Open and Closed Circuit Cooling Towers Flow Meter with analog output per §110.2(e)3
Open and Closed Circuit Cooling Towers Overflow Alarm per §110.2(e)4
Open and Closed Circuit Cooling Towers Efficient Drift Eliminators per §110.2(e)5
Pipe Insulation per §120.3(b)
Combustion air shutoff, combustion air fan controls and stack design and controls for boilers per §120.9
Heat Pump with Supplementary Electric Resistance Heater Controls per §110.2(b)
The air duct and plenum system is designed per §120.4(a)-(f)
Kitchen range hoods shall be rated for sound in accordance with Section 7.2 of ASHRAE 62.2
MM Note Block Dropdown
Yes
No
Note on A3: 2019 Update: Updated Table to Q.
Note on E7: Katie Gustafson: Ben, only active if Dropdown = "Yes", otherwise greyed out.
Note on A8: Katie Gustafson: Ben, rows 8-21 are hidden unless the user selects "No" in column 01. Then these rows expand for user input. October 2019 Update: rows 8-24 need to be hidden unless the user selects "No" in column 01. Then these rows expand for user input.
Note on A20: Sally Blair: All code sections referenced throughout the form will hyperlink to the correct page in the Standards pdf on CEC website. See Hyperlinks tab for hyperlinks.