## New Table Sequence
Label | Table Title | Trigger within:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Refrigerated Warehouses | Table B
Table G | Commercial Refrigeration | Table B
Table H | Enclosed Parking Garage Exhaust | Table B
Table I | Process Boilers | Table B
Table J | Compressed Air Systems | Table B
Table K | Elevators | Table B
Table L | Escalators and Moving Walkway Controls | Table B
Table M | Computer Room Equipment | Table B
Table N | Commercial Kitchen Ventilation | Table B
Table O | Laboratory Exhaust | Table B
Table P | Controlled Environment Horticulture | Table B
Table Q | Steam Traps | Table B
Table R | Pool/ Spas | Table B
Table P S | Declaration of Required Certificates of Installation | ALWAYS
Table Q T | Declaration of Required Certificates of Acceptance | ALWAYS
| Signature Page | ALWAYS

## Code References
Section
§120.6 | Header, B, C, F
140.9 | Header, B, C
120.6(a) | B, C
120.6(b)
120.6(c)
120.6(d)/(e)
120.6(f)/(g)
140.9(a) | B, C
140.9(b)
140.9(c)
TABLE 120.6-A | F
120.6(a)2 | F
§120.6(a)3A | F
§120.6(a)3B | F
§120.6(a)3C | F
§120.6(a)4D/E | F
§120.6(a)4B | F
§120.6(a)4G | F
§120.6(a)5A/B/C | F
§120.6(a)6 | F
120.6(f)2
120.6(f)3
160.7

## LMCC Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Process Systems
LMCC-PRC-01-E |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | LMCC-PRC-01-E
Table Instructions: Include This form is used to document any process systems that are within the scope of the permit application and are demonstrating compliance with mandatory requirements in §120.6/ §160.7, or prescriptive requirements in §140.9. This compliance document is used for newly constructed, addition and alteration projects.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
The project name and date prepared is a user input on the first page, but will populate the heading on all other pages.
STATE OF CALIFORNIA
Process Systems
LMCC-PRC-01-E |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | LMCC-PRC-01-E
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
Footer on all pages:
CA Building Energy Efficiency Standards - 2022 Low-rise Multifamily/Mixed-use Compliance: http://www.energy.ca.gov/title24/201922standards
First Page Heading
Heading for all other pages

## LMCC A. General Info
|  | User input | auto calculated |  |  |  | From another Table |  |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  | 04 | Total Conditioned Floor Area
02 | Climate Zone |  | Dropdown |  | 05 | Total Unconditioned Floor Area
03 | Occupancy Types Within Project: |  |  |  | 06 | # of Stories (Habitable Above Grade)
¨ | Office |  | ¨ | Retail | ¨ | Non-refrigerated Warehouse |  | ¨ | Grocery
¨ | Hotel/ Motel |  | ¨ | School or Classroom | ¨ | Healthcare facility |  | ¨ | Financial Institution
¨ | Rise Residential |  | ¨ | Relocatable Class Bldg Public School | ¨ | All Other Occupancy Types (Write In) |  | ¨ | Unleased Tenant Space
¨ | Auditorium |  | ¨ | Library | ¨ | Restaurant |  | ¨ | Parking Garage
¨ | Convention Center |  | ¨ | Medical Office Bldg/ Clinic | ¨ | Theater |  | ¨ | Religious Facility
¨ | Commercial Industrial |  | ¨ | Data Center | ¨ | Gymnasium |  | ¨ | Support Area
Alert! Healthcare Facilities do not have to meet the elevator, computer room, commercial kitchen, or lab exhaust requirements under Title 24, Part 6 and therefore are not documented on the NRCC-PRC-E. The corresponding tables (K,M,N,O) say "This section does not apply" when healthcare facility has been chosen as an occupancy within Table A. Systems serving these spaces shall meet the requirements of the Appliance Efficiency Regulations for walk-in coolers or freezers contained in the Appliance Efficiency Regulations (California Code of Regulations, Title 20, Sections 1601 through 1608).
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on B6: 11.23.21: Only the occupancy types selected by the user will display on the form with a checked box. Occupancy types not selected will not show.
Note on H8: 11.21.21: When A.03 = "Healthcare Facility" then Tables K,M,N,O do not trigger and say "This section does not apply" This overrides any other trigger logic for these Tables
Note on B13: 2019 Updates: This note is triggered when A.03 = "healthcare facility"

## LMCC B. Project Scope
|  | User input |  | auto calculated | From another Table | From look up table
B. PROJECT SCOPE
This table includes proccess systems that are within the scope of the permit application and are demonstrating compliance with mandatory requirements in §120.6/§160.7 for multifamily occupancies or prescriptive requirements in §140.9 for nonersidential occupancies in mixed-use buildings.
My project consists of (check all that apply):
01 |  | 02
¨ | Refrigerated Spaces <3,000 ft2 Total (no Title 24, Pt 6 requirements) | ¨ | Escalator & Moving Walkway Speed Controls (mandatory §120.6(g))
¨ | Refrigerated Spaces >=3,000 ft2 Total (mandatory §120.6(a)) | ¨ | Controlled Environment Horticulture (mandatory §120.6(h))1
¨ | Food/Beverage Stores > 8,000ft2 cfa (mandatory §120.6(b)) | ¨ | New Steam Traps (mandatory §120.6(i))
¨ | Enclosed Parking Garage Exhaust >= 10,000 cfm (mandatory §120.6(c)) | ¨ | Computer Rooms > 20 W/ft2 Power Density (mandatory §120.6(j) & prescriptive §140.9(a))1
¨ | Newly Installed Process Boilers (mandatory §120.6(d)) | ¨ | Commercial Kitchen Ventilation/Exhaust (prescriptive §140.9(b))1
¨ | Compressed Air Systems Combined HP >= 25 (mandatory §120.6(e)) | ¨ | Laboratory Exhaust/Factory Exhuast & Fume Hood (prescriptive §140.9(c))1
¨ | Elevator Lighting & Ventilation Controls (mandatory §120.6(f)/§160.7) | ¨ | Pool/Spa (mandatory §110.4/§160.7)
1 FOOTNOTE: These building features can comply using the performance method. If using the performance method for these features, compliance should be demonstrated on the NRLMCC-PRF-E compliance document.
Alert! Refrigerated Warehouses and refrigerated spaces that are less than 3,000 square feet do not have requirements under Title 24, Part 6 and therefore are not documented on the NRCC-PRC-E. Systems serving these spaces shall meet the requirements of the Appliance Efficiency Regulations for walk-in coolers or freezers contained in the Appliance Efficiency Regulations (California Code of Regulations, Title 20, Sections 1601 through 1608).
Note on A5: Sally Blair: Selections made here trigger the corresponding Tables in the form.
Note on B7: Katie Gustafson: Triggers Note in row 16 below

## C. Compliance
|  | auto calculated |  | From another Table |  | From look up table |  | From look up table
C. COMPLIANCE RESULTS
Results in this table are automatically calculated from data input and calculations in Tables F through OR. Note: If any cell on this table says "COMPLIES with Exceptional Conditions" refer to Table D. Exceptional Conditions for guidance or see the applicable Table referenced below.
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 11 14
Refrigerated Warehouse/ Space §120.6(a) | Commercial Refrigeration §120.6(b) | Parking Garage Exhaust §120.6(c) | Process Boilers §120.6(d) | Compressed Air Systems §120.6(e) | Elevators §120.6(f)/ §160.7 | Escalators & Moving Walkways §120.6(g) | Computer Rooms §140.9(a) | Commercial Kitchens §140.9(b) | Laboratory/Factory Exhaust §140.9(c) | Controlled Environment Horticulture §120.6(h) | Steam Traps §120.6(i) | Multifamily Pool/Spa §160.7 | Compliance Results
(See Table F) | (See Table G) | (See Table H) | (See Table I) | (See Table J) | (See Table K) | (See Table L) | (See Table M) | (See Table N) | (See Table O) | (See Table P) | (See Table Q) | (See Table R)
Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | COMPLIES or "COMPLIES WITH EXCEPTIONAL CONDITIONS" or DOES NOT COMPLY
Note on A6: 2019 Updates: If any of 01-10 13 corresponding tables do not expand and instead say this section does not apply then the corresponding column in table C should be blank and grey.
Note on N7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will the processes not included in the LMCC version be greyed out or just not show up at all? Reply: My plan is they would just be greyed out because they wouldn't apply.
Note on A9: 11.23.21 Says "Yes" if: - Ext. Surface Ins subtable col 01 checked AND - Underslab Heating subtable all fields completed AND - Fan Power Evap subtable all fields completed which aren't grey AND - Condensers subtable 01 completed + Air-cooled Cond. all columns 11 say "Yes" if triggered + Water/Evap Cond. all col 10 say "Yes" if triggered + Adiabatic Cond. all col 09 say "Yes" if triggered AND - Compressors subtable 01 completed & 02-05 completed if expanded AND - Infiltration Barrier subtable 01 & 02 -03 completed AND - Transcritical CO2 Gas Cooler subtable 01 completed + all columns 09 say "Yes" if triggered
Note on B9: 11.23.21 Says "Yes" if: - 01 completed AND - Condensers subtable 01 OR 02 checked OR all column 11 say "yes" if subtable applies AND - Compressor & Cond. Units subtable 01 checked OR 02-04 05 completed if subtable applies AND - Refrigerated Display Cases subtable 02 OR 03 checked if subtable applies AND - Heat Recovery Subtable 01 checked OR 02 completed if subtable applies AND - Transcritical CO2 Gas Cooler subtable 01 completed + all columns 09 say "Yes" if triggered Otherwise says "No"
Note on C9: 2019 Update: 03 says "Yes" if - EITHER 01 OR 02 = "yes" OR - 3-9 are completed and 14 says "complies" for ALL fans added to Table H. Otherwise 03 says "No"
Note on D9: Sally Blair: Says "Yes" if: - 01-05 completed if not grey
Note on E9: 11.21.21: Says "Yes" if: - 01-03 07 completed
Note on F9: 2019 Updates: Updated 6/23/20 06 says "Yes" if - sum of column 06 <= sum of column 07 AND - EITHER 10 = "Yes" OR 13<=14 AND - everything not grey is completed Otherwise 06 says "no"
Note on G9: Sally Blair: Says "Yes" if: - 01 completed
Note on H9: 11.21.21: Says "Yes" if: In HVAC subtable - 01-09 completed if not grey AND - 06 <= 07 AND In UPS Subtable - 02 completed AND - 06>=05 if not grey
Note on I9: 2019 Update: Updated 3.1.21 09 says "yes" if - kitchen ventilation 01 is checked OR -02,03,05 have been completed AND kitchen exhuast 01 -07 have been completed if not grey, AND 07<=08 if 08 not grey Otherwise says no
Note on J9: 2019 Update: Says "Yes" if columns 01-05 are completed if table is triggered. Otherwise says "No"
Note on K9: 11.23.21: Says "Yes" if - HVAC Subtable columns 01-02 are completed AND - Ltg Subtable 01-06 complete if not grey AND - Env Subtable 01-04 complete if not grey Otherwise says "No"
Note on L9: 11.23.21: Says "Yes" if columns 01-03 are completed if table is triggered. Otherwise says "No"
Note on M9: 11.23.21: Says "Yes" if columns 01-08 are completed AND 09-15 completed if triggered. Otherwise says "No"
Note on N9: Sally Blair: 1. Says "COMPLIES" if no other cells in row 9 say "No" & no exceptional conditions have been triggered in Table D. 2. Says "COMPLIES WITH EXCEPTIONAL CONDITIONS" if no other cells in row 9 say "No" & an exceptional conditioned has been triggered in Table D. 3. Says "DOES NOT COMPLY" if one of the cells in row 9 says "No"

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Table M indicates a computational fluid dynamics (CFD) analysis was performed to meet computer room containment requirements in §140.9(a)6. Authority Having Jurisdiction may ask for calculations to confirm compliance at their discretion.
Table K indicates one or more elevators which have designed lighting power greater than the Maximum Power Allowed. Please revise Table K to demonstrate compliance.
Table K indicates one or more elevators which have designed ventilation Watts/cfm greater than the maximum Watts/cfm allowed. Please revise Table K to demonstrate compliance.
Selections made in Table P S have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination.
Selections made in Table Q T have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination.

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## H. Garage Exhaust
[5 empty] | User input |  | auto calculated | From another Table | From look up table
H. ENCLOSED PARKING GARAGE EXHAUST
This table includes all newly installed mechanical ventilation systems which serve parking garages and have a design exhuast rate greater than or equal to 10,000 cfm. The inputs of Table H are used to demonstrate compliance with the requirments of §120.6(c).
| Yes | Exceptions
01 | ¨ | Garage is expected to have vehicles with non-gasoline combustion engines for > 20% of the parked vehicles per Exception 1 to §120.6(c)
02 | ¨ | Project scope includes an addition or alteration to an existing garage where < 10,000 cfm of new exhaust capacity is being added Exception 2 to §120.6(c)
| Yes | Requirements
03 | ¨ | Exhaust fan control modulates airflow rates <= 50% design capacity when contaminant levels are maintained per §120.6(c)1
04 | ¨ | Fan control or device allows fan motor demand ≤ 30% design wattages at 50% of design airflow per §120.6(c)2
05 | ¨ | Design includes monitoring CO with a sensor density >= 1 per 5,000 ft2 per §120.6(c)3
06 | ¨ | CO sensors are located in the highest expected concentration locations, with at least two per proximity zone per §120.6(c)3
07 | ¨ | Design CO sensor setpoint <= 25 ppm per §120.6(c)4
08 | ¨ | Occupied garage design maintains negative pressurization per §120.6(c)6
09 | ¨ | Designed occupied total ventilation rate >= 0.15 CFM/ ft2 §120.6(c)5
|  | 10 | 11 | 12 | 13 | 14
|  | Fan Name | Parking Garage Area (ft2) | Ventilation Fan Rate (CFM) | Minimum Ventilation Rate Required (CFM) | Compliant?
[5 empty] | 0 | Yes/No
[5 empty] | Add Ventilation Fan | Remove Last
15 | Indicate where in the construction documents these requirements can be verified
Note on B7: 2019 Updates: If Yes is checked in 01 or 02 then row 3-13 grey out
Note on H18: Sally Blair: "Yes" if column 12>= column 13
Note on G19: Sally Blair: would duplicate user input rows on row 18

## K. Elevator
|  | User input |  |  | auto calculated |  | From another Table | From look up table
K. ELEVATOR LIGHTING AND VENTILATION
This table includes all elevator lighting and ventilation systems within the scope of the permit application to show compliance with the requirements of §120.6(f)/ §160.7.
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Lighting §120.6(f)1 & §120.6(f)3 / §160.7
Elevator Name or Item Tag | Elevator Area (ft2) | Fixture Name or Item Tag | Watts per Fixture | Number of Fixtures | Power per Design (W) | Maximum Power Allowed1 (W) | Controls
[5 empty] | (equals 04*05) | = '0.6*B8 | Dropdown
[5 empty] | (equals 04*05) | (grey and blank) | Dropdown
|  | Total Design Watts |  |  | (= sum of column 06) | (= sum of column 07)
[5 empty] | Add Fixture | Remove Last Fixture
09 | 10 | 11 | 12 | 13 | 14 | 15
Name or Item Tag | Conditioned Cab? | Ventilation §120.6(f)2 & §120.6(f)3/ §160.7 |  |  |  |  | Controls
|  | Fan Power (Watts) | Design Airflow (CFM) | Design Watts per CFM | Maximum Watts per CFM Allowed | Controls | Occupancy sensors provided
pull from 01 | Dropdown |  |  | #DIV/0! | 0.33 | Dropdown
1 FOOTNOTE: 0.6 watts per ft2 allowed per §120.6(f)1. Interior signal lighting and display lighting not included in power density calculation. |  |  |  |  | Add Elevator | Remove Last
16 | Indicate where in the construction documents these requirements can be verified
Occupancy sensors provided
Occupancy sensors provided
| Conditioned Drpdn |  |  |  |  | Controls
| Yes |  |  |  |  | Occupancy sensors provided
No
Note on G8: Sally Blair: If 07<06 trigger note in Table D row 9.
Note on G9: October 2019 Update: When the "Add Fixture" button is used the "maxiumum power allowed" cell in the added row should be gray with no value. The sum of the "maximum power allowed" should match the value in the first row of K.07
Note on F11: 2019 Update: ability to add (and remove) multiple fixtures incase elevator has more than one fixture type. Table can now expand columns 2-7 and sum up columns 5 and 6
Note on A15: Ben Lalor: Should pull elevator ID not fixture ID
Note on F15: Sally Blair: If 14<13 trigger note in Table D row 10.
Note on F16: Sally Blair: Duplicates columns 01-08 and 09-15
Note on B30: Sally Blair: grey out columns 11-15 if selected.

## N. Commercial Kitchen
0 | User input |  |  |  |  | auto calculated |  |  | From another Table | From look up table
N. COMMERCIAL KITCHEN EXHAUST AND VENTILATION
This table contains all new or replacement hoods being installed within the scope of the permit application. The inputs within Table N are used to demonstrate compliacne within §140.9(b).
Kitchen Ventilation §140.9(b)2
01 | ¨ | Existing kitchen hoods not being replaced as part of an addition or alteration (do not need to meet requirements) | [6 empty] | << Greys out entire table
Requirements
02 | Replacement Air to Hood Compliance Method §140.9(b)1A
Dropdown
03 | Mechanically cooled or heated makeup air delivered to any space with a kitchen hood is designed per 140.9(b)2A to not exceed the greater of:
Dropdown
04 | Location that is supplying transfer air:
05 | The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and is designed to have one of the following per 140.9(b)2B:
Dropdown
Kitchen Exhaust: Airflow Rate §140.9(b)1B
01 | Kitchen Name or Tag |  | Compliance Method per §140.9(b)1B |  |  | Dropdown
02 | 03 | 04 | 05 | 06 | 07 | 08
Name or Item Tag | Hood Type1 | Hood Style | Hood Length (ft) | Equipment Duty | Design Hood Exhaust Rate CFM | Max Hood Exhaust Rate Allowed CFM
| Dropdown | Dropdown |  | Dropdown
<< Example of add hood button
[7 empty] | Add Hood | Remove Last
1 FOOTNOTE: Type II hoods do not have a max hood exhaust air rate per Part 6 §140.9(b)1B. | [6 empty] | Add Kitchen | Remove Last
Equipment Duty
Light Duty
| Hood Type | Hood Style |  | Medium Duty
| Type I | Wall-mounted Canopy |  | Heavy Duty |  | Compliance Method Dropdown 01
| Type II | Single Island |  | Extra Heavy Duty |  | Type I hood design exhaust rates do not exceed the maximum allowed per §140.9(b)1 as documented below.
|  | Double Island |  |  |  | NA: Kitchen/ dining facility has a total Type I and Type II hood exhaust rate < 5,000 cfm.
|  | Eyebrow |  | Equipment Duty |  | NA: 75% of the total Type I and Type II exhaust replacement air is transfer air that would otherwise be exhausted.
|  | Backshelf / Passover |  | Light Duty |  | NA: Existing hoods are being replaced as part of an addition or alteration.
Medium Duty
Equipment Duty
Light Duty
Medium Duty
Heavy Duty
N.02 Compliance Method Dropdown
Providing replacement air directly to the hood(s) that does not exceed 10% of the hood(s) exhaust rate.
Not providing replacement air directly to the hood(s)
N.03 Dropdown
The supply flow required to meet the space heating and cooling load
The hood exhaust flow minus the available transfer air from adjacent spaces.
NA: Make up air is not mechanically cooled or heated
N.05 Dropdown
At least 50% of all replacement air is transferred air that would otherwise be exhausted
Demand ventilation system(s) on at least 75% of the exhaust air per 140.9(b)2Bii
Listed energy recovery devices with a sensible heat recovery effectiveness of > 40 on at least 50% of the total exhaust airflow
A minimum of 75% of makeup air volume having a total of no more than 60°F and uncooled or cooled without the use of mechanical cooling
NA: Not a kitchen /dining facility having a total Type I and Type II kitchen hood exhaust airflow rate > 5,000 cfm
Note on A4: 2019 Updates: 6.9.20 Update: keeping Kitchen Exhaust Section initially triggered with Table N. When Table N is triggered only N.01,02,03,05 and the kitchen exhaust section are initially triggered. N.04 is triggered through the choices made in this table.
Note on C7: 2019 Updates: When user selects 01, the rest of the table should grey out, all requirements are NA
Note on A17: 2019 Updates: Triggers only when 03 = "not exceed the hood exhaust flow minus the available transfer air…"
Note on G28: 11.21.21: See Table 140.9-A C for rate, then multiply by column 05.
Note on H31: Ben Lalor: ability to add a kitchen, instead of just adding a new row like the add hood button, add kitchen would replicate 01-08 and add hood remove hood buttons, only one set of add kitchen buttons should stay with the top kitchen.
Note on E32: Sally Blair: Custom drropdown for the following selections in column 04: - Wall Mounted Canopy - Single Island - Double Island
Note on B36: Sally Blair: This selection should grey out columns 04-06 & 08
Note on G37: Sally Blair: All 3 of these "NA" options should grey out columns 04-06 & 08
Note on E38: Sally Blair: Custom drropdown for the following selections in column 04: - Eyebrow
Note on E42: Sally Blair: Custom drropdown for the following selections in column 04: - Backshelf/ Passover

## R. PoolSpa
| User input |  | auto calculated |  |  |  | From another Table | From look up table
THIS ENTIRE TABLE IS NEW FOR 2022
R. POOL & SPAs
This table documents compliance with mandatory pool/spa requirments in §110.4/§160.7.
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Pool/ Spa Description | Pool/Spa Service Type | Efficiency1 | On/Off Control | Instructions & Covers | Electric Resistance Heating | Piping | Pool Directional Inlets & Pump Control
| Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
1 FOOTNOTE: CEC's appliance efficiency database, the Modernized Appliance Efficiency Database System (MAEDBS), is available online at https://cacertappliances.energy.ca.gov/Pages/ApplianceSearch.aspx.
| Type Dropdown | Efficiency dropdown | Control Dropdown | Cover Dropdown | Elec Resistance Dropdown | Piping Dropdown | Inlet Dropdown
| Serves multiple tenants or public | Equipment subject to State/federal appliance efficiency standards is in the CEC's directory of certified equipment | Includes on-off switch mounted on outside of heater allowing shutting off heater without adjusting thermostat | Heated outdoor pools/spas must include cover and weatherproof instruction for proper care of when cover is used | No electric resistance heating used | >= 36 in of pipe installed between filter & heater or dedicated suction and return lines to allow for the future addition of solar heating equipment | Has directional inlets to mix the pool water & control mechanism to allow pumps to run only during off-peak electric demand period and for min time necessary
| Serves one tenant |  |  | NA: Pool/spa not heated | Listed package units with fully insulated enclosures, and with tight-fitting covers that are insulated to at least R-6 | Built-in/built-up connections installed to allow for future addition of solar heating equipment | NA: Spa
Pools/spas where >= 60% of annual heating energy is from site solar energy or recovered energy
Additional Requirements for Pool/ Spa Serving One Tenant §150.0(p)
| Yes | Not Applicable | Requirement
09 | ¨ |  | All pump flow rates shall be calculated using H = C × F2 WHERE: H is the total system head in feet of water F is the flow rate in gallons per minute (gpm) C is a coefficient based on the volume of the pool (0.0167 for pools less than or equal to 17,000 gallons & 0.0082 for pools greater than 17,000 gallons)
10 | ¨ |  | Filtration pumps shall be sized, or if programmable, shall be programmed, so that the filtration flow rate is not greater than the rate needed to turn over the pool water volume in 6 hours or 36 gpm, whichever is greater.
11 | ¨ |  | Pump motors used for filtration shall meet the applicable federal standard in 10 CFR 431.465.
12 | ¨ | ¨ | Each auxiliary pool load shall be served by either separate pumps or the system shall be served by a multispeed pump if pump hp >= 1. - Multispeed pumps shall have controls which default to the filtration flow rate when no auxiliary pool loads are operating; and - For multispeed pumps, the controls shall default to the filtration flow rate setting within 24 hours and shall have an override capability for servicing.
13 | ¨ |  | System Piping must meet the following requirements: - A length of straight pipe that is greater than or equal to at least 4 pipe diameters shall be installed before the pump; and - Pool piping shall be sized so that the velocity of the water at maximum flow for auxiliary pool loads does not exceed 8 feet per second in the return line and 6 feet per second in the suction line; and - All elbows shall be sweep elbows or of an elbow-type that has a pressure drop of less than the pressure drop of straight pipe with a length of 30 pipe diameters.
14 | ¨ |  | Filters shall be at least the size specified in NSF/ANSI 50 for public pool intended applications.
15 | ¨ |  | Minimum diameter of backwash valves shall be 2 inches or the diameter of the return pipe, whichever is greater.
Note on B12: 11.21.21: Triggers "Additional Requirements…" subtable below.

## S. LMCI
| User input |  |  | auto calculated |  | From another Table | From look up table
P S. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ |  |  |  |  | fds
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | LMCI-PRC--E Covered Process | o | o
Note on A4: Sally Blair: Need to update URL when available
Note on A7: Sally Blair: this defaults to "Yes" and if the user moves it, the note in Table D row 11 shows up.

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/ HERS Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Designer Name: | Responsible Designer Signature:
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
[d:OnlyUI] The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-PRC form. [d:/OnlyUI]
Diane, in schema this needs to allow more than one responsible person.
?
Add Responsible Person
Remove Last
Note on F13: 2019 Update: This button should duplicate this table in the pdf, but the user input fields should be blank, but editable by the user.
Note on B15: UI Only: Table tip only applies to UI, does not apply to report generator.