CERTIFICATE OF INSTALLATION

This Certificate of Installation documents the installation of process system features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies.

| Project Name: | Enforcement Agency: |
| --- | --- |
| Dwelling Address: | Permit Number: |
| City and Zip Code: | Date Permit Issued: |

| A. GENERAL INFORMATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | Project Location (city): |  | 05 | Authority Having Jurisdiction: |  |
| 02 | Zip Code: |  | 06 | Building Permit #: |  |
| 03 | Date of Permit Set used for construction: |  | 07 | Date of As-built Set: |  |
| 04 | Name of Permit Set used for construction: |  | 08 | Name of As-built Set: |  |

| B. INSTALLER SCOPE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| This table indicates construction systems and materials documented on this Certificate of Installation. |  |  |  |  |  |
| 01 |  |  |  |  |  |
| Electrical |  |  |  |  |  |
| □ | Elevator Lighting | □ | Escalator and Moving Walkways Controls |  |  |
| HVAC |  |  |  |  |  |
| □ | Refrigerated Spaces Underslab Heating | □ | Parking Garage Exhaust | □ | Elevator Ventilation Controls |
| □ | Computer Rooms | □ | Commercial Kitchen Ventilation | □ | Laboratory/Factory Exhaust & Fume Hood |
| Insulation |  |  |  |  |  |
| □ | Refrigerated Spaces Exterior Insulation |  |  |  |  |
| Plumbing |  |  |  |  |  |
| □ | Process Boilers | □ | Compressed Air Systems |  |  |
| Refrigeration |  |  |  |  |  |
| □ | Food/Beverage Stores >= 8,000 ft2 | □ | Refrigerated Space >= 3,000 ft2 Fan Powered Evaporators | □ | Refrigerated Space >= 3,000 ft2 Condensers |
| □ | Refrigerated Space >= 3,000 ft2 Compressors | □ | Refrigerated Space >= 3,000 ft2 Infiltration Barriers | □ | Refrigerated Space >= 3,000 ft2 Transcritical CO2 Fan-powered Gas Coolers (new only) |
| Specialty |  |  |  |  |  |
| □ | Commercial Kitchen Hood | □ | Escalator and Moving Walkways Controls | □ | Pool/Spa |
| □ | Controlled Environment Horticulture Lighting | □ | New Steam Traps |  |  |

| C. COMPLIANCE RESULTS |  |
| --- | --- |
| This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance. If the installation is not equal or better, Section 10-103(a)2B requires the Certificate of Compliance form to be revised accordingly to demonstrate compliance. |  |
| 01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE |
| Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply. |  |
| The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly. |  |

D. EXCEPTIONAL CONDITIONS

This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact requirements documented on the Certificate of Compliance.

E. INSTALLER NOTES

This table includes remarks made by the installer to the Authority Having Jurisdiction.

F. INSTALLATION DETAILS The following tables indicate performance requirements as documented on the permitted Certificate of Compliance for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.

| Refrigerated Warehouse/Space Fan Powered Evaporators |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| Name or Item Tag | Model # | Motor HP | Phase | Type or Efficiency | Fan Controls | Evaporator Compliance |
| Per NRCC |  |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |

| Refrigerated Warehouse/Space Condensers (Air-cooled, Water-cooled, Evaporative-cooled, Adiabatic) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 |
| Name or Item Tag | Model # | Condenser Location | Temp Setpoint Controls | Variable Speed Control | Refrigerant Type | Efficiency (Btuh/W) | Condenser Compliance |
| Per NRCC |  |  |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |  |

| Refrigerated Warehouse/Space Compressors |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 |
| Name or Item Tag | Model # | Condensing Temp | Variable Speed Control | Variable Volume Ratio | Compressor Compliance |
| Per NRCC |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |

| Refrigerated Warehouse/Space Infiltration Barriers and Automatic Door Closers |  |  |  |
| --- | --- | --- | --- |
| 01 | 02 | 03 | 04 |
| Room ID/ Description | Infiltration Barrier | Door Closure | Infiltration Barrier Compliance |
| 1 FOOTNOTE: Infiltration barriers include strip curtains, automatically closing door, or an air curtain designed by the manufacturer |  |  |  |

| Transcritical CO2 Fan-powered Gas Coolers |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 |
| Name or Item Tag | Variable Speed Control | Gas Cooler Pressure Controls | Design Condensing Temperatures | Efficiency (Btuh/W) | Compliance |
| Per NRCC | Variable speed fan(s) provided controlled per §120.6(a)8D | Condensing temp reset per §120.6(a)4F and cooler pressure setpoint maximizes efficiency |  |  |  |
| As-built Conditions |  |  |  |  |  |

| Refrigerated Warehouse/Space Exterior Surface Insulation |  |  |  |  |
| --- | --- | --- | --- | --- |
| 01 | □ | Exterior surfaces of refrigerated warehouses/spaces are insulated at least to the R-values in TABLE 120.6-A (see below). |  |  |
| TABLE 120.6-A REFRIGERATED WAREHOUSE/SPACE INSULATION |  |  |  |  |
| 02 |  | 03 | 04 | 05 |
| Space |  | Surface | Minimum R-Value | Insulation Compliance |
| Freezers |  | Roof/ Ceiling | 40 |  |
|  |  | Wall | 36 |  |
|  |  | Floor | 35 |  |
|  |  | Floor with all heating from productive refrigeration capacity1 | 20 |  |
| Coolers |  | Roof/ Ceiling | 28 |  |
|  |  | Wall | 28 |  |
| 1 FOOTNOTE: All underslab heating is provided by a heat exchanger that provides refrigerant subcooling or other means that result in productive refrigeration capacity on the associated refrigerated system. |  |  |  |  |

| Refrigerated Warehouse/Space Underslab Heating |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Room ID/ Description | Compliance Method | Underslab Heating Compliance |
| Per NRCC |  |  |
| As-built Conditions |  |  |

| Condensers Serving Commercial Refrigeration System |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance. |  |  |  |  |  |  |
| The project includes replacement condensers that meet the following conditions: - attached compressor system Total Heat of Rejection does not increase and; - less than 25 percent of both the attached compressors and the attached display cases are new. |  |  |  |  |  |  |
| All equipment, appliances and components serving the refrigeration system have been certified by the Energy Commission as compliant with Title 20 and listed in the Modernized Appliance Efficiency Database System found at https://cacertappliances.energy.ca.gov/Pages/Search/AdvancedSearch.aspx.1 |  |  |  |  |  |  |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| Name or Item Tag | Condenser Type | Variable Speed Control | Temp Setpoint Controls | Specific Efficiency (Btuh/W) | Fin Density | Condenser Compliance |
| Per NRCC |  |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |

| Compressors and Condensing Units Serving Commercial Refrigeration System |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Name or Item Tag | Saturation suction temperature control (SST) | Condenser Compliance |
| Per NRCC |  |  |
| As-built Conditions |  |  |

| Refrigerated Display Cases |  |  |  |
| --- | --- | --- | --- |
| 01 |  |  | 02 |
| Lighting Controls for Refrigerated Display Cases & Illuminated Glass Doors of Walk-in Coolers/ Freezers |  |  | Refrigerated Display Case Compliance |
| Per NRCC |  |  |  |
| As-built Conditions | □ | Timeclock: Turn off lighting power automatically during non-business hours |  |
|  | □ | Motion Sensor: Reduce lighting power by at least 50% within 30 minutes after the nearby area is vacated |  |
| Heat Recovery of Refrigeration System |  |  |  |
| Per NRCC |  |  |  |
| As-built Conditions |  |  |  |

| Transcritical CO2 Fan-powered Gas Coolers |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 |
| Name or Item Tag | Variable Speed Control | Gas Cooler Pressure Controls | Design Condensing Temperatures | Efficiency (Btuh/W) | Compliance |
| Per NRCC | Variable speed fan(s) provided controlled per §120.6(b)5D | Condensing temp reset per §120.6(b)1A and cooler pressure setpoint maximizes efficiency |  |  |  |
| As-built Conditions |  |  |  |  |  |

| Enclosed Parking Garage Exhaust Controls |  |  |  |
| --- | --- | --- | --- |
|  | Per C of C | As-built | Exceptions |
| 01 | □ | □ | Garage is expected to have vehicles with non-gasoline combustion engines for > 20% of the parked vehicles per Exception 1 to §120.6(c) |
| 02 | □ | □ | Project scope includes an addition or alteration to an existing garage where < 10,000 cfm of new exhaust capacity is being added Exception 2 to §120.6(c) |
|  |  |  | Requirements |
| 03 | □ | □ | Exhaust fan control modulates airflow rates <= 50% design capacity when contaminant levels are maintained per §120.6(c)1 |
| 04 | □ | □ | Fan control or device allows fan motor demand ≤ 30% design wattages at 50% of design airflow per §120.6(c)2 |
| 05 | □ | □ | Design includes monitoring CO with a sensor density >= 1 per 5,000 ft2 per §120.6(c)3 |
| 06 | □ | □ | CO sensors are located in the highest expected concentration locations, with at least two per proximity zone per §120.6(c)3 |
| 07 | □ | □ | Design CO sensor setpoint <= 25 ppm per §120.6(c)4 |
| 08 | □ | □ | Occupied garage design maintains negative pressurization per §120.6(c)6 |
| 09 | □ | □ | Designed occupied total ventilation rate >= 0.15 CFM/ ft2 §120.6(c)5 |
| CO Sensors shall be: A. Certified by the manufacturer to be accurate within plus or minus 5% of measurement. B. Factory calibrated C. Certified by the manufacturer to drift no more than 5% per year. D. Certified by the manufacturer to require calibration no more frequently than once a year. E. Monitored by a control system. The system shall have logic that automatically checks for sensor failure by the following means. Upon detection of a failure, the system shall reset to design ventilation rates and transmit an alarm to the facility operators. i. If any sensor has not been calibrated according to the manufacturer's recommendations within the specified calibration period, the sensor has failed. ii. During unoccupied periods the system compares the readings of all sensors, e.g., if any sensor is more than ppm above or below the average of all sensors for longer than 4 hrs, the sensor has failed. iii. During unoccupied periods the system compares the readings of sensor in the same proximity zone, e.g. if the 30 minute rolling average for any sensor in a proximity zone is more than 15 ppm above or below the 30 minute rolling average for other sensor(s) in that proximity zone, the sensor has failed. |  |  |  |

| Enclosed Parking Garage Exhaust |  |  |  |
| --- | --- | --- | --- |
| 01 | 02 | 03 | 04 |
| Fan Name or Item Tag | Parking Garage Area (ft2) | Ventilation Fan Rate (CFM) | Exhaust Compliance |
| Per C of C |  |  |  |
| As-built Conditions |  |  |  |

| Process Boilers |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| Name or Item Tag | Model # | Rated Input Capacity per Boiler (Btu/h) | Fan Controls | Combustion Air Shutoff | Stack Design and Controls | Process Boiler Compliance |
| Per NRCC |  |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |

| Compressed Air Systems |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| System Name/ Description | Model # | Trim Compressor | Controls | Monitoring | Service Line Size1 | Compressed Air Compliance |
| Per NRCC |  |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |
| 1 FOOTNOTE: Service line piping are pipes that deliver compressed air from distribution piping to end uses. |  |  |  |  |  |  |

| Elevator Lighting and Ventilation |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lighting |  |  |  |  |  |  |  |  |  |  |
| 01 |  | 02 |  | 03 |  | 04 |  | 05 |  | 06 |
| Elevator Name or Item Tag |  | Fixture Name or Item Tag |  | Number of Fixtures |  | Watts per Fixture |  | Total Power |  | Elevator Lighting Compliance |
| Per C of C |  |  |  |  |  |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |  |  |  |  |
| Ventilation |  |  |  |  |  |  |  |  |  |  |
| 07 | 08 |  | 09 |  | 10 |  | 11 |  | 12 |  |
| Name or Item Tag | Fan Power (Watts) |  | Airflow (CFM) |  | Watts per CFM |  | Controls |  | Elevator Ventilation Compliance |  |
| Per C of C |  |  |  |  |  |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |  |  |  |  |

Escalators and Moving Walkway Speed Controls

The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.

Escalators and moving walkways located in airports, hotels, and transportation function areas shall automatically slow to the minimum permitted speed in accordance with ASME A17.1/CSA B44 when not conveying passengers.

| Computer Room Systems |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 |
| Computer Room Name/ID | Economizer | Reheat Controls | Humidification | Sensible Cooling Capacity (kBtuh) | Total Fan System Power (Watts) | Fan Controls | Containment | Computer Room Compliance |
| Per NRCC |  |  |  |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |  |  |

| Computer Room Uninterruptible Power Supply (UPS) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 |
| Computer Room Name/ID | Alternating Current Output UPS Compliance Method | Type of UPS | UPS Rated Output Power (W) | Efficiency | Compliance |
| Per NRCC |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |

Commercial Kitchen Exhaust & Ventilation

Kitchen Ventilation

The following ventilation requirements have been included on the permitted Certificate of Compliance to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.

Providing replacement air directly to the hood(s) that does not exceed 10% of the hood(s) exhaust rate.

Not providing replacement air directly to the hood(s).

Mechanically cooled or heated makeup air delivered to any space with a kitchen hood does not exceed the supply flow required to meet the space heating and cooling load.

Mechanically cooled or heated makeup air delivered to any space with a kitchen hood does not exceed the hood exhaust flow minus the available transfer air from adjacent spaces.

The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and at least 50% of all replacement air is transferred air that would otherwise be exhausted.

The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and demand ventilation system(s) on at least 75% of the exhaust air.

The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and listed energy recovery devices with a sensible heat recovery effectiveness of > 40 on at least 50% of the total exhaust airflow.

The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and a minimum of 75% of makeup air volume having a total of no more than 60°F and uncooled or cooled without the use of mechanical cooling.

| Kitchen Hood |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| Name or Item Tag | Hood Type | Hood Style | Equipment Duty | Hood Length (ft) | Hood Exhaust Rate (CFM) | Kitchen Exhaust Compliance |
| Per C of C |  |  |  |  |  |  |
| As-built |  |  |  |  |  |  |

| Laboratory And Factory Exhaust and Fume Hoods |  |  |  |  |
| --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 |
| Zone/System or Item Tag | Airflow Reduction | Transfer Air | Fan Power | Hood Sash Closure |
| Per NRCC |  |  |  |  |
| As-built Conditions |  |  |  |  |

| Controlled Environment Horticulture Lighting |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 |
| Zone/System or Item Tag | Photosynthetic Photon Efficacy (PPE) | Timeswitch Lighting Controls | Multilevel Lighting Controls | Electrical System Monitoring | CEH Compliance |
| Per NRCC |  |  |  | Electrical system capable of monitoring electrical energy usage of horticulture lighting load |  |
| As-built Conditions |  |  |  |  |  |

| Space Conditioning for Plant Production |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| System Name/ Description | Dehumidification System for Indoor Grow CEH Compliance Method | CEH Compliance |

| Steam Traps in Industrial Facilities |  |  |  |
| --- | --- | --- | --- |
| 01 | 02 | 03 | 04 |
| Fault Detection Diagnostics Monitoring |  | Strainer Installation | Steam Traps Compliance |
| Update Interval | Alarm Display |  |  |
| Per NRCC |  |  |  |
| As-built Conditions |  |  |  |

| Pool & Spas |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 |
| Pool/Spa Description | Efficiency | On/Off Control | Instructions & Covers | Electric Resistance Heating | Piping | Directional Inlets & Pump Control | Pool/Spa Compliance |
| Per C of C | Equipment subject to State/federal appliance efficiency standards is in the CEC's directory of certified equipment | Includes on-off switch mounted on outside of heater allowing shutting off heater without adjusting thermostat |  |  |  |  |  |
| As-built Conditions |  |  |  |  |  |  |  |

Additional Requirements for Pool/ Spa Serving One Tenant

All pump flow rates shall be calculated using H = C × F2 WHERE: H is the total system head in feet of water F is the flow rate in gallons per minute (gpm) C is a coefficient based on the volume of the pool (0.0167 for pools less than or equal to 17,000 gallons & 0.0082 for pools greater than 17,000 gallons)

Filtration pumps shall be sized, or if programmable, shall be programmed, so that the filtration flow rate is not greater than the rate needed to turn over the pool water volume in 6 hours or 36 gpm, whichever is greater.

Pump motors used for filtration shall meet the applicable federal standard in 10 CFR 431.465.

Each auxiliary pool load shall be served by either separate pumps or the system shall be served by a multispeed pump if pump hp >= 1. - Multispeed pumps shall have controls which default to the filtration flow rate when no auxiliary pool loads are operating; and - For multispeed pumps, the controls shall default to the filtration flow rate setting within 24 hours and shall have an override capability for servicing.

System Piping must meet the following requirements: - A length of straight pipe that is greater than or equal to at least 4 pipe diameters shall be installed before the pump; and - Pool piping shall be sized so that the velocity of the water at maximum flow for auxiliary pool loads does not exceed 8 feet per second in the return line and 6 feet per second in the suction line; and - All elbows shall be sweep elbows or of an elbow-type that has a pressure drop of less than the pressure drop of straight pipe with a length of 30 pipe diameters.

Filters shall be at least the size specified in NSF/ANSI 50 for public pool intended applications.

Minimum diameter of backwash valves shall be 2 inches or the diameter of the return pipe, whichever is greater.

| Documentation Author's Declaration Statement |  |
| --- | --- |
| - I certify that this Certificate of Compliance documentation is accurate and complete. |  |
| Documentation Author Name: | Documentation Author Signature: |
| Company: | Signature Date: |
| Address: | CEA/HERS Certification Identification (if applicable): |
| City/State/Zip: | Phone: |
| Responsible Person's Declaration statement |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: - The information provided on this Certificate of Compliance is true and correct. - I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer). - The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. - The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. - I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy. |  |
| Responsible Designer Name: | Responsible Designer Signature: |
| Company : | Date Signed: |
| Address: | License: |
| City/State/Zip: | Phone: |

A. General Information

- This field is filled out automatically.

- Enter the Zip Code.

- Enter the Date of Permit Set used for construction.

- Enter the Name of Permit Set used for construction.

- Enter the Authority Having Jurisdiction.

- Enter the Building Permit #.

- Enter the Date of As-Built Set.

- Enter the Name of As-Built Set.

B. Project Scope

- Select applicable electrical components.

- Select applicable HVAC components.

- Select applicable insulation.

- Select applicable plumbing components.

- Select applicable refrigeration scope.

- Select applicable specialties.

C. Compliance Results

- This table is automatically filled with uneditable comments based on data entered in Section F.

D. Exceptional Conditions

- This table is automatically filled with uneditable comments because of selections made or data entered in tables throughout the form.

E. Additional Remarks

- Enter any notes or comments for the AHJ.

F. INSTALLATION DETAILS

Refrigerated Warehouse/Space Fan Powered Evaporators

- This field is filled out automatically.

- Enter the Model #.

- Motor HP: Select from dropdown.

- Phase: Select from dropdown.

- Type or Efficiency: Select from dropdown.

- Fan Controls: Select from dropdown.

- This field is filled out automatically.

Refrigerated Warehouse/Space Condensers (Air-cooled, Water-cooled, Evaporative-cooled, Adiabatic)

- This field is filled out automatically.

- Enter the Model #.

- Condenser Location: Select from dropdown.

- Temp Setpoint Controls: Select from dropdown.

- Variable Speed Control: Select from dropdown.

- Refrigerant Type: Select from dropdown.

- Enter the Efficiency (Btuh/W).

- This field is filled out automatically.

Refrigerated Warehouse/Space Compressors

- This field is filled out automatically.

- Enter the Model #.

- Condenser Temp: Select from dropdown.

- Variable Speed Control: Select from dropdown.

- Variable Volume Ratio: Select from dropdown.

- This field is filled out automatically

Refrigerated Warehouse/Space Infiltration Barriers and Automatic Door Closers

- This field is filled out automatically.

- Infiltration Barrier: Select from dropdown.

- Door Closure: Select from dropdown.

- This field is filled out automatically

Transcritical CO2 Fan-powered Gas Coolers

- This field is filled out automatically.

- Static text describing variable speed fan control requirement

- Static text describing gas cooler pressure control requirements

- Design Condensing Temperatures: Select from dropdown.

- Enter the Efficiency (Btuh/W).

- This field is filled out automatically.

Refrigerated Warehouse/Space Exterior Surface Insultation

- Select if exterior surfaces of refrigerated warehouses/spaces are insulated at least to the minimum R-values.

- Nothing to do for this column.

- Nothing to do for this column.

- Nothing to do for this column.

- This field is filled out automatically.

Refrigerated Warehouse/Space Underslab Heating

- This field is filled out automatically.

- Compliance Method: Select from the dropdown.

- This field is filled out automatically.

Condensers Serving Commercial Refrigeration System

- This field is filled out automatically.

- Condenser Type: Select from dropdown.

- Variable Speed Control: Select from dropdown.

- Temp Setpoint Controls: Select from dropdown.

- Enter the Specific Efficiency (Btuh/W).

- Fin Density: Select from dropdown.

- This field is filled out automatically.

Compressors and Condensing Units Serving Commercial Refrigeration System

- This field is filled out automatically.

- Saturation suction temperature control (SST): Select from dropdown.

- This field is filled out automatically.

Refrigerated Display Cases

- Select applicable lighting controls for refrigerated display cases & illuminated glass doors of walk-in coolers/ freezers.

- This field is filled out automatically.

Heat Recovery of Refrigeration System:

- Select from dropdown.

Transcritical CO2 Fan-powered Gas Coolers

- This field is filled out automatically.

- Static text describing variable speed fan control requirement

- Static text describing gas cooler pressure control requirements

- Design Condensing Temperatures: Select from dropdown.

- Enter the Efficiency (Btuh/W).

- This field is filled out automatically.

Enclosed Parking Garage Exhaust Controls

- Select the As-built box if the Exception applies.

- Select the As-built box if the Exception applies.

- Select the As-built box if the Requirement is met.

- Select the As-built box if the Requirement is met.

- Select the As-built box if the Requirement is met.

- Select the As-built box if the Requirement is met.

- Select the As-built box if the Requirement is met.

- Select the As-built box if the Requirement is met.

- Select the As-built box if the Requirement is met.

Enclosed Parking Garage Exhaust

- This field is filled out automatically.

- Enter the Parking Garage Area (ft2).

- Enter the Ventilation Fan Rate (CFM).

- This field is filled out automatically.

Process Boilers

- This field is filled out automatically.

- Enter the Model #.

- Rated Input Capacity per Boiler (Btu/h): Select from dropdown.

- Fan Controls: Select from dropdown.

- Combustion Air Shutoff: Select from dropdown.

- Stack Design and Controls: Select from dropdown.

- This field is filled out automatically.

Compressed Air Systems

- This field is filled out automatically.

- Enter the Model #.

- Trim Compressor: Select from dropdown.

- Controls: Select from dropdown.

- Monitoring: Select from dropdown.

- Service Line Size: Select from dropdown.

- This field is filled out automatically.

Elevator Lighting and Ventilation

- This field is filled out automatically.

- This field is filled out automatically.

- Enter the Lighting Number of Fixtures.

- Enter the Lighting Watts per Fixture.

- This field is filled out automatically.

- This field is filled out automatically.

- This field is filled out automatically.

- Enter the Ventilation Fan Power (Watts).

- Enter the Ventilation Airflow (CFM).

- This field is filled out automatically.

- Controls: Select from dropdown.

- This field is filled out automatically.

Escalators and Moving Walkway Speed Controls

- This table covers requirements for Escalators and moving walkways located in airports, hotels, and transportation function areas.

Computer Room Systems

- This field is filled out automatically.

- Economizer: Select from dropdown.

- Reheat Controls: Select from dropdown.

- Humidification: Select from dropdown.

- Enter the Sensible Cooling Capacity (kBtuh).

- Enter the Total Fan System Power (Watts).

- Fan Controls: Select from dropdown.

- Containment: Select from dropdown.

- This field is filled out automatically.

Computer Room Uninterruptible Power Supply (UPS)

- This field is filled out automatically.

- Alternating Current Output UPS Compliance Method: Select from dropdown.

- Type of UPS: Select from dropdown.

- Enter the UPS Rated Output Power.

- Enter the Efficiency.

- This field is filled out automatically.

Commercial Kitchen Ventilation

- This table covers commercial kitchen ventilation requirements.

Commercial Kitchen Hood

- This field is filled out automatically.

- Hood Type: Select the dropdown.

- Hood Style: Select the dropdown.

- Equipment Duty: Select the dropdown.

- Enter the Hood Length (ft).

- Enter the Hood Exhaust Rate (CFM).

- This field is filled out automatically.

Laboratory and Factory Exhaust and Fume Hoods

- Enter the Zone/System or Item Tag.

- Airflow Reduction: Select from dropdown.

- Transfer Air: Select from dropdown.

- Fan power: Select from dropdown.

- Hood Sash Closure: Select from dropdown.

Controlled Environment Horticulture Lighting

- This field is filled out automatically.

- Photosynthetic Photon Efficacy (PPE): Select from dropdown.

- Timeswitch Lighting Controls: Select from dropdown.

- Multilevel Lighting Controls: Select from dropdown.

- Static text describing electrical system monitoring requirement.

- This field is filled out automatically.

Space Conditioning for Plant Production

- Enter name or description of system.

- Dehumidification System for Indoor Grow CEH Compliance Method: Select from dropdown.

- This field is filled out automatically.

- This field is filled out automatically

Steam Traps in Industrial Facilities

- Update Interval Fault Detection Diagnostics Monitoring: Select from dropdown.

- Alarm Display Fault Detection Diagnostics Monitoring: Select from dropdown.

- Strainer Installation: Select from dropdown.

- This field is filled out automatically.

Pool & Spas

- This field is filled out automatically.

- Efficiency

- On/Off Control

- Instructions & Covers: Select from dropdown.

- Electric Resistance Heating: Select from dropdown.

- Piping: Select from dropdown.

- Directional Inlets & Pump Control: Select from dropdown.

- This field is calculated automatically.