| A. General Information |  |  |
| --- | --- | --- |
| 01 | Building Name |  |

| B. Design HERS Verified Central Water Heating Systems Information (other than HPWH) This table reports features of the water heating system other than HPWH system that were specified on the registered NRCC compliance document for this project. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value |

| B2. Design HERS Verified CHPWH System Information This table reports the water heating systems specified on the registered NRCC compliance document for this project. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 |  | 06 |  | 07 |  | 08 | 09 |  | 10 |  | 11 |  | 12 |  |
| Water Heating System ID or Name | Modeled Equipment Make and Model | Number of Water Heaters/ Compressors | Primary Tank Location | Primary Tank Volume |  | Primary Tank Total Insulation |  | Loop Tank Location |  | Loop Tank Volume | Loop Tank Total Insulation |  | Loop Pipe Insulation Thickness |  | Loop Tank Type |  | Simulated Equipment Make and Model |  |

| C. Installed HERS Verified Central Water Heating Systems Information This table reports features the water heating system other than HPWH systems that were specified on the registered NRCC compliance document for this project. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value |

| C2. Installed HERS Verified CHPWH System Information This table reports the water heating systems specified on the registered NRCC compliance document for this project. |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 |
| Water Heating System ID or Name | Modeled Equipment Make and Model | Number of Water Heaters/ Compressors | Primary Tank Location | Primary Tank Volume | Primary Tank Insulation | Loop Tank Location | Loop Tank Volume | Loop Tank Insulation | Loop Pipe Insulation Thickness | Loop Tank Type |

| D. Design HERS Verified Central Water Heating Distribution Systems Information This table reports the water heating distribution types specified on the registered NRCC compliance document for this project. |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |

| E. Installed HERS Verified Central Water Heating Distribution Systems Information This table reports the water heating distribution types specified on the registered NRCC compliance document for this project. |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |

| F. Installed HERS Verified Water Heater Manufacturer Information |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Manufacturer | Model Number |

| G. Mandatory Requirements for All Central Domestic Hot Water Systems |  |
| --- | --- |
| 01 | On systems that have a total capacity greater than 167,000 Btu/hr, outlets that require higher than service water temperatures as listed in the ASHRAE Handbook have separate remote heaters, heat exchangers, or boosters to supply the outlet with the higher temperature. (Section 110.3 (c)1) |
| 02 | Systems with circulating pumps or with electrical heat trace systems shall be capable of automatically turning off the system. (Section 110.3(c)2). |
| 03 | Unfired storage tanks are insulated with an external R-3.5 or combination of R-16 internal and external Insulation. (Section 110.3(c)4). |
| 04 | Recirculation loops shall meet the following requirements: - The recirculation pump is mounted on a vertical section of the return line, OR an automatic air release valve is installed on a riser at least 12 inches in length, on the inlet side of the recirculation pump, no more than 4 feet from the pump. (Section 110.3(c) 4A). - A check valve is located between the recirculation pump and the water heater. (Section 110.3(c) 4B). - A hose bib is installed between the pump and the water heating equipment with an isolation valve between the hose bib and the water heating equipment. (Section 110.3(c) 4C). - Isolation valves shall be installed on both sides of the pump, of which the valve required in 110.3(c)4C can be one. (Section 110.3(c)4D). - The cold water piping and the recirculation loop piping shall not be connected to the hot water storage tank drain port. (Section 110.3(c)4E). - A check valve shall be installed on the cold water supply line between the hot water system and the next closest tee on the cold water supply line. (Section 110.3(c) 4F). |
| 05 | Instantaneous water heaters with an input greater than 6.8 kBTU/hr. (2kW) shall have isolation valves on both the cold water supply and the hot water line. (110.3 (c) 6). |
| 06 | All domestic hot water piping shall be insulated as specified in Section 609.11 of the California Plumbing Code. - Insulation buried below grade must be installed in a waterproof and non-crushable casing or sleeve. - Piping that penetrates framing members shall not be required to have pipe insulation for the distance of the framing penetration. Piping that penetrates metal framing shall use grommets, plugs, wrapping or other insulating material to assure that no contact is made with the metal framing. Insulation shall butt securely against all framing members. - Piping installed in interior or exterior walls that is surrounded on all sides by at least 1 inch (2.5 cm) of insulation. - Piping installed in crawlspace with a minimum of 1 inches (2.5 cm) of crawlspace insulation above and below. - Piping installed in attics with a minimum of 4 inches (10 cm) of attic insulation on top. - Pipe insulation shall fit tightly and all elbows and tees shall be fully insulated. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| H. HERS-Verified Multiple Recirculation Loops for DHW Systems Serving Multiple Dwelling Units Requirements All distribution systems listed on this compliance document shall comply with these requirements. |  |
| --- | --- |
| 01 | All buildings with 8 or more dwelling units have a minimum of 2 recirculation loops. |
| 02 | Each loop roughly serves the same number of dwellings. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table.

| I. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 |  |

| Documentation Author's Declaration Statement |  |  |
| --- | --- | --- |
| - I certify that this Certificate of Verification documentation is accurate and complete. |  |  |
| Name: | Signature: |  |
| Company: | Date: |  |
| Address: | CEA / HERS Certification Identification (If applicable): |  |
| City/State/Zip: | Phone: |  |
| Responsible Person's Declaration statement |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: - The information provided on this Certificate of Verification is true and correct. - I am the certified HERS Rater who performed the verification identified and reported on this Certificate of Verification (responsible rater). - The installed features, materials, components, manufactured devices, or system performance diagnostic results that require HERS verification identified on this Certificate of Verification comply with the applicable requirements in Reference Nonresidential Appendices NA1 and NA2, and the requirements specified on the Certificate of Compliance for the building approved by the enforcement agency. - The information reported on applicable sections of the Certificate(s) of Installation (NRCI), signed and submitted by the person(s) responsible for the construction or installation conforms to the requirements specified on the Certificate(s) of Compliance (NRCC) approved by the enforcement agency. - I will ensure that a registered copy of this Certificate of Verification shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Verification is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |
| BUILDER OR INSTALLER INFORMATION AS SHOWN ON THE CERTIFICATE of Installation |  |  |
| Company Name (Installing Subcontractor or General Contractor or Builder/Owner): |  |  |
| Responsible Builder/Installer Name: | CSLB License: |  |
| HERS PROVIDER DATA REGISTRY INFORMATION |  |  |
| Sample Group Number (if applicable): | Dwelling Test Status in Sample Group (if applicable): |  |
| HERS RATER INFORMATION |  |  |
| HERS Rater Company Name: |  |  |
| Responsible Rater's Name: |  | Responsible Rater's Signature: |
| Responsible Rater's Certification Number w/ this HERS Provider: |  | Date Signed: |

A. General Information

This table reports the building name as specified on the Registered NRCC.

B. Design HERS Verified Central Water Heating Systems Information

This table reports the water heating system features that were specified on the registered NRCC compliance document for this project. This section is for information/verification purposes only and requires no user input.

B2. Design HERS Verified Dwelling Unit HPWH System Information

This table reports the water heating system features that were specified on the registered NRCC compliance document for this project. This section is for information/verification purposes only and requires no user input.

C. Installed HERS Verified Central Water Heating Systems Information

This table reports the water heating system information that is being installed. Require one line for each installed water heater.

01 Water Heating System ID or Name – Reference information from NRCC.

02 Water Heating System Type – Reference information from NRCC. The different kinds of water heating system type are DHW or Combined Hydronic.

03 Water Heater Type – Information from NRCC. The different kinds of water heaters are Large/Commercial Storage, Small/Consumer Storage, Residential-Duty Commercial Storage, Heat Pump, Boiler, Large/Commercial Instantaneous, Small/Consumer Instantaneous, Residential-Duty Commercial Instantaneous or Indirect.

04 # of Water Heaters in system – Reference information from NRCC.

05 Water Heater Storage Volume (gal) – User input. Value may be N/A if water heater type is instantaneous with zero storage.

06 Fuel Type – Reference information from NRCC. The different kinds of fuel types are natural gas, propane, oil, or electricity.

07 Rated Input Type – Reference information from NRCC. For natural gas, propane and oil fuel type the input type is Btu/Hr. For electric the input type is kW.

08 Rated Input Value – User input. Numerical value of the rated input. Must be equal to or less than value indicated on the NRCC.

09 Heating Efficiency Type – Reference information from NRCC. Different efficiency types are Energy Factor, AFUE, UEF and Thermal Efficiency.

10 Heating Efficiency Value – User input. Numerical value of the Heating Efficiency. Must be equal to or higher efficiency than value indicated on the NRCC.

11 Standby Loss – User input. Must be equal to or less than value indicated on the NRCC. Value may be N/A if NRCC value is N/A.

12 Exterior Insul. R-Value – User input. Must be equal to or higher than value indicated on the NRCC. Value may be N/A if NRCC value is N/A.

C2. Installed HERS Verified Dwelling Unit HPWH System Information

This table reports the water heating system information that is being installed. Require one line for each installed water heater.  Require one line for each installed water heater.

01 Water Heating System ID or Name – Reference information from Table B2.

02 Modeled Equipment Make and Model – User input must be equal to the value indicated on Table B2 as default and allow user to override with an equivalent system based on the simulated equipment in Table B2.

03 Number of Water Heaters/ Compressors – User input, must be equal to the value indicated on table B2.

04 Primary Tank Location – Reference information from Table B2.

05 Primary Tank Volume – User input, must be equal to or higher than the value indicated on table B2.

06 Primary Tank Insulation – User input, must be equal to or higher than value indicated on table B2.

07 Loop Tank Location – Reference information from Table B2.

08 Loop Tank Volume – User input, must be equal to or higher than the value indicated on table B2.

09 Loop Tank Insulation – User input, must be equal to or higher than value indicated on table B2.

10 Loop Pipe Insulation Thickness – User input, must be equal to or higher than the value indicated on table B2.

11 Loop Tank – Reference information from Table B2.

D. Design HERS Verified Central Water Heating Distribution Systems Information

This table reports the water heating distribution types specified on the registered NRCC compliance document for this project.

E. Installed HERS Verified Central Water Heating Distribution Systems Information

01 Water Heating System ID or Name – Reference information from NRCC.

02 Central DHW System Distribution Type = Reference information from NRCC.

03 Dwelling Unit DHW System Distribution Type = Reference information from NRCC.

F. Installed HERS Verified Central Water Heater Manufacturer Information

This table reports the manufacturer information of the installed water heater(s). Require one line for each installed water heater.

01 Water Heating System ID or Name – Reference information from NRCC.

02 Manufacturer – User input. Enter the name of the water heater manufacturer.

03 Model Number – User input. Enter the model number of the water heater.

G. Mandatory Requirements for All Central Domestic Hot Water Recirculation Systems

This table lists the requirements for all central recirculation systems. HERS rater must ensure all the requirements in this table are met.

H. HERS-Verified Multiple Recirculation Loops for DHW Systems Serving Multiple Dwelling Units Requirements

This table lists the requirements for HERS Verified multiple recirculation loop credit for central recirculation systems.

| A. General Information |  |  |
| --- | --- | --- |
| 01 | Building Name | <<User input>> |

| B. Design HERS Verified Central Water Heating Systems Information This table reports the water heating system features that were specified on the registered NRCC compliance document for this project. <<If LMCC only has CHPWH, display the "section does not apply" message>> <<require one row of data for each water heater identified on the NRCC-PRF>> |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value |
| <<Reference values from NRCC >> | <<If Performance, then reference values from NRCC-PRF-01, allowed values: DHW, Hydronic or Combined Hydronic; elseif Prescriptive, then NA >> | << Reference values from NRCC. Allowed values: Boiler, Indirect, Consumer Instantaneous, Commercial Instantaneous, Consumer Storage, Commercial Storage, Residential-Duty Commercial Storage, or Residential-Duty Commercial Instantaneous >> | <<Reference values from NRCC >> | << Reference values from NRCC >> | << Reference values from NRCC, allowed values: Natural Gas, Propane, Electric Resistance, or Heat Pump >> | <<if B06= Heat Pump, then result = NA; If B06 = Natural Gas or Propane, then value = Btu/Hr; Else if B06= Electric Resistance, then value = kW >> | << if B03 = Heat Pump, then result = NA; If performance, reference value from NRCC-PRF; Else if prescriptive, then value = NA >> | <<If Performance, reference values from NRCC-PRF-01, allowed values: *Energy Factor, *AFUE *Thermal Efficiency *Uniform Energy Factor; else value = NA >> | <<If Performance, reference value from NRCC-PRF-01; Else value = NA>> | <<If Performance, reference Value from NRCC-PRF-01; Else = NA. >> | <<If Performance, reference Value from NRCC-PRF-01; Else = NA >> |

| B2. Design HERS Verified CHPWH System Information This table reports the water heating systems specified on the registered NRCC compliance document for this project. <<If NRCC has CHPWH, then require table, else display the "section does not apply" message>> <<require one row of data for each water heater identified on the NRCC>> |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Modeled Equipment Make and Model | Number of Water Heaters/ Compressors | Primary Tank Location | Primary Tank Volume | Primary Tank Total Insulation | Loop Tank Location | Loop Tank Volume | Loop Tank Total Insulation | Loop Pipe Insulation Thickness | Loop Tank Type | Simulated Equipment Make and Model |
| <<Reference values from NRCC >> | <<Reference values from NRCC-PRF-01; else if prescriptive, report default value = Sanden>> | <<Reference values from NRCC>> | <<Reference value from NRCC>> | << Reference value from NRCC>> | << Reference value from NRCC>> | << Reference value from NRCC>> | << Reference value from NRCC>> | << Reference value from NRCC>> | << Reference value from NRCC>> | << Reference value from NRCC>> | <<if performance, hide column from user, needed for equivalency lookup; Reference value from XML; Elseif prescriptive, do not require field>> |

| C. Installed HERS Verified Central Water Heating Systems Information This table reports the water heating system features that were specified on the registered NRCC compliance document for this project. <<require one row of data for each water heater identified on the NRCC-PRF>> |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value |
| << Reference value from B01 >> | << Reference value from B02>> | << Reference value from B03 >> | << Reference value from B04>> | << Reference value from B05, NA is allowed only if B03 = Consumer Instantaneous, Commercial Instantaneous, or Residential-Duty Commercial Instantaneous >> | << Reference value from B06 >> | << Reference value from B07>> | <<User input value which must pass the following range tests: If C06 = Heat Pump, then C08 = NA; If C06 = Natural Gas or Propane, then If C03 = Commercial Storage, then value must be > 75,000 Btu/hr; If C03 = Consumer Storage, then value must be ≤ 75,000 Btu/hr; If C03 = Commercial Instant, then value must be > 200,000 Btu/hr; If C03 = Consumer Instant, then value must be ≤ 200,000 Btu/hr; Else if C03 = Residential-Duty Commercial Storage, then value must be ≤ 105,000 Btu/hr; Else if C06 = Electric Resistance, then If C03 = Commercial Storage or Commercial Instant, then value must be > 12 kW; If C03 = r Consumer Storage or Consumer Instant, then value must be ≤ 12 kW; Else if C03 = Residential-Duty Commercial Instantaneous, then value must be ≤ 58.6 kW; End If If the value passes range test, it is stored in WaterHeaterElectricFiredRatedInput, if C06 = Electric Resistance. Otherwise the value is stored in WaterHeaterGasFiredRatedInput; Elseif C03 = Boiler or Indirect, no limit on input value >> | << Reference value from B09; If prescriptive, then user select from: AFUE, Thermal Efficiency, Uniform Energy Factor >> | << User Input must ≥ B10, Value may only be NA if B10 = NA>> | << User Input must ≤ B11, Value may only be NA if B11 = NA >> | << User Input must ≥ B12, Value may only be NA if B12 = NA>> |

| C2. Installed HERS Verified CHPWH System Information This table reports the water heating systems specified on the registered NRCC compliance document for this project. <<If NRCC has CHPWH, then require table, else display the "section does not apply" message>> <<require one row of data for each water heater identified on the NRCC>> |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 |
| Water Heating System ID or Name | Modeled Equipment Make and Model | Number of Water Heaters/ Compressors | Primary Tank Location | Primary Tank Volume | Primary Tank Insulation | Loop Tank Location | Loop Tank Volume | Loop Tank Insulation | Loop Pipe Insulation Thickness | Loop Tank Type |
| <<reference values from B2-01>> | << If performance, user input is equal to B2-02 as default, and allow user to override with an equivalent system based on the simulated equipment in B2-12; else if prescriptive, value = Sanden>> | << User Input must equal reference values from B2-03 reference values from NRCC>> | << Reference values from B2-04>> | <<User input, must be ≥ value from B2-05>> | << User input, must be ≥ value from B2-06>> | << Reference values from B2-07>> | <<User input, must be ≥ value from B2-08>> | << User input, must be ≥ value from B2-09>> | << User input, must be ≥ value from B2-10>> | <<Reference value from B2-11>> |

| NRCC NRCC NRCC |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| NRCC | NRCC | NRCC | NRCC | NRCC | NRCC | NRCC | NRCC | NRCC | NRCC | NRCC |  |

| NRCC NRCC NRCC |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | NRCC |  |  |  |  |  |  |  |  |

| D. Design HER Verified Central Water Heating Distribution Systems Information This table reports the water heating distribution types specified on the registered NRCC compliance document for this project. <<require one row of data for each water heating system identified on the NRCC-PRF>>>> |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |
| <<reference values from NRCC (see rule in header)>> | <<Reference value from NRCC-PRF-01. Allowed values are: * Multi-family: Recirculation *Multifamily: Non-recirculation >> | <<Reference value from NRCC-PRF-01. Allowed values are *Standard Distribution System *HER-Verified Pipe Insulation>> |

| E. Installed HERS Verified Central Water Heating Distribution Systems Information This table reports the water heating distribution types specified on the registered NRCC compliance document for this project. <<require one row of data for each water heating system identified on the NRCC-PRF>> |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |
| <<reference values from NRCCD01>> | << Reference value from D02>> | << Reference value from D03>> |

| F. Installed HERS Verified Water Heater Manufacturer Information << require one row of data for each water heater identified in Section C, elseif no Section C, then display the "section does not apply" message.>> |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Manufacturer | Model Number |
| <<Reference value from C01>> | <<User input>> | <<User input>> |

| G. Mandatory Requirements for All Central Domestic Hot Water Systems |  |
| --- | --- |
| 01 | On systems that have a total capacity greater than 167,000 Btu/hr, outlets that require higher than service water temperatures as listed in the ASHRAE Handbook have separate remote heaters, heat exchangers, or boosters to supply the outlet with the higher temperature. (Section 110.3 (c)1) |
| 02 | Systems with circulating pumps or with electrical heat trace systems shall be capable of automatically turning off the system. (Section 110.3(c)2). |
| 03 | Unfired storage tanks are insulated with an external R-3.5 or combination of R-16 internal and external Insulation. (Section 110.3(c)4). |
| 04 | Recirculation loops shall meet the following requirements: - The recirculation pump is mounted on a vertical section of the return line, OR an automatic air release valve is installed on a riser at least 12 inches in length, on the inlet side of the recirculation pump, no more than 4 feet from the pump. (Section 110.3(c)4A). - A check valve is located between the recirculation pump and the water heater. (Section 110.3(c)4B). - A hose bib is installed between the pump and the water heating equipment with an isolation valve between the hose bib and the water heating equipment. (Section 110.3(c)4C). - Isolation valves shall be installed on both sides of the pump, of which the valve required in 110.3(c)4C can be one. (Section 110.3(c)4D). - The cold water piping and the recirculation loop piping shall not be connected to the hot water storage tank drain port. (Section 110.3(c)4E). - A check valve shall be installed on the cold water supply line between the hot water system and the next closest tee on the cold water supply line. (Section 110.3(c)4F). |
| 05 | Instantaneous water heaters with an input greater than 6.8 kBtu/hr. (2kW) shall have isolation valves on both the cold water supply and the hot water line. (110.3 (c)6). |
| 06 | All domestic hot water piping shall be insulated as specified in Section 609.11 of the California Plumbing Code. - Insulation buried below grade must be installed in a waterproof and non-crushable casing or sleeve. - Piping that penetrates framing members shall not be required to have pipe insulation for the distance of the framing penetration. Piping that penetrates metal framing shall use grommets, plugs, wrapping or other insulating material to assure that no contact is made with the metal framing. Insulation shall butt securely against all framing members. - Piping installed in interior or exterior walls that is surrounded on all sides by at least 1 inch (2.5 cm) of insulation. - Piping installed in crawlspace with a minimum of 1 inches (2.5 cm) of crawlspace insulation above and below. - Piping installed in attics with a minimum of 4 inches (10 cm) of attic insulation on top. Pipe insulation shall fit tightly and all elbows and tees shall be fully insulated. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |

| H. HERS Verified Multiple Recirculation Loops for DHW Systems Serving Multiple Dwelling Units Requirements All distribution systems listed on this compliance document shall comply with these requirements. |  |
| --- | --- |
| 01 | All buildings with 8 or more dwelling units have a minimum of 2 recirculation loops. |
| 02 | Each loop roughly serves the same number of dwellings. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Installation documentation is accurate and complete. |  |  |  |
| Documentation Author Name: |  | Documentation Author Signature: |  |
| Documentation Author Company Name: |  | Date Signed: |  |
| Address: |  | CEA/HERS Certification Identification (if applicable): |  |
| City/State/Zip: |  | Phone: |  |
| Responsible Person's Declaration statement |  |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: ### The information provided on this Certificate of Installation is true and correct. ### I am either: a) a responsible person eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction, or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Installation and attest to the declarations in this statement, or b) I am an authorized representative of the responsible person and attest to the declarations in this statement on the responsible person’s behalf. - The constructed or installed features, materials, components or manufactured devices (the installation) identified on this Certificate of Installation conforms to all applicable codes and regulations and the installation conforms to the requirements given on the Certificate of Compliance, plans, and specifications approved by the enforcement agency. - I understand that a HERS rater will check the installation to verify compliance and if such checking determines the installation fails to comply, I am required to offer any necessary corrective action at no charge to the building owner. - I will ensure that a registered copy of this Certificate of Installation shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Installation is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| Responsible Builder/Installer Name: | Responsible Builder/Installer Signature: |  |  |
| Company Name: (Installing Subcontractor or General Contractor or Builder/Owner) | Position With Company (Title): |  |  |
| Address: | CSLB License: |  |  |
| City/State/Zip: | Phone: |  | Date Signed: |
| Third Party Quality Control Program (TPQCP) Status: | Name of TPQCP (if applicable): |  |  |