## Change log
Date | Table | Description Of Change | Color | Addressed in XSD
2024-04-17 | Signature Block | Add "Responsible Person Scope" Field | Yellow with red text | Handled globally via 2025 ELC init commit
2024-04-17 | Table I | Add footnote 2 | Yellow with red text | Addressed
2024-04-17 | Table I | Replace "splitwire receptacle" with new enumeration | Yellow with red text | Addressed
2024-04-17 | Table I | Remove "durable" from "permanent durable…" checkbox | Yellow with red text | Addressed
2024-04-17 | Table J | Remove text from J.08 | Yellow with red text | Addressed
2024-04-17 | Table J | Add J.09-J.17 | Yellow with red text | Addressed
2024-04-17 | Table C | Modify C.05 logic | Yellow with red text | Addressed
2024-06-26 | Signature Block | Added AEA and replaced "HERS" with "ECC" | Yellow with red text | Handled globally via 2025 ELC init commit
2024-06-28 | Table A | Modify building occupancy type field | Yellow with red text | This was already in the 2022 form, no change needed to the xsd schema.

## Table Sequence
Label | Table Title | Trigger within:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Service Electrical Metering | Table B
Table G | Separation of Electrical Circuits for Energy Monitoring | Table B
Table H | Voltage Drop | Table B
Table I | Circuit Controls for 120-Volt Receptacles and Controlled Receptacles | Table B
Demand Response Controls- NOT USED
Table J | Electric Ready | Table A
Table K | Declaration of Required Certificates of Installation | ALWAYS
Table L | Declaration of Required Certificates of Acceptance | ALWAYS
- | Signature Page | ALWAYS

## NRCC Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Electrical Power Distribution
NRCC-ELC-E |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-ELC-E
This document is used to demonstrate compliance with mandatory requirements in §130.5 for electrical systems in newly constructed nonresidential, and hotel/motel occupancies and §160.6 and §160.9 for electrical systems in newly constructed multifamily occupancies. Additions and alterations to electrical service systems in nonresidential & hotel/motel occupancies will also use this document to demonstrate compliance per §141.0(a) or §141.0(b)2P for alterations. For multifamily addition or alterations compliance will be documented per §180.1(a) or §180.2(b)4Bvii.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
This is a heading. The project name, address and date prepared should be a user input on the first page, but that should populate the heading on all other pages.
STATE OF CALIFORNIA
Electrical Power Distribution
NRCC-ELC-E |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-ELC-E
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
First & Last Page Heading
Heading all other pages
Note on C8: 2/17/23 This cell grays out on all pages other than Page 1 and the last page.
Note on C17: 2022: Remove this field on all but first & last page header

## LMCC Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Electrical Power Distribution
LMCC-ELC-01-E |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | LMCC-ELC-01-E
This document is used to demonstrate compliance with mandatory requirements in §130.5 for electrical systems in newly constructed nonresidential and hotel/motel occupancies in low-rise multifamily mixed-use buildings and §160.6 and §160.9 for electrical systems in newly constructed low-rise multifamily occupancies. Additions and alterations to electrical service systems in nonresidential & hotel/motel occupancies in low-rise multifamily mixed-use buildings will also use this document to demonstrate compliance per §141.0(a) or §141.0(b)2P for alterations. For low-rise multifamily addition or alterations compliance will be documented per §180.1(a) or §180.2(b)4Bvii.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Electrical Power Distribution
LMCC-ELC-01-E |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | LMCC-ELC-01-E
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
First & Last Page Heading
Heading all other pages
Note on C8: 2/17/23 This cell grays out on all pages other than Page 1 and the last page.
Note on C17: 2022: Remove this field on all but first & last page header

## NRCC Footers
| User input | auto calculated |  | From another Table |  | From look up table
Footer for every page:
Registration Number: |  |  | Registration Date/Time: |  | Documentation Software
|  |  | Report Version: |  | Compliance ID:
|  |  | Schema Version: |  | Report Generated:
CA Building Energy Efficiency Standards - 2025 Nonresidential Compliance

## LMCC Footer
| User input | auto calculated |  | From another Table |  | From look up table
Footer for every page:
Registration Number: |  |  | Registration Date/Time: |  | Documentation Software
|  |  | Report Version: |  | Compliance ID:
|  |  | Schema Version: |  | Report Generated:
CA Building Energy Efficiency Standards - 2025 Low-rise Multifamily Compliance

## A. General Info
| User input | auto calculated | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  | 02 | Climate Zone | Dropdown
|  |  |  | 03 | Occupancy Types Within Project:
Climate Zone Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on A6: 6/282/4 Applicable occupancy types show up as bullet point list.

## B. Project Scope
| User input |  | auto calculated |  | From another Table | From look up table
B. PROJECT SCOPE
This table includes electrical service systems that are within the scope of the permit application.
01 | 02 | 03 | 04 | 05 | 06 | 07
Electrical Service Designation/ Description | Scope of Work1 | Rating2 (kVA) | Utility Provided Metering System Exception to §130.5(a)/§160.6(a)3 | System subject to CA Elec Code Article 517 Exception to §130.5(a)&(b) | Demand Response Controls | Provides power to dwelling units/common living areas only in multifamily occupancy
Where required, demand response controls must be specified which are capable of receiving and automatically responding to at least one standards based messaging protocol which enables demand response after receiving a demand response signal. Sections §120.2/§160.3, §130.1/§160.5 and §130.3/§160.5 and mechanical, indoor lighting, and sign lighting Certificate of Compliance documents will indicate when demand response controls are required.
| See dropdown below |  | o | o |  | o
1FOOTNOTES: Adding only new feeders and branch circuits triggers Voltage Drop 130.5(c)/160.6(c), no other requirements from 130.5/160.6 are required.
2 If common use areas in a multifamily occupancy are submetered, rating is for submeter size serving common use areas.
3 Applicable if the utility company is providing a metering system that indicates instantaneous kW demand and kWh for a utility-defined period.
Scope of Work Dropdown
| New electrical service equipment & meter | << triggers Table F. unless column 04 OR column 05 OR column 07 are checked, also triggers Table G unless column 05 is checked, triggers Table H & Table I.
| Complete replacement service equipment & meter | << triggers Table F. unless column 04 OR column 05 OR column 07 are checked, also triggers Table G unless column 05 is checked, triggers Table H & Table I.
| New or replacement service meter only | << triggers Table F. unless column 04 OR column 05 OR column 07 are checked
| Add/Alt to feeders and branch circuits only | << triggers Table H.
| Complete replacement service equipment, no meter change | << triggers Table G. unless column 05 is checked, triggers Table H. and Table I. Does NOT trigger Table F.
Note on C9: Usability Update: Grey out if Table F is not triggered AND Table G is not triggered.
Note on I9: 6.22.21: If == true, do not trigger/ include this service in Tables F AND Table G.
Note on A11: 6.22.21 Added new footnote 2 to col 03 heading, made old footnote 2 become footnote 3 in column 04 heading.

## C. Compliance
| User input |  |  | auto calculated |  |  |  |  | From another Table | From look up table
C. COMPLIANCE RESULTS
Results in this table are automatically calculated from data input and calculations in Tables F through J. Note: If any cell on this table says "COMPLIES with Exceptional Conditions" refer to Table D. Exceptional Conditions for guidance or see the applicable Table referenced below.
01 | AND | 02 | AND | 03 | AND | 04 | AND | 05 | 06
Service Electrical Metering §130.5(a)/ §160.6(a) |  | Separation for Monitoring §130.5(b)/ §160.6(b) |  | Voltage Drop §130.5(c)/ §160.6(c) |  | Controlled Receptacles §130.5(d)/ §160.6(d) |  | Electric Ready §160.9 | Compliance Results
(See Table F) |  | (See Table G) |  | (See Table H) |  | (See Table I) |  | (See Table J)
Yes/No | AND | Yes/No | AND | Yes/No | AND | Yes/No | AND | Yes/No | COMPLIES, DOES NOT COMPLY, Or COMPLIES with Exceptional Conditions
Note on A9: 2019 Update: Says "Yes" if Table F is triggered and something is entered in Table F column 04 for all rows in Table F. Otherwise says "No". Grey out and blank if Table F isn't triggered.
Note on C9: Sally Blair: Says "Yes" if Table G is triggered and something is entered in Table G column 04 and if ohter row is selected in g.03 and something is entered OR if Table G is triggered and all rows say "Not required" in column 02 ... Says "No" if "other" is selected in Table G column 03, but no note has been provided OR if Table G is triggered and nothing is entered in column 04 Grey out and blank if Table G not triggered.
Note on E9: Sally Blair: Says "Yes" if Table H column 02/03 are completed Says "No" if Table H is triggered, but the row isn't completed.
Note on G9: 9.7.21: Says "Yes" if Table I is triggered AND columns 02-06 are completed otherwise says "No"
Note on I9: 4.17.2024: Says "Yes" if Table J is triggered AND at least one selection is made in row 01 AND rows 02-17 are checked if triggered, otherwise says "No"
Note on J9: Novemeber 2019 Updates: Says "COMPLIES" if no other cells in row 9 say "No" Says "COMPLIES with Exceptional Conditions" if: - no other cells in row 9 say "No" AND and an exceptional condition note has been triggered in Table D OR - B.02 = "New or Replacement Service Meter Only" and either B.04 or B.05 has been checked. Otherwise says "DOES NOT COMPLY"

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Comment:
Note about not including a note in Table G. if required (copy from LTI).
Note about not including a note in Table I. if required (copy from LTI).
Note about changing the NRCI from "yes" to "no" in Table K.
Table H. indicates voltage drop calculations will be provided by the contractor.
"Table B indiates the project is exempt from §130.5(a) Service Electrical Metering requirements because the utility company has provided the project a metering system that indicates instantaneous kW demand and kWh for a utility-definied period."
Table B indicates the project is exempt from §130.5(a) Service Electrical Metering requirements and §130.5(b) Seperation of Electrical Circuits requirements because the system is subject to CA Elec Code Article 517"
Note on B12: 12/19/22: Triggered if 'Contractor Responsible' is selected in Table H.03.
Note on B13: Novemeber 2019 Updates: This note should trigger when B.04 is checked.
Note on B14: Ben Lalor: This note should trigger when B.05 is checked

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## F. Service Electrical Metering
| User input |  | auto calculated |  |  |  | From another Table |  | From look up table
F. SERVICE ELECTRICAL METERING
This table includes new or replacement electrical service systems OR equipment to demonstrate compliance with §130.5(a)/§160.6(a). For multifamily occupancies, submetered systems that provide power to common use areas must meet the following metering requirements. Submetered systems providing power to dwelling units do not.
01 | 02 | 03 |  |  |  | 04 | 05
Electrical Service Designation/ Description | Rating1 (kVA) | Required Metering Capabilities per Table 130.5-A |  |  |  | Location of Requirements in Construction Documents | Field Inspector
|  | Instantaneous Demand (kW) | Historical Peak Demand (kW) | Tracking kWh for user-defined period | kWh per rate period |  | Pass | Fail
carries over from Table B. |  | o | o | o | o |  | o | o
carries over from Table B if more than one service entered. |  | o | o | o | o |  | o | o
1FOOTNOTES: If common use areas in a multifamily occupancy are submetered, rating is for submeter size serving common use areas.
a
a
a
a
Note on B8: 2019 Update: These two fields come in from table B for any ES Designations that meet ANY of the following 3 conditions: - Selects "New electrical service equipment & meter" in Table B column 02 AND does not have Table B column 04 checked AND does not have Table B column 05 checked. OR - Selects "Complete replacement service equipment & meter" in Table B column 02 AND does not have Table B column 04 checked AND does not have Table B column 05 checked. OR - Selects "New or replacement service meter only" in Table B column 02 AND does not have Table B column 04 checked AND does not have Table B column 05 checked.
Note on D8: Sally Blair: This checks if column 02 is >250 and cannot be edited by user.
Note on E8: Sally Blair: This and the instantaneous are always checked without the user being able to change it.
Note on F8: Sally Blair: This checks if column 02 is > 1000 and cannot be edited by user.

## G. Sep of Circuits
| User input |  |  | auto calculated |  | From another Table | From look up table
G. SEPARATION OF ELECTRICAL CIRCUITS FOR ENERGY MONITORING
This table includes entirely new or complete replacement electrical power distribution systems to demonstrate compliance with §130.5(b)/§160.6(b). Any load types that are not included in the service do not need to be shown. For multifamily occupancies, submetered systems that provide power to dwelling units do not need to meet these separation requirements and therefore load types on those submetered systems also do not need to be shown.
Electrical Service Designation/ Description: | Here we'll bring in the Electrical Service Designation/ Description from Table B column 01.
01 | 02 | 03 | 04 | 05
Load Type per Table 130.5-B1 | Minimum Required Separation of Load per Table 130.5-B | Compliance Method2 | Location of Requirements in Construction Documents | Field Inspector
|  |  |  | Pass | Fail
See dropdown below |  | See dropdown below |  | o | o
*NOTES If "Other*" is selected under Compliance Method above, please indicate how compliance has been achieved in the space provided below.
If user selects "other" in column 03, the "Load Type" (uneditable) should show up in Notes section. If they unselect "other", the load type should dissapear.
1 FOOTNOTES: For each separate load type, up to 10% of the connected load may be of any type.
² Method 1: Switchboards/ motor control centers/ panelboard loads disaggregated for each load type Method 2: Switchboards/ motor control centers/ panelboard supply other distribution equipment with loads disaggregated for each load type Method 3: Branch circuits serve load types individually & provisions for adding future branch curcuit monitoring Method 4: Complete metering system measures and reports loads by type See Chapter 8 of the Nonresidential Compliance Manual for more detail on Compliance Methods.
Load Type Dropdown |  | Compliance Method Dropdown
Lighting including exit, egress and exterior |  | Method 1
HVAC systems and components |  | Method 2
Domestic and service water systems |  | Method 3
Plug Loads and appliances < 25kVA |  | Method 4
Other non-HVAC loads or appliances > 25kVA |  | Other*
Elevators, escalators, moving walkways
Indust./ commercial load centers > 25kVA
Renewable power sources (net or total)
Loads associated with renewable power source
Charging stations for electric vehicles
Only MF dwelling units on this service
Note on B5: Sally Blair: Each Electrical service designated in Table B column 02 as "New or complete replacement EPD system" will need to have it's own section (rows 5-9) in this table.
Note on B9: Sally Blair: Depending on the Rated kVA for the Electrical Service designation in Table B column 03, and the load type selected in column 01, the relevant requirement from Table 130.5-B (example "All loads in aggregate") would populate here.
Note on C20: 2019 Update: Added new method for 2019.
Note on C21: Benjamin Park: triggers a note in Table G
Note on A27: 8.16.21: Greys out columns 02-04

## H. Voltage Drop
| User input |  | auto calculated |  |  |  | From another Table | From Lookup Table
H. VOLTAGE DROP
This table includes entirely new or complete replacement electrical power distribution systems, or alterations that add, modify or replace both feeders and branch circuits to demonstrate compliance with §130.5(c)/§160.6(c). For alterations, only the altered circuits must demonstrate compliance per §141.0(b)2Piii/§180.2(b) 4Bviic.
01 | 02 |  | 03 | 04 | 05
Electrical Service Designation/ Description | Combined Voltage Drop on Installed Feeder/Branch Circuit Conductors Compliance Method |  | Location of Voltage Drop Calculations1 | Sheet Number for Voltage Drop Calculations in Construction Documents | Field Inspector
[5 empty] | Pass | Fail
| ¨ Voltage drop < 5% | ¨ Permitted by CA Elec Code (Exception to §130.5(c))* | See dropdown below |  | o | o
*NOTES If "Permitted by CA Elec Code*" is selected under Compliance Method above, please indicate where the exception applies in the space provided below.
If user selects "Permitted by CA Elec Code" in column 02, the "Electrical Service Designation/ Description" (uneditable) should show up in Notes section. If they unselect "Permitted by CA Elec Code", the "Electrical Service Designation/ Description" should dissapear.
1 FOOTNOTES: Voltage drop calculations may be attached to the permit application outside the construction documents if allowed by the Authority Having Jurisdiction. Select "attached" if applicable. If calculations will be the responsibility of the installing contractor, select "Contractor Responsible".
Location of Calcs Dropdown
In construction documents
Attached
Contractor Responsible
Note on A9: Sally Blair: This field comes in from table B for any ES Designations that choose "New or Complete Replacement Systems" OR "Alterations of Feeders and Branch Circuits"
Note on E9: Sally Blair: Open for user input if "In construction documents" is selected in column 03
Note on D17: Sally Blair: Triggers a note in Table D (see Table D row 14)

## I. Controlled Receptacles
| User input |  |  | auto calculated |  | From another Table |  | From look up table
I. CIRCUIT CONTROLS FOR 120-VOLT RECEPTACLES AND CONTROLLED RECEPTACLES
This table includes entirely new or complete replacement electrical power distribution systems to demonstrate compliance with §130.5(d)/§160.6(d). Both controlled and uncontrolled receptacles must be provided in office areas, lobbies, conference rooms, kitchen areas in office spaces, copy rooms and hotel/motel guest rooms.
01 | 02 | 03 | 04 | 05 | 06 | 07
Room Name or Description | Location/ Type of Controlled Receptacles1,2 | Shut-Off Controls | Demand Responsive Controls | Permanent Durable Marking Will be Used | Location of Requirements in Construction Documents | Field Inspector
[6 empty] | Pass | Fail
| See dropdown below | See dropdown below | See dropdown below | ¨ |  | o | o
*NOTES: If "Other*" is selected under Shut-Off Controls above, please indicate how compliance has been achieved in the space provided below.
If user selects "other" in column 03, the "Room Name" (uneditable) should show up in Notes section. If they unselect "other", the room name should dissapear.
1 FOOTNOTES: Receptacles dedicated to refrigerators and water dispensers in kitchens, located a minimum of 6ft above the floor specifically for clocks, network copiers, fax machines, A/V and data equipment other than personal computers in copy rooms, circuits rated more than 20 Amps, or connected to a UPS that are intended to be in continuous use and are marked to differentiate them from other receptacles or circuits are excepted from the requirements.
2 Plug-in strips and other plug-in devices shall not be used to comply with the requirements of section 130.5(d)
| Location/ Type Dropdown | Control Dropdown | Demand Response Dropdown
| Within 6ft of uncontrolled receptacles | Auto Time-Switch with applicable overrides | Included w capabilities per §110.12(e)
| Splitwire receptacle Multiple receptacle outlet with > 1 controlled and uncontrolled receptacle | Occupancy Sensor | NA: Building does not require demand responsive lighting controls per §110.12(c)
| Within 6ft of uncontrolled AND Splitwire receptacle multiple receptacle outlet | Occ-sensing Hardwired Power Strip | NA: Health/ life safety regulation does not permit the receptacles to be automatically controlled
| 50% are controlled receptacles (hotel/motel room only) | Captive Card Key (hotel only)
| NA: Healthcare Facility | Other*
| NA: Data Equipment Receptacle | NA: Data Equipment Receptacle
| NA: Circuit > 20 Amperes | NA: Circuit > 20 Amperes
| NA: Uninteruptible Power Supply Receptacle intended for 24/7/365 | NA: Uninteruptible Power Supply Receptacle intended for 24/7/365 | 309
| NA: Clock Receptacle >= 6FT Above Floor | NA: Clock Receptacle >= 6FT Above Floor
| NA: Refrigerator/Water Dispenser Receptacle | NA: Refrigerator/Water Dispenser Receptacle
NA: Healthcare Facility
Note on A3: Rebecca Rice: If Healthcare Facility is selected in Table I, then this table does not open up. Instead show This Section Does Not Apply.
Note on B8: 6.22.21: This field needs to become select all that apply.
Note on C8: 6.22.21: This field needs ot become select all that apply.
Note on C18: Benjamin Park: triggers a * note in Table I

## J. Demand Resp_NOT USED (hidden)
|  | User input |  | auto calculated | From another Table | From look up table
J. DEMAND RESPONSE CONTROLS
Table Instructions: Please complete this table for nonresidential occupancies indicated in Table B as requiring Demand Response controls.
01 |  |  | 02
o | HVAC | Demand response controls have been specified which are capable of receiving and automatically responding to at least one standards based messaging protocol which enables demand response after receiving a demand response signal. | Location of Requirements in Construction Documents
o | Indoor Lighting | Demand response controls have been specified which are capable of receiving and automatically responding to at least one standards based messaging protocol which enables demand response after receiving a demand response signal. | Location of Requirements in Construction Documents
o | Sign Lighting | Demand response controls have been specified which are capable of receiving and automatically responding to at least one standards based messaging protocol which enables demand response after receiving a demand response signal. | Location of Requirements in Construction Documents
Table Tip:
Rows trigger based on what is selected in Table B column 05

## J. Electric Ready
| User input |  |  | auto calculated |  | From another Table |  | From look up table
J. ELECTRIC READY BUILDINGS
This table includes electrical system requirements that must be met when using gas or propane heating, cooking or clothes drying in multifamily occupancies to demonstrate compliance with §160.9.
01 | Systems serving multifamily occupancy that use gas or propane include: |  | ¨ Furnaces serving individual dwelling units | ¨ Cooktops serving individual dwelling units | ¨ Clothes dryers serving individual dwelling units | ¨ Clothes dryers in common areas | ¨ Gas/propane water heater serving individual dwelling units | ¨ Gas/propane water heater serving multiple dwelling units | ¨ None of these
Gas/ Propane Furnaces Serving Individual Dwelling Units (Heat Pump Space Heater Ready)
| Yes | Requirement
02 | ¨ | A dedicated 240 volt branch circuit shall be installed within 3 feet from the furnace and accessible to the furnace with no obstructions. The branch circuit shall be rated at 30 amps minimum. The blank cover shall be identified as “240V ready”. All electrical components shall be installed in accordance with the California Electrical Code.
03 | ¨ | The main electrical service panel shall have a reserved space to allow for the installation of a double pole circuit breaker for a future heat pump space heater installation. The reserved space shall be permanently marked as “For Future 240V use”.
Gas/ Propane Cooktops Serving Individual Dwelling Units
| Yes | Requirement
04 | ¨ | A dedicated 240 volt branch circuit shall be installed within 3 feet from the cooktop and accessible to the cooktop with no obstructions. The branch circuit shall be rated at 50 amps minimum. The blank cover shall be identified as “240V ready”. All electrical components shall be installed in accordance with the California Electrical Code.
05 | ¨ | The main electrical service panel shall have a reserved space to allow for the installation of a double pole circuit breaker for a future electric cooktop installation. The reserved space shall be permanently marked as “For Future 240V use”.
Gas/ Propane Clothes Dryers Serving Individual Dwelling Units
| Yes | Requirement
06 | ¨ | A dedicated 240 volt branch circuit shall be installed within 3 feet from the clothes dryer and accessible to the clothes dryer with no obstructions. The branch circuit shall be rated at 30 amps minimum. The blank cover shall be identified as “240V ready”. All electrical components shall be installed in accordance with the California Electrical Code.
07 | ¨ | The main electrical service panel shall have a reserved space to allow for the installation of a double pole circuit breaker for a future electric clothes dryer installation. The reserved space shall be permanently marked as “For Future 240V use”.
Gas/ Propane Clothes Dryers In Common Areas
| Yes | Requirement
08 | ¨ | Conductors or raceway shall be installed with termination points at the main electrical panel, via subpanels panels if applicable, to a location no more than 3 feet from each gas outlet or a designated location of future electric replacement equipment. Both ends of the conductors or raceway shall be labelled “Future 240V Use.” The conductors or raceway and any intervening subpanels, panelboards, switchboards, and busbars shall be sized to meet the future electric power requirements, at the service voltage to the point at which the conductors serving the building connect to the utility distribution system, as specified below. The capacity requirements may be adjusted for demand factors in accordance with the California Electric Code. Gas flow rates shall be determined in accordance with the California Plumbing Code. Capacity shall be one of the following: - 24 amps at 208/240 volts per clothes dryer; - 2.6 kVA for each 10,000 Btu per hour of rated gas input or gas pipe capacity; or - The electrical power required to provide equivalent functionality of the gas-powered equipment as calculated by the responsible person.
Gas/Propane Water Heaters Serving Individual Dwelling Units
| Yes | Requirement
09 | ¨ | A dedicated 125 volt, 20 amp electrical receptacle that is connected to the electric panel with a 120/240 volt 3 conductor branch circuit rated to 30 amps minimum, within 3 feet from the water heater and accessible to the water heater with no obstructions. In addition, all the following: - Both ends of the unused conductor shall be labeled with the word “spare” and be electrically isolated; and - A reserved single pole circuit breaker space in the electrical panel adjacent to the circuit breaker for the branch circuit in A above and labeled with the words “Future 240V Use”
10 | ¨ | The construction drawings shall designate a space at least 39 inches by 39 inches and 96 inches tall for the future location of heat pump water heater
Gas/Propane Water Heaters Serving Multiple Dwelling Units
| Yes | Requirement
11 | ¨ | Physical space shall be reserved on the bus system of the main switchboard or on the bus system of a distribution board to serve the future heat pump water heater system including the heat pump and temperature maintenance tanks. In addition, the physical space reserved shall be capable of providing adequate power to the future heat pump water heater in accordance with the following: - Heat Pump. Meet one of the following: - The electrical power required to power a heat pump water heater system heat pump that meets the total building hot water demand as calculated and documented by the responsible person associated with the project. - The electrical power required that meets the requirements specified for the heat pump in Joint Appendix JA15.2.5. - Temperature Maintenance Tank. Meet one of the following: - The electrical power required to power a heat pump water heater system temperature maintenance tank that meets the total building hot water demand as calculated and documented by the responsible person associated with the project. - The electrical power required that meets the requirements specified for the temperature maintenance tank in Joint Appendix JA15.2.5.
Note on A5: 2022: selection triggers associated subtable below, otherwise subtable doesn't show.

## K. NRCI
| User input |  |  | auto calculated | From another Table | From look up table
K. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online.
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | NRCI-ELC-E - Must be submitted for all buildings. | o | o
Note on A4: 8.16.21: Need to include new URL for Cert of install forms.
Note on A7: Sally Blair: NRCI form defaults to "Yes" but user can change just like on LTI. Would trigger table D. comment too.

## K. LMCI
| User input |  |  | auto calculated | From another Table | From look up table
K. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online.
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | LMCI-ELC-E - Must be submitted for all buildings. | o | o
Note on A4: 8.16.21: Need to include new URL for Cert of install forms.
Note on A7: Sally Blair: LMCI form defaults to "Yes" but user can change just like on LTI. Would trigger table D. comment too.

## L. NRCA
| User input |  |  | auto calculated |  | From another Table | From look up table
L. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/programs-and-topics/programs/building-energy-efficiency-standards/2025-building-energy-efficiency#accordion-13813 [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and any with "-A" in the form name must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html
YES | NO | Form/Title | Systems To Be Field Verified | Field Inspector
|  |  |  | Pass | Fail
m | m | NRCA-LTI-04-A - Demand Response Controls |  | o | o
Note on B5: Sally Blair: Form will select based on user input in other Tables. User can edit, but if they do a note will show up in Table D. See Table D row 12 for note.
Note on D5: 9/11/20: This is a user entry column where users would list the systems that require each form.
Note on A7: 9/4/2024 If I.04 = "Included.." = Yes Else = No

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/AEA/ECC Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Person Name: | Responsible Personal Signature:
Responsible Person Scope
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
[d:OnlyUI] The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-CXR form. [d:OnlyUI]
Note on B16: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on E17: Corrected 3.29.19: Corrected to say CXR instead of LTI
?
Add Responsible Person
Remove Last