## Change Log
Date | Table | Description | Color
| A. General Info | Updated Religious Facility to Religious Worship | yellow with red text
| Footers | Updated dates in footers | yellow with red text
| F - Equipment Schedule subtable | Updated section reference in F.04 Header | yellow with red text
| F - Equipment Schedule subtable | Add dropdown field - Space Type | yellow with red text
| F - Equipment Schedule subtable | Revised dropdown options for Equipment Type dropdown | yellow with red text
| F - Equipment Schedule subtable | Deleted several columns | yellow with red text
| F - Equipment Schedule subtable | Revised logic for several fields | yellow with red text
| F - Equipment in Individual Dwelling Units | Added System Name field | yellow with red text
| F - Equipment in Individual Dwelling Units | Added "120 volt" row in 16 | yellow with red text
| F - Equipment in Individual Dwelling Units | Added section references | yellow with red text
| F - Equipment in Individual Dwelling Units | Removed footnote | yellow with red text
| F - Equipment in Individual Dwelling Units | Revised logic for several fields | yellow with red text
| F - Equipment All Occupancies | Added System Name field | yellow with red text
| F - Equipment All Occupancies | Add new rows 18 and 20 | yellow with red text
| F - Equipment All Occupancies | Add new rows (F22) for air-source heat pump water heater requirements | yellow with red text
| F - Equipment All Occupancies | Revised logic for several fields | yellow with red text
| F - Equipment for Central Systems… | Added System Name field | yellow with red text
| F - Equipment for Central Systems… | Added section references | yellow with red text
| F - Equipment for Central Systems… | Altered langauge in first row of F.23 | yellow with red text
| F - Equipment for Central Systems… | Altered langauge in third row of F.23 | yellow with red text
| F - Equipment for Central Systems… | New row added in F.23 for NEEA requirements | yellow with red text
| G - Recirculation Loops in Central Systems… | Added System Name field | yellow with red text
| G - Recirculation Loops in Central Systems… | Revised logic for several fields | yellow with red text
| G - Recirculation Loops in Central Systems… | Removed row 07 and renumbered subsequent rows | yellow with red text
| G - Recirculation Loops in Central Systems… | Updated language in G.08 (was G.09) | yellow with red text
| G - Recirculation Loops in Central Systems… | Added rows 09, 10, and 11 | yellow with red text
| G - Distribution of Individual System(s)… | Added System Name field | yellow with red text
| G - Distribution of Individual System(s)… | Added section references | yellow with red text
| G - Mandatory Pipe Insulation… | Added System Name field | yellow with red text
| G - Mandatory Pipe Insulation… | Updated table 120.3-A to 120.3-A1 and 120.3-A2 in G.16 (was G.14) | yellow with red text
| G - Mandatory Pipe Insulation… | Updated language in G.17 (was G.15) | yellow with red text
| G - Mandatory Pipe Insulation… | Added new table 120.3-A1 and 120.3-A2 screenshots for reference | yellow with red text
| H - Controls | Updated section 160.4(e) reference in Table H header and H.06 | yellow with red text
| H - Controls | Updated language in H.04 | yellow with red text
| H - Controls | Revised logic for several fields | yellow with red text
| I. Electric Ready | New table | yellow with red text
| J - Pool/Spa | New table | yellow with red text
| Signature block | Updated HERS to ECC | yellow with red text
| Signature block | Added responsible person scope row | yellow with red text
| Table Labels | Updated table headers K-M due to new addition of Table I and J. | yellow with red text

## New Table Sequence
Label | Table Title | Trigger within: | Note:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Domestic Hot Water Equipment | Table B.
Table G | Domestic Hot Water Distribution Systems | Table B.
Table H | Domestic Hot Water System Controls | Table B.
Table I | Declaration of Required Certificates of Installation | ALWAYS
Table J | Declaration of Required Certificates of Acceptance | ALWAYS
- | Documentation Author's Declaration Statement | ALWAYS

## Hyperlinks
Section | Applicable Tables
110.1 | header, F
110.3 | header, F, H
120.3 | header, G
140.5 | header, B, G
141.0 | header
141.0(a) | header, B
150.0 | header, G
150.1(c)8 | header, B, F, H
150.2 | header, F, H
141.0(b)2N | B
150.1(c)8Ai | F
§150.2(b)1H | F
150.2(b)1G | F
150.0(n)1 | F
150.0(a)1 | F
110.3(c)3/4 | F
110.3(c)5 | F
110.3(c)6 | D
110.3(c) | G
110.3(c)4A/B/C/D/E/F | G
150.1 | G
110.3(c)5 | G
150.1(c)8Bii | G, H
RA3.6.9 | G
RA4.4.6 | G
150.1(c)8Aii | G
150.1(c)8Aiv | G
150.1(c)14 | G
150.1(c)8Av | G
RA4.4.16 | G
150.1(c)8Aiii | G
Table 120.3-A | G
150.0(j)2A | G
150.0(j)3 | G
110.3(a) | H
110.3(c)1/2 | H
RA4.4.9 | H
110.12(a) | H
150.2(b)1Hiii

## NRCC Headers
| User input |  | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Domestic Water Heating System
NRCC-PLB-E |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-PLB-E
This document is used to demonstrate compliance for nonresidential occupancies with requirements in §110.1, §110.3, §120.3, and §140.5, and with requirements in §141.0 for additions and alterations, for domestic water heating scopes using the prescriptive path. For high-rise residential and hotel/motel occupancies, compliance is demonstrated with requirements in §110.1, §110.3, §160.4 and §170.2(d), and with requirements in §180.1 for additions and §180.2 for alterations.
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Domestic Water Heating System
NRCC-PLB-E |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-PLB-E
Project Name: |  |  |  |  | Report Page: | Page 2 of ??
Project Address: |  | Remove this field on all but first & last page header |  |  | Date Prepared:
Heading First & Last Page Only
Heading All Other Pages
Note on C9: 2/17/23 This cell grays out on all pages other than Page 1 and the last page.

## LMCC Headers
| User input |  | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Domestic Water Heating System
LMCC-PLB-01-E |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | LMCC-PLB-01-E
This document is used to demonstrate compliance with requirements in §110.1, §110.3, §120.3, and §140.5, and with requirements in §141.0 for additions and alterations, for domestic water heating systems serving nonresidential occupancies within low-rise mixed use buildings using the prescriptive path. For low-rise residential and hotel/motel occupancies, compliance is demonstrated with requirements in §110.1, §110.3, §160.4 and §170.2(d), and with requirements in 180.1 for additions and §180.2 for alterations.
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Domestic Water Heating System
LMCC-PLB-01-E |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | LMCC-PLB-01-E
Project Name: |  |  |  |  | Report Page: | Page 2 of ??
Project Address: |  | Remove this field on all but first & last page header |  |  | Date Prepared:
Heading First & Last Page Only
Heading All Other Pages
Note on C9: 2/17/23 This cell grays out on all pages other than Page 1 and the last page.

## NRCC Footers
| User input | auto calculated |  | From another Table |  | From look up table
Footer for every page:
Registration Number: |  |  | Registration Date/Time: |  | Registration Provider:
|  |  | Report Version: |  | Compliance ID:
|  |  | Schema Version: |  | Report Generated:
CA Building Energy Efficiency Standards - 20225 Nonresidential Compliance:
Footer All Pages

## LMCC Footers
| User input | auto calculated |  | From another Table |  | From look up table
Footer for every page:
Registration Number: |  |  | Registration Date/Time: |  | Registration Provider:
|  |  | Report Version: |  | Compliance ID:
|  |  | Schema Version: |  | Report Generated:
CA Building Energy Efficiency Standards - 20225 Low-Rise Multifamily Compliance:
Footer All Pages
Note on K9: 8.24.21: Update with new URL

## NRCC A. General Info
| User input | auto calculated | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  | 02 | Climate Zone | Dropdown
03 | Occupancy Types Within Project (select all that apply): |  |  | 04 | Conditioned Square Footage
• Applicable occupancies show up here
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on J5: 2/6/25 User input

## LMCC A. General Info
| User input | auto calculated | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  | 02 | Climate Zone | Dropdown
03 | Occupancy Types Within Project (select all that apply): |  |  | 04 | Conditioned Square Footage
• Applicable occupancies show up here
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on J5: 2/6/25 User input

## NRCC B. Project Scope
|  | User input | auto calculated | from another table |  |  | From look up table
B. PROJECT SCOPE
This table identifies any domestic water heating systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive paths outlined in §140.5/ §170.2(d), and §141.0(a)/ §180.1, or §141.0(b)2N/ §180.2 for additions or alterations. Solar water heating systems should be documented on the NRCC-SAB compliance document. Combined hydronic water heating systems should be documented on the NRCC-MCH compliance document.
01 |  |  | 02 | 03
My project consists of (check all that apply): |  |  | System Type1,2 | System Components
¨ | New System (DHW system being installed for the first time) |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls
¨ | System Alteration (equipment, distribution or controls) |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls
ALERT! Note: Gas or propane central water heating systems serving multiple dwelling units require a solar water heating system per §170.2(d)3. Solar water heating systems are documented on the NRCC-SAB compliance document. If solar water heating systems are used in conjunction with non-solar systems to meet the water heating needs of the building, document the non-solar systems on this compliance document. | [6 empty] | << triggers exception condition in Table D. See Table D item 1.
ALERT! Note: Combined domestic and hydronic water heating systems are documented on the NRCC-MCH compliance document. If combined hydronic water heating systems are used in conjunction with domestic only systems to meet the water heating needs of the building, only document the domestic only systems on this compliance document. | [6 empty] | << triggers exception condition in Table D. See Table D item 2
1 FOOTNOTE: Point of use water heaters, or other non-central systems used to serve nonresidential spaces, are considered individual systems.
2 Dwelling units refers to hotel/ motel guest rooms and units in a multifamily residential occupancy.
3 DHW systems serving 2 or more dwelling units are considered "Central Systems" for multifamily and hotel/motel occupancies
System Type Dropdown
Central System (serving nonresidential spaces) Serving Nonresidential or MF/Hotel/Motel Common use area
Individual System (serving nonresidential spaces)1
Central System (serving 2+ dwelling units)2, 3
Individual Dwelling Unit System(s)2
Dwelling Unit Solar Thermal System
Combined Hydronic System
Pool/Spa
Note on G8: Sally Blair: Any selection of "Equipment" in column 03 opens Table F.
Note on H8: Sally Blair: Any selection of "Distribution" in column 03 opens Table G.
Note on I8: Sally Blair: Any selection of "Controls" in column 03 opens Table H.
Note on D15: Sally Blair: these triggers are secondary to column 03. For example, if distribution is NOT checked in column 03, the Table G is not triggered. If it is checked, this selection in column 02 would open the triggered section. Let me know if you need clarification.
Note on E15: 2/5/25 Triggers Table F, Table G Central System subtable, Table H, and table I
Note on E17: 2/6/25 Triggers Table F, Table G Central System subtable, Table H, and table I
Note on E18: 2/6/25 Triggers Table F, Table G Individual Dwelling Unit subtable,Table H, and table I
Note on E21: 2/6/25 Triggers Table J

## LMCC B. Project Scope
|  | User input | auto calculated | from another table |  |  | From look up table
B. PROJECT SCOPE
This table identifies any domestic water heating systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive paths outlined in §140.5/ §170.2(d), and §141.0(a)/ §180.1, or §141.0(b)2N/ §180.2 for additions or alterations. Solar water heating systems should be documented on the LMCC-SAB compliance document. Combined hydronic water heating systems should be documented on the LMCC-MCH compliance document.
01 |  |  | 02 | 03
My project consists of (check all that apply): |  |  | System Type1,2 | System Components
¨ | New System (DHW system being installed for the first time) |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls
¨ | System Alteration (equipment, distribution or controls) |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls
ALERT! Note: Gas or propane central water heating systems serving multiple dwelling units require a solar water heating system per §170.2(d)3. Solar water heating systems are documented on the NRCC-SAB compliance document. If solar water heating systems are used in conjunction with non-solar systems to meet the water heating needs of the building, document the non-solar systems on this compliance document. | [6 empty] | << triggers exception condition in Table D. See Table D item 1.
ALERT! Note: Combined domestic and hydronic water heating systems are documented on the NRCC-MCH compliance document. If combined hydronic water heating systems are used in conjunction with domestic only systems to meet the water heating needs of the building, only document the domestic only systems on this compliance document. | [6 empty] | << triggers exception condition in Table D. See Table D item 2
1 FOOTNOTE: Point of use water heaters, or other non-central systems used to serve nonresidential spaces, are considered individual systems.
2 Dwelling units refers to hotel/ motel guest rooms and units in a multifamily residential occupancy.
3 DHW systems serving 2 or more dwelling units are considered "Central Systems" for multifamily occupancies and hotel/motel.
System Type Dropdown
Central System (serving nonresidential spaces) Serving Nonresidential or MF/Hotel/Motel Common use area
Individual System (serving nonresidential spaces)1
Central System (serving 2+ dwelling units)2, 3
Individual Dwelling Unit System(s)2
Dwelling Unit Solar Thermal System
Combined Hydronic System
Note on G8: Sally Blair: Any selection of "Equipment" in column 03 opens Table F.
Note on H8: Sally Blair: Any selection of "Distribution" in column 03 opens Table G.
Note on I8: Sally Blair: Any selection of "Controls" in column 03 opens Table H.
Note on E15: 2/5/25 Triggers Table F and Table G Central System subtable
Note on E17: 2/6/25 Triggers Table F and Table G Central System subtable
Note on E18: 2/6/25 Triggers Table F and Table G Individual Dwelling Unit subtable

## C. Compliance
| User input |  |  |  | From look up table
C. COMPLIANCE RESULTS
Table Instructions: Table C will indicate if the project data input into the compliance document is compliant with water heating requirements. This table is not editable by the user. If this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D., or the table indicated as not compliant for guidance.
01 |  | 02 | 03 | 04 | 04
Domestic Hot Water Equipment |  | Distribution Systems | Controls | Pool/Spa | Compliance Results
Table F |  | Table G | Table H | Table J
YES |  |  |  |  | COMPLIES, COMPLIES with Exceptional Conditions or DOES NOT COMPLY
Note on A9: 9.1.21 Says "YES" if all of the below conditions are met: 1. If "Equipment Schedule: Water Heater Efficiency and Standby Loss" is triggered for user input, EITHER: - column 05 is not checked AND - F11 >= F12 if not gray AND - F14 <= F15 if not gray OR - column 05 is checked AND - col 06 >= 90% AND - F11 >= F12 if not gray AND - F14 < F15 if not gray 2. If "Equipment in Individual Dwelling Units" is triggered for user input, F17 is "Y" or "NA" 3. F18, F19 anf F20 and F21 are all either "Y" or "NA" 4. Otherwise says "NO" Grey out if Table F not triggered
Note on C9: Katie Gustafson: Says "YES" if no "No" have been checked AND if all triggered rows for Mandatory Pipe Insulation have been checked. Otherwise, says "NO" Grey out if Table G not triggered.
Note on E9: Sally Blair: Says "YES" if no "No" have been checked. Otherwise, says "NO" Grey out if Table H not triggered.
Note on F9: Alexis Markstrum: Says "Yes" if columns 01-10 are completed AND 11-16 completed if triggered. Otherwise says "No"
Note on G9: Sally Blair: Says "COMPLIES" if all columns which are not greyed out say "YES". Says "COMPLIES with Exceptional Conditions" if all columns which are not greyed out say "YES" AND an exceptional condition is triggered in Table D. Otherwise, says "DOES NOT COMPLY"

## NRCC D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
1. | Table B indicates a solar water heating system will be used to comply with Title 24, Part 6. These systems shall be documented on the NRCC-SAB-E compliance document.
2. | Table B indicates a combined hydronic system will be used to comply with Title 24, Part 6. These systems shall be documented on the NRCC-MCH-E compliance document.
3 | Tables A and B indicate the project is a new State building. This requires 60% of energy for service water heating from site solar energy or recovered energy per §110.3(c)6.
4. | Table F indicates an electric water heater is being used to replace an existing electric resistance water heater.
Table J indicates project has inadequate Solar Access Roof Area (SARA) for solar water heating system. Please confirm plans include SARA calculations documenting lack of SARA.
Note on B9: 12/12/2022: Triggered if Table B "ALERT! Gas or propane central water" note is triggered.
Note on B10: 12/12/2022: Triggered if Table B "ALERT! Combined domestic and" note is triggered.
Note on B11: 12/12/2022: Triggered if Table A says "State Building" in column 03 AND "New System" is selected in Table B column 01.
Note on B12: 12/12/2022: Triggers when F16e_EquipmentTypeApplies = "Yes"
Note on B13: 3/24/25 Triggers when J.08 == SARA Exception

## LMCC D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
1. | Table B indicates a solar water heating system will be used to comply with Title 24, Part 6. These systems shall be documented on the LMCC-SAB-E compliance document.
2. | Table B indicates a combined hydronic system will be used to comply with Title 24, Part 6. These systems shall be documented on the LMCC-MCH-E compliance document.
3 | Tables A and B indicate the project is a new State building. This requires 60% of energy for service water heating from site solar energy or recovered energy per §110.3(c)6.
4. | Table F indicates an electric water heater is being used to replace an existing electric resistance water heater.
Table J indicates project has inadequate Solar Access Roof Area (SARA) for solar water heating system. Please confirm plans include SARA calculations documenting lack of SARA.
Note on B9: 12/12/2022: Triggered if Table B "ALERT! Gas or propane central water" note is triggered.
Note on B10: 12/12/2022: Triggered if Table B "ALERT! Combined domestic and" note is triggered.
Note on B11: 12/12/2022: Triggered if Table A says "State Building" in column 03 AND "New System" is selected in Table B column 01
Note on B12: 12/12/2022: Triggers when F16e_EquipmentTypeApplies = "Yes"
Note on B13: 3/24/25 Triggers when J.08 == SARA Exception

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## F. Equipment
| User input |  |  | auto calculated |  |  | From another Table |  |  | From look up table
F. DOMESTIC HOT WATER EQUIPMENT
Table Instructions: Complete the following table to demonstrate compliance with mandatory equipment requirements in §110.1 and §110.3. Compliance with prescriptive requirements in §140.5(c)/§170.2(d) must also be demonstrated and with §141.0/§180.1/§180.2 for addition and alteration scopes.
Equipment Schedule: Water Heater Efficiency and Standby Loss
03 01 |  | 02 |  | 03 |  |  | 05 |  | 04
System Name: |  | Space Type: | See Dropdown | Exception to §140.5(c)/§170.2(d)32B: |  | dropdown | ¨ | Gas Service Water Heating System >= 1MMBtu/h1 | Capacity-weighted Average Efficiency (%)
06 05 | 06 | 07 | 08 | 09 | 10 |  | 11 | 12 | 13 | 14 | 13
Name or Item Tag | Quantity | System Status | Equipment Type | Volume (gal) | Rated Input Capacity (Btu/h) | Max GPM/ First Hour Rating (FHR) | Rated Efficiency | Minimum Efficiency Required | Efficiency Unit | Designed Standby Loss | Maximum Standby Loss
|  |  | See dropdown |  |  |  |  | Ben, values come from Table F-4 OR Table 110.2-J OR S140.5(c) (see column P) depending on column 08 |  |  | See Table F-4 in column P
1 FOOTNOTE: In systems >= 1MMBtu/h with multiple units, gas water heaters with input capacity > 100,000 Btu/h may meet the 90% Et requirement via an input capacity-weighted average.
2 FOOTNOTE: Compliant equipment may be found in the Modernized Appliance Efficiency Database System (MAEDBS) on the Energy Commission website: https://cacertappliances.energy.ca.gov/Pages/Search/AdvancedSearch.aspx
| Space Status Dropdown |  | Space Type Dropdown (select all that apply) |  | Exception Dropdown
| New/Addition |  | Multiple Dwelling Units/Hotel/Motel Guest Rooms |  | 25% of the annual service water-heating requirement is provided by site-solar energy or site-recovered energy per Exception 1 to 140.5(c) or 170.2(d)Bi
| Alteration |  | Individual Dwelling Unit/Hotel/Motel Guest Room |  | Adding gas SWH system >= 1MMBtu/h input capacity to existing building per Exception 6 to 141.0(a)
|  |  | Common Use Area |  | Heat pump system serves multifamily dwelling units only (§170.2(d)2)
|  |  | Nonresidential |  | Gas system serves multifamily dwelling units only in CZ 10-16 per Exception to 170.2(d)Bi
|  |  | State Building |  | Exceptions Do Not Apply
School
Individual School Bathroom
Multifamily Water Heating Equipment Serving in Individual Dwelling Units - §170.2(d)1, §180.2(b)3C
Equipment Type (select all that apply):
System Name: |  | System Name (01) from table above
16 | ¨ | Gas/propane instantaneous water heater with input rating ≤ 200,000 BTUH and no storage tank. Note: Can not comply using the prescriptive path with a storage tank per Exception 1 §170.2(d)1C (New Construction and Additions Only)
| ¨ | A single 240 volt heat pump water heater serving the dwelling unit. (New Construction and Additions Only, §170.2(d)1A)
| ¨ | A single 120 volt heat pump water heater serving a dwelling unit with 1 bedroom or less. (New Construction and Additions Only, Exception 2 to §170.2(d)1)
| ¨ | A single heat pump water heater that meets the requirements of NEEA Advanced Water Heater Specification Tier 3 or higher (§170.2(d)1B or §180.2(b)3).
| ¨ | A single heat pump water heater with storage tank located in the garage or conditioned space and be placed on an incompressible, rigid insulated surface with minimum R-10. The water heater shall be installed with a communication interface that meets either the requirements of 110.12(a) or has a ANSI/CTA-2045-B communication port . (Alterations Only, §180.2(b)3)
| ¨ | If the existing water heater is an electric resistance water heater, a consumer electric water heater. (Alterations only, §180.2(b)3)
17 | ¨ | Replacement or altered gas or propane water heater (Alterations only, §180.2(b)3ci)
1 FOOTNOTE: Dwelling units refers to hotel/ motel guest rooms and units in a multifamily residential occupancy. | For gas or propane water heaters serving individual dwelling units, the follow components are included in the design per §160.4: (New Construction and Additions only) - Dedicated 125V, 20 amp electrical receptacle that is connected to the panel with a 120/240V 3 conductor, 10 AWG copper branch circuit within 3 ft from the water heater that's accessible and with both ends of the unused conductor labeled with the word "spare" and be electrically isolated. A single pole circuit breaker space in the panel adjacent to the circuit breaker for the branch circuit is provided labeled with the word "future 240V use"; and - Category III or IV vent, or Type B vent with straight pipe between the outside termination and where the water heater is installed; and - Condensate drain that is no more than 2in higher than the base of the water heater and drains without pump assistance; and - Gas supply line with a capacity of at least 200,000 BTUH
Water Heating Equipment All Occupancies - §110.3(c)3, §140.5(a)
System Name: |  | System Name (01) from table above
| Yes | No | Not Applicable | Requirement
19 18 | ¨ | ¨ | ¨ | Unfired storage tank insulation shall have Internal + External ≥ R-16 OR External ≥ R-3.5. Label required per §110.3(c)3
20 19 | ¨ | ¨ | ¨ | New state buildings 60% of energy for service water heating from site solar energy or recovered energy per §110.3(c)5
21 20 | ¨ | ¨ | ¨ | Isolation valves for instantaneous water heater with input rating > 6.8 kBTUH or 2 kW has been specified per §110.3(c)6
21 | ¨ | ¨ | ¨ | School buildings < 25,000ft2 and < 4 stories must install a heat pump water heating system per §140.5(a)1. Water heating systems serving an individual bathroom space may be an instantaneous electric water heater.
22 | Air-Source Heat Pump Water Heaters (HPWHs) (§110.3(c)7)
| ¨ | ¨ | ¨ | Backup heat is required when inlet air is unconditioned unless the compressor cut-off temperature is below the Heating Winter Median of Extremes for the closest location listed in Table 2-3 from Reference Joint Appendix JA2.
| ¨ | ¨ | ¨ | Consumer integrated HPWHs shall meet one of the following ventilation requirements:
|  |  |  | Dropdown (to the right) |  |  |  |  | <<<< Dropdown | 110.3(c)7B1: Installed using a method provided by the manufacturer to meet or exceed the ventilation requirements of Section 110.3(c)7B2 through Section 110.3(c)7B4.
110.3(c)7B2: HPWHs without ducts: Installation space shall have a volume not less than the greater of 100 cubic feet per kBtu per hour of compressor capacity, or the minimum volume provided by the manufacturer.
Multifamily and Hotel/Motel Water Heating Equipment for Central Systems Serving Dwelling Units §170.2(d)2&3 | [9 empty] | 110.3(c)7B3: HPWHs without ducts: Installation space shall be vented to a communicating space via permanent openings.The minimum volume of the communicating space shall meet Section 110.3(c)7B2 minus the volume of the HPWH installation space. Permanent openings shall consist of a single layer of fixed flat slat louvers or grilles, with a minimum Net Free Area (NFA) detailed in Section 110.3(c)7B3ii.
Equipment Type (select all that apply): | [9 empty] | 110.3(c)7B4: HPWHs with ducts: Space joined to the installation space via ducts shall meet the minimum volume of Section 110.3(c)7B2 above, minus the volume of the HPWH installation space.All duct connections and building penetrations shall be sealed and ducts insulated to minimum of R-6. Permanent openings shall consist of a single layer of fixed flat slat louvers or grilles, with a minimum Net Free Area (NFA) detailed in Section 110.3(c)7B4v.
System Name: |  | System Name (01) from table above
22 23 | ¨ | Heat pump Water Heater (New Construction and Additions Only - §170.2(d)2A) | [9 empty] | S140.5(c)
|  | ¨ | The primary heat pump water heater shall be a single-pass heat pump water heater - §170.2(d)2Ai For systems with single pass primary heat pump water heater, the primary thermal storage tanks shall be piped in series if multiple tanks are used. For systems with multi-pass primary heat pump water heater, the primary thermal storage tanks shall be piped in parallel if multiple tanks are used. | [9 empty] | << 90% Et applies to >= 1MMBtu/h if "Exception does not apply" selected in col 05
|  | ¨ | The primary storage tank temperature setpoint shall be at least 135°F - §170.2(d)2Aiv
|  | ¨ | such that hot water from the recirculation loop tank is used for the temperature maintenance load before engaging the recirculation loop tank heater.
|  | ¨ | The minimum heat pump water heater compressor cut-off temperature shall be equal to or lower than 40°F ambient air temperature - §170.2(d)2Avi
|  | ¨ | Design documentation shall specify the operating conditions at which the primary heat pump water heater can supply hot water at design outlet water temperature without engaging auxiliary heating mechanism. - §170.2(d)2Avii
24 | ¨ | NEEA Advanced Water Heater Specification for commercial heat pump water heater Tier 2 or higher (§170.2(d)2A)
25 | ¨ | Gas/propane water heater (New Construction and Additions Only, §170.2(d)2B)
|  | ¨ | A solar water-heating system meeting the installation criteria specified in Reference Residential Appendix RA4 and with a minimum solar savings fraction of 0.20 in Climate Zones 1 through 9 or a minimum solar savings fraction of 0.35 in Climate Zones 10 through 1 - §170.2(d)2Bi . This system should be documented on the NRCC-SAB form OR;
|  | ¨ | A solar water-heating system meeting the installation criteria specified in Reference Residential Appendix RA4 and with a minimum solar savings fraction of 0.15 in Climate Zones 1 through 9 or a minimum solar savings fraction of 0.30 in Climate Zones 10 through 16. - §170.2(d)2Bii This system should be documented on the NRCC-SAB form. AND, a drain water heat recovery system that is field verified as specified in the Reference Appendix RA3.6.9.
| Equipment Type Dropdown for Column 08 |  | Volume Dropdown for Column 03
| Gas Instantaneous Consumer Rated Gas-Fired Instantaneous (50,000-200,000 BTUH) |  | < 2
| Electric Instantaneous Consumer Rated Gas-Fired Storage (< 75,000 BTUH) |  | Volume Dropdown for Column 03
| Gas Storage Residential-Duty Commercial Gas-Fired Storage (75,000-105,000 BTUH) |  | <30
| Electric Storage Consumer Rated Electric Instantaneous (<12kW) |  | 31-40
| Commercial Boilers Residential-Duty Commercial Electric Instantaneous (12-58.6kW) |  | 41-50
| Consumer Rated Electric Storage |  | 51-55
| Consumer Rated Electric Tabletop Water Heater |  | 56-60
| Commercial Gas Storage Water Heater |  | >75
| Commercial Gas Instantaneous Water Heater |  | Volume Dropdown for Column 03
| Commercial Gas Hot Water Supply Boilers |  | <50
| Commercial Electric Storage Water Heater |  | 51-60
| Residential-duty Gas Hot Water Supply Boilers (<300k Btu/h) |  | 61-75
| Commercial Package Gas Hot Water Supply Boilers (300k- <1MM Btu/h) |  | >75
S140.5(c) | Commercial Package Gas Hot Water Supply Boilers (>= 1MM Btu/h) |  | Volume Dropdown for Column 03
| NA: Central Heat Pump Water Heater |  | <30
| Non-Air Source Heat Pump Water Heater |  | >30
NEEA Individual Heat Pump Water Heater
Non-NEEA Individual Heat Pump Water Heater
Air Source Heat Pump Water Heater
1
Note on G7: 9.26.22 If anything other than "Exceptions Do Not Apply" is selected, 05 and 06 = blank/gray and the minimum efficiency should not come from 140.5. If 140.5 is the applicable efficiency, use table 110.2-J instead.
Note on K7: 2/5/25 Only populates if Col 05 is true equals (sum (Rated Efficiency x input capacity))/ total input capacity of water heaters > 100,000Btu/h in col 10 that are gas where F.06 = New/Addition This is gray if an exception has been selected in F.04, or the above is not true
Note on E9: 2/3/25 User input (no longer predefined dropdown)
Note on I9: Alexis Markstrum: Add Tooltip for where they can find the minimum requirements - Title 20 or DOE 10 CFR
Note on D10: 2/6/25 If F.02 == School And A.03 == 2-15 And A.04 = <=25,000 and F.06 == New/Addition, F.07 is restricted to: - Non-NEEA HPWH - NEEA HPWH - ASHPWH
Note on F10: 10.28.22 Always open
Note on I10: Values for Table 110.2-J changed for 2022 + new efficiency req in S1405.(c) for >=1MMbtu/h, pls review table in column P Need to add the UEF values from Individual Table col 06 above when "Consumer Rated" equipment type in col 08. Show "Must meet Federal Minimum Requirements"
Note on L10: Ben, columns 10, 14 & 15 grey out if there is no standby loss req. in table F-4. For the equation in F-4, Q is from column 10 & Vm or Vr is from column 09. Show "If applicable, must meet Federal Minimum Requirements"
Note on A22: 2/4/25 Ben, F.16 items expand for user input if "Individual Dwelling Unit/Hotel/Motel is Selected in F.02. Otherwise, these rows stay minimized.
Note on C24: 2/4/25 Only show rows applicable to the space selected for this system. User only gets to select one of the F16 options per system
Note on C25: 2/4/25 This is active for user input if F.06 = "New" Or "Addition" AND F.02 == "Individual Dwelling Unit" And F07 = Gas Instantaneous. NOT APPLICABLE TO LMCC-PLB
Note on C26: 2/4/25 Ben, This is active for user input if F.06 = "New" Or "Addition" AND F.02 == "Individual Dwelling Unit" And F.07 = Non NEEA Heat Pump Water Heater
Note on C27: 2/4/25 Ben, This is active for user input if F.06 = "New" Or "Addition" AND F.02 == "Individual Dwelling Unit" AND F07 = Non NEEA Heat Pump Water Heater OR NEEA Heat Pump Water Heater.. Otherwise, grey out this whole row (& rated vol sub rows)
Note on C28: 2/4/25 This is active for user input if F.02 =="Individual Dwelling Unit" And F07 = NEEA Individual Heat Pump Water Heater
Note on C29: 2/6/25 This is active for user input if F.02 =="Individual Dwelling Unit" And F.06 = "Alteration" and F07 = Non NEEA Heat Pump Water Heater
Note on C30: 2/6/25 Ben, This is active for user input F.02 =="Individual Dwelling Unit" And F.06 = "Alteration" is selected in Table B and F07 = Electric. Otherwise, grey out this whole row. Also, the selection of this by the user triggers the exceptional condition note in Item #4 in Table D.
Note on C31: 2/6/25 This is active for user input if F.02 =="Individual Dwelling Unit" And F.06 = "Alteration" and F07 = Gas. Otherwise, grey out this whole row & subrow
Note on A34: 2/6/25 Transfer all water heater systems here no matter the space type or system status
Note on C35: Alexis Markstrum: Only show rows applicable to the space selected for this system
Note on E37: 2/6/25 Only show row if 08 = Gas Storage, Electric Storage, NEEA HPWH, Non-NEEA HPWH, or ASHPWH
Note on E38: 2/6/25 Ben, This is active for user input If F.02 == "State Building".
Note on E39: 2/6/25 Only show this row if F.07 = Instantaneous or NEEA HPWH, Non-NEEA HPWH, or ASHPWH
Note on E40: 2/6/25 Only show this row if "School" is selected in F02
Note on B41: 2/6/25 Only show this and sub bullets below if F.07 = Air Source Heat Pump
Note on A46: 2/6/25 Expands for user input if F.02 == New And "Multiple Dwelling Units/Hotel/Motel Rooms . Otherwise, these rows stay minimized.
Note on C49: 2/6/25 This and all sub-bullets below are active for user input if F.06 == New and F.07 = Non-NEEA Heat Pump Water Heater. Otherwise, grey out this whole row
Note on B55: 11/20/24 Project must either indicate NEEA tier 2 or meet the requirements above to comply
Note on C55: 2/6/25 This is active for user input if F.06 == New and F07 = NEEA Heat Pump Water Heater.
Note on C56: 2/6/25 This is active for user input if F.06 == New and F07 = Gas
Note on D57: 2/6/25 This is active if cz == 1-9
Note on D58: 2/6/25 This is active if cz == 10-16
Note on D63: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Gas-Fired Instantaneous -Electric Instantaneous -Residential-Duty Commercial Electric Instantaneous
Note on D65: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Gas-Fired Storage -Electric Storage
Note on D72: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Residential-Duty Commercial Gas-Fired Storage
Note on B74: 10/23/20: When Electric Storagae Water Heater is selected in F.08, F.11 and F.12 should gray out.
Note on D77: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Electric Tabletop Water Heater
Note on B78: 4.12.22: Greys out col 09-15 because no efficiency requirements.

## G. Dist Syst
G. DOMESTIC HOT WATER DISTRIBUTION SYSTEM
Table Instructions: Complete the following table to demonstrate compliance for nonresidential occupancies with distribution requirements in §120.3 and §140.5. For multifamily and hotel/motel occupancies, compliance is demonstrated with requirements in §110.3(c), §160.4 and §170.2(d).
Recirculation Loops in Central Systems Serving Dwelling Units, Hotel/Motel Guest Rooms or Nonresidential Spaces - §110.3, §170.2(d)2
System Name: |  | System Name (01) from Section F
| Yes | No | Not Applicable | Requirement
01 | ¨ | ¨ | ¨ | Air release valve or verticle pump installation per §110.3(c)4A
02 | ¨ | ¨ | ¨ | Check valve or similar located between recirculation pump and water heating equipment to prevent backflow per §110.3(c)4B
03 | ¨ | ¨ | ¨ | Hose bibb installed between pump and equipment and isolation valve between hose bibb and equipment per §110.3(c)4C
04 | ¨ | ¨ | ¨ | Isolation valves on both sides of the pump per §110.3(c)4D
05 | ¨ | ¨ | ¨ | Cold water and recirculation loop piping shall not be connected to the hot water storage tank drain port per §110.3(c)4E
06 | ¨ | ¨ | ¨ | Check valve installed on cold water supply between hot water system and next closest tee on cold water supply per §110.3(c)4F
07 | ¨ | ¨ | ¨ | DWELLING UNITS ONLY: For central systems serving multiple dwelling units, design includes a recirculation system serving separate dwelling units per §170.2(d) unless building has < 8 dwelling units.
08 07 | ¨ | ¨ | ¨ | DWELLING UNITS ONLY: For heat pump water heating systems, the hot water return from the recirculation loop shall connect to a recirculation loop tank and shall not directly connect to the primary heat pump water heater inlet or the primary thermal storage tanks per §170.2(d)2Aii
09 08 | ¨ | ¨ | ¨ | DWELLING UNITS ONLY: For heat pump water heating systems, the fuel source for the recirculation loop tank shall be electricity if auxiliary heating is needed. The recirculation loop heater shall be capable of multi-pass water heating operation per §170.2(d)2Aiii B.
09 | ¨ | ¨ |  | DWELLING UNITS ONLY: The recirculation loop tank temperature setpoint shall be at least 10°F lower than the primary thermal storage tank temperature setpoint - §170.2(d)2Av
10 | ¨ | ¨ | ¨ | DWELLING UNITS ONLY: All hot water distribution piping shall be sized in accordance with the California Plumbing Code Appendix M per §170.2(d)2C.
11 | ¨ | ¨ | ¨ | DWELLING UNITS ONLY:A recirculation system with mechanical or digital thermostatic master mixing valve on each distribution supply and return loop and meet the requirements in Reference Appendix RA4.4, unless building has ≤ 8 dwelling units, per §170.2(d)2D.
12 | ¨ | ¨ | ¨ | DWELLING UNITS ONLY: Insulation for hot water pipes shall be field verified as specifid in Reference Appendix RA3.6.3 per §170.2(d)2E.
Distribution of Individual System(s) serving Dwelling Units - §170.2(d)1
System Name: |  | System Name (01) from Section F
| Yes | No | Not Applicable | Requirement
10 13 | ¨ | ¨ | ¨ | Per §170.2(d)1A, single 240 volt heat pump water heaters serving dwelling units must also include systems with:
| ¨ | ¨ | ¨ | ¨ | Compact hot water distribution system as specified in Reference Appendix RA4.4.16 in climate zone 1 & 16; AND
| ¨ | ¨ | ¨ | ¨ | A drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9 in climate zone 16.
11 14 | ¨ | ¨ | ¨ | A drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9 in climate zone 16 per §170.2(d)1B.
12 15 | ¨ | ¨ | ¨ | For recirculation distribution systems serving individual dwelling units, only Demand Recirculation Systems with manual on/off control as specified in the Reference Appendix RA4.4.9 shall be used per §170.2(d)1.
Mandatory Pipe Insulation All Occupancies - §120.3, §160.4
System Name: |  | System Name (01) from Section F
| Yes | Not Applicable | Requirement
13 16 | ¨ | ¨ | For systems serving dwelling units and common areas, pipe insulation must meet the minimum insulation requirements in Table 160.4-A (see below) except: - Piping that penetrates framing members shall not be required to have pipe insulation for the distance of the framing penetration. Piping that penetrates metal framing shall use grommets, plugs, wrapping or other insulating material to assure that no contact is made with the metal framing. Insulation shall abut securely against all framing members. - Piping installed in interior or exterior walls shall not be required to have pipe insulation if all of the requirements are met for compliance with Quality Insulation Installation (QII) as specified in the Reference Residential Appendix RA3.5. - Piping surrounded with a minimum of 1 inch of wall insulation, 2 inches of crawlspace insulation, or 4 inches of attic insulation, shall not be required to have pipe insulation.
14 17 | ¨ | ¨ | For systems serving nonresidential spaces, pipe insulation for the following applications is specified to comply with Table 120.3-A1 or or Table 120.3-A2 (see below) per §120.3: - Recirculating system piping, including supply and return piping of the water heater - The first 8 ft of hot and cold outlet piping, including between storage tank and heat trap, for a nonrecirculating storage system - Pipes that are externally heated
15 18 | ¨ | ¨ | Per §120.3(b)/ §160.4(f), pipe and appurtenance insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Protection shall include: - Insulation exposed to weather shall be installed with a cover suitable for outdoor service per §120.3(b)/ §160.4(f). - Pipe insulation buried below grade must be installed in a water proof and non-crushable casing or sleeve.
TABLE 120.3-A-1/ 160.4-A PIPE INSULATION THICKNESS
New table structure for 2025. Table 120.3-A was split into two Tables, Table 120.3-A-1 and Table 120.3-A-2. Minor formatting changes, no actual values changed.
Note on A3: 2/6/25 If F.02 == Multiple Dwelling Units, Common Use, or Nonresidential. Or B.01 == Alteration and B.02 = "Central System Serving Dweling Units" or "Nonresidnetial/common areas" This section is open for user input Else these rows stay minimized.
Note on C4: 2/5/25 If B.01 = alteration and alteration inlcudes distribution systems and not Equipment, this is user input
Note on E12: Sally Blair: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Central serving dwelling units" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E13: 2/6/25 If F.02 == multiple dwelling unit and F.23 == true Or B.01 == Alteration and B.02 = Central System (serving 2+ dwelling units) G.07-11 are open for user input Else this row stays minimized
Note on A20: 2/6/25 Table applies if F.02 == "Individual Dwelling Unit.." Else table stays minimized
Note on C21: 2/5/25 If B.01 = alteration and alteration inlcudes distribution systems and not Equipment, this is user input
Note on E23: 2/6/25 If F.16b or F16c == True Or B.01 == alteration, this row is open for user input Else this row stays minimized
Note on F24: 2/6/25 If F.16b or F16c == True And A.03 = 1 Or 16, this row is open for user input Else this row stays minimized
Note on F25: 2/6/25 If F.16b or F16c == True And A.03 = 16, this row is open for user input Else this row stays minimized
Note on E26: 2/6/25 If F.16d == True Or B.01 == alteration this row is open for user input Else this row stays minimized
Note on E27: 9.9.21: Always leave this row open for Y/N/NA if this subtable is triggered.
Note on C30: 2/5/25 If B.01 = alteration and alteration inlcudes distribution systems and not Equipment, this is user input
Note on D32: 2/5/25 If F.02 == Individual Dwelling Or Multiple Dwelling, Or B.01 = Alteration This row is open for user input Else this row stays minimized
Note on D33: 2/5/25 If F.02 == Nonresidential, Or B.01 = Alteration This row is open for user input Else this row stays minimized
Note on D34: 2/5/25 Always show this row

## H. Controls
H. DOMESTIC HOT WATER SYSTEM CONTROLS - §110.3, §120.9, §160.4(d), §170.2(d), §180.1(b)3
Table Instructions: Complete the following table to demonstrate compliance with controls requirements in §110.3 for all occupancies. For nonresidential occupancies, compliance is demosntrated with requirements in §120.9. For multifamily residential and hotel/motel occupancies, compliance is demonstrated with requirements in §160.4(ed) and §170.2(d).
System Name: |  | System Name (01) from Section F
| Yes | No | Not Applicable | Requirement
01 | ¨ | ¨ | ¨ | Construction documents require manufacturer certification that service water-heating systems are equipped with automatic temperature controls capable of adjusting temperature settings per §110.3(a).
02 | ¨ | ¨ | ¨ | Systems with capacity > 167,000 BTUH equipped with outlet temperature controls per §110.3(c)1 unless covered by California Plumbing Code Section 613.0.
03 | ¨ | ¨ | ¨ | Controls for circulating pumps or electrical heat trace systems are capable of automatically turning off the system per §110.3(c)2 unless system serves healthcare facility.
04 | ¨ | ¨ | ¨ | For recirculation systems serving multiple dwelling units, design includes automatic pump controls a mechanical or digital thermostatic master mixing valve on each distribution supply and return loop per §170.2(d), or §180.1(b)3 for additions.
05 | ¨ | ¨ | ¨ | For recirculation systems serving individual dwelling units, design includes manual on/off controls as specified in Reference Appendix RA 4.4.9 per §170.2(d).
06 | ¨ | ¨ | ¨ | Combustion air positive shut-off shall be provided per §120.9(a) & §160.4(ed) on all newly installed commercial boilers as follows: - Boiler with input capacity >= 2.5 MMBtu/h, in which the boiler is designed to operate with a nonpositive vent static pressure - Boilers where one stack serves two or more boilers with a total combined input capacity per stack of 2.5 MMBtu/h.
07 | ¨ | ¨ | ¨ | Boiler combustion air fans with motors >= 10 hp shall meet one of the following for newly installed boilers per §120.9(b) & §160.4(d)2: - The fan motor shall be driven by a variable speed drive OR - The fan motor shall include controls that limit the fan motor demand to <= 30% of the total design wattage at 50% of the design air volume.
08 | ¨ | ¨ | ¨ | Newly installed boilers with an input capacity >= 5 MMbtu/h and a steady state full-load combustion efficiency < 90% shall maintain excess (stack-gas) oxygen concentrations <= 5% by volume on a dry basis over firing rates of 20-100%. Combustion air volume shall be controlled with respect to firing rate or flue gas oxygen concentration. Use of a common gas and combustion air control linkage or jack shaft is prohibited per §120.9(c) & §160.4(d)3
Note on C3: 2/7/25 If B.01 = alteration and alteration inlcudes distribution systems and not Equipment, this is user input
Note on E5: 2/7/25 This row is open for user input if F02 != Dwelling Units/Hotel/Motel Guest Rooms
Note on E6: 2/7/25 This row is open for user input if one or more F.09 >= 167,000 Or if B.01 = Alteration and Table F is not in scope Else this row stays minimized
Note on E7: 2/7/25 this row is open for user input if A.03 != healthcare Else this row stays minimized
Note on E8: 2/7/25 This row is open for user input if F.02 = Multiple dwelling units Or B.02 = Central System serving 2+ Dwelling units Else this row stays minimized
Note on E9: 2/7/25 This row is open for user input if F.02 = Multiple dwelling units Or B.02 = Central System serving 2+ Dwelling units Else this row stays minimized
Note on E10: 2/7/25 This row is open for user input if one or more F.09 >=2,500,000 Or If B.01 = Alteration and Table F is not in scope Else this row stays minimized
Note on E11: 2/7/25 This row is open for user input if one or more F.09 >=300,000 Or If B.01 = Alteration and Table F is not in scope Else this row stays minimized
Note on E12: 2/7/25 This row is open for user input if one or more F.09 >=5,000,000 Or If B.01 = Alteration and Table F is not in scope Else this row stays minimized

## I-Electric Ready
NEW TABLE FOR PLB FOR 2025
I. ELECTRIC READY BUILDINGS
This table includes electric ready requirements that must be met when installing gas or propane water heaters in dwelling units to demonstrate compliance with §160.9.
01 | Systems serving multifamily occupancy that use gas or propane include: |  | ¨ Gas/propane water heater serving individual dwelling units | ¨ Gas/propane water heater serving multiple dwelling units | ¨ None of these
Gas/Propane Water Heaters Serving Individual Dwelling Units - §160.9(e)
System Name |  | User Input
| Yes | Requirement
02 | ¨ | 160.9(e)2: A condensate drain that is no more than 2 inches higher than the base of the installed water heater, and allows natural draining without pump assistance
03 | ¨ | A ventilation method meeting the following per 160.9(e)4: Dropdown options (only the one that is selected shows up): - The designated space for the future heat pump water heater shall have a minimum volume of 700 cubic feet; or - The designated space for the future heat pump water heater shall vent to a communicating space in the same pressure boundary via permanent openings with a minimum total NFA of 250 square inches., so that the total combined volume connected via permanent openings is 700 cubic feet or larger. The permanent openings shall be: - Fully louvered doors with fixed louvers; or - Two permanent fixed openings located within 12 inches from the enclosure top and bottom; - The designated space for the future heat pump water heater shall include two 8 inches capped ducts, venting to the building exterior: - All ducts, connections, and building penetrations shall be sealed. - Exhaust air ducts and all ducts which cross pressure boundaries shall be insulated to a minimum insulation level of R-6. - Airflow from termination points shall be diverted away from each other.
Gas/Propane Water Heaters Serving Multiple Dwelling Units - §160.9(f)
System Name |  | User Input
| Yes | Requirement
04 | ¨ | 160.9(f)2A: Space shall be reserved for a Heat Pump. The minimum space reserved shall include space for service clearances and air flow clearances and shall meet the following: Dropdown options (only the one that is selected shows up): - The space reserved shall be the space required for a heat pump water heater system that meets the total building hot water demand as calculated and documented by the responsible person associated with the project; or - The space reserved shall meet the requirements specified in Joint Appendix JA15.2.1.
05 | ¨ | 160.9(f)2B: Space shall be reserved for Tanks.The minimum space reserved shall include space for service clearances and shall meet the following: Dropdown options (only the one that is selected shows up): - The space reserved shall be the space required for a heat pump water heater system that meets the total building hot water demand as calculated and documented by the responsible person associated with the project; or - The space reserved shall meet the requirements specified in Joint Appendix JA15.2.2.
06 | ¨ | 160.9(f)3: Ventilation shall be provided by meeting the following: Dropdown options (only the one that is selected shows up): - Physical space reserved for the heat pump shall be located outside; or - A pathway shall be reserved for future routing of supply and exhaust air via ductwork from the reserved heat pump location to a suitable outdoor location. Penetrations through the building envelope for louvers and ducts shall be planned and identified for future use. The reserved pathway and penetrations through the building envelope shall be sized to meet one of the following: - The reserved pathway and penetrations shall be sized to serve a heat pump water heater system that meets the total building hot water demand as calculated and documented by the responsible person associated with the project. - The reserved pathway and penetrations shall be sized to meet the requirements specified in Joint Appendix JA15.2.3.
07 | ¨ | 160.9(f)4: Condensate drainage piping. An approved receptacle that is sized per the California Plumbing Code for condensate drainage shall be installed within 3 feet of the reserved heat pump location, or piping shall be installed from within 3 feet of the reserved heat pump location to an approved discharge location that is sized in accordance with the California Plumbing Code, and meet the following: Dropdown options (only the one that is selected shows up): - Condensate drainage shall be sized to serve a heat pump water heater system that meets the total building hot water demand as calculated and documented by the responsible person associated with the project. - Condensate drainage piping shall be sized to meet the requirements specified in Joint Appendix JA15.2.4.
Note on A4: 11/18/24 This table is triggered if A.03 = highrise residential or low-rise residential
Note on A6: 2022: selection triggers associated subtable below, otherwise subtable doesn't show.
Note on D6: 3/24/25 These three cells should be auto calculated based on Table F. We can determine if they have gas/propane serving dwelling units.

## J. PoolSpa
| User input |  | auto calculated | [5 empty] | From another Table
NEW TABLE FOR PLB FOR 2025 (was Section R. on PRC form, changes shown are from 2022 table to 2025 from that table)
J. POOL & SPAs
This table documents compliance with mandatory pool/spa requirments in §110.4/§160.7.
Is the pool/spa heated? | Heated/NotHeated
01 | 02 | 03 | 04 | 05 | 06 | 06 07 | 08 | 07 09 | 08 10
Pool/ Spa Description | Pool/Spa Service Type | Efficiency1 | On/Off Control | Instructions & Covers | Covers | Electric Resistance Heating Equipment | Heating Source Sizing | Piping | Pool Directional Inlets & Pump Control
| Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
1 FOOTNOTE: CEC's appliance efficiency database, the Modernized Appliance Efficiency Database System (MAEDBS), is available online at https://cacertappliances.energy.ca.gov/Pages/ApplianceSearch.aspx.
1 FOOTNOTE: Heat pump pool heaters with supplementary heaters shall also meet the requirements in Section 110.4(d).
| Type Dropdown | Efficiency dropdown | Control Dropdown | Instructions Dropdown | Covers Dropdown | Elec Resistance Heating Dropdown | Heating Source Sizing Dropdown | Piping Dropdown | Inlet Dropdown
| Serves multiple tenants or public | Equipment subject to State/federal appliance efficiency standards complies with Section 110.1 is in the CEC's directory of certified equipment | Includes on-off switch mounted on outside of heater allowing shutting off heater without adjusting thermostat | Includes weatherproof plate with energy efficiency rating and instruction for operation Heated outdoor pools/spas must include cover and weatherproof instruction for proper care of when cover is used | Outdoor pool/spa has pool cover installed | No electric resistance heating used Installed equipment meets standards from Table 110.4-A | Solar heating system w/ collector surface >= 65% of pool/spa surface area | >= 36 18 in of pipe installed between filter & heater or dedicated suction and return lines to allow for the future addition of solar heating equipment | Has directional inlets to mix the pool water & control mechanism to allow pumps to run only during off-peak electric demand period and for min time necessary
| Serves public |  |  |  | NA: Pool/spa heated by solar heating system | Listed package units with fully insulated enclosures, and with tight-fitting covers that are insulated to at least R-6 | Heat pump heater that meets sizing requirements of JA16.3. Supplementary heater can be any energy source.1 | Built-in/built-up connections installed to allow for future addition of solar heating equipment | NA: Spa
| Serves one tenant |  |  |  |  | Pools/spas where >= 60% of annual heating energy is from site solar energy or recovered energy | System where >= 60% of heating energy from on-site renewable or recovered energy | NA: Pool/spa heated by solar heating system
Combination of solar heating system and heat pump heater without supplementary heater
Heating system determined by the Executive Director to use no more energy than other allowed systems
NA: Portable electric spa compliant with 20 CCR § 1605.3(g)(7) of Appliance Efficiency Regulations per Exception 1 to 110.4(c)
NA: Alteration to existing pool/spa with existing heating system per Exception 2 to 110.4(c)
NA: Pool/spa heated by solar heating system without backup heater per Exception 3 to 110.4(c)
NA: Heating system used for permanent spa applications in exsting buildings with gas available per Exception 4 to 110.4(c)
NA: Heating system used for permanent spa application where there is inadequate SARA for a solar heating system per Exception 5 to 110.4(c)
Additional Requirements for Pool/ Spa Serving One Tenant §150.0(p)
Pool/Spa Description | Pulls from J.01 above
| Yes | Not Applicable | Requirement
11 | ¨ |  | Dedicated-purpose pool pumps and replacement dedicated-purpose pump motors subject to State or Federal appliance standards shall be listed in the Commission's directory of certified equipment. - Dedicated-purpose pool pumps shall meet 20 CCR § 1605.1(g)(7) of the Appliance Efficiency Regulations. - Replacement dedicated-purpose pool pumpmotors shall meet 20 CCR § 1605.3 of the Appliance Efficiency Regulations.
12 09 | ¨ |  | All pump flow rates shall be calculated using H = C × F2 WHERE: H is the total system head in feet of water F is the flow rate in gallons per minute (gpm) C is a coefficient based on the volume of the pool (0.0167 for pools less than or equal to 17,000 gallons & 0.0082 for pools greater than 17,000 gallons)
13 10 | ¨ |  | Filtration pumps shall be sized, or if programmable, shall be programmed, so that the filtration flow rate is not greater than the rate needed to turn over the pool water volume in 6 hours or 36 gpm, whichever is greater.
11 | ¨ |  | Pump motors used for filtration shall meet the applicable federal standard in 10 CFR 431.465.
14 12 | ¨ | ¨ | Each auxiliary pool load shall be served by either separate pumps or the system shall be served by a multispeed pump if pump hp >= 1. Multispeed Dedicated-purpose pool pumps with more than one speed shall have: - Controls which default to the filtration flow rate when no auxiliary pool loads are operating; and - Multispeed pumps the Controls shall default to the filtration flow rate setting within 24 hours and shall have an override capability for servicing.
15 13 | ¨ |  | System Piping must meet the following requirements: - A length of straight pipe that is greater than or equal to at least 4 pipe diameters shall be installed before the pump; and - Pool piping shall be sized so that the velocity of the water at maximum flow for auxiliary pool loads does not exceed 8 feet per second in the return line and 6 feet per second in the suction line; and - All elbows shall be sweep elbows or of an elbow-type that has a pressure drop of less than the pressure drop of straight pipe with a length of 30 pipe diameters.
16 14 | ¨ |  | Filters shall be at least the size specified in NSF/ANSI 50 for public pool intended applications.
17 15 | ¨ |  | Minimum diameter of backwash valves shall be 2 inches or the diameter of the return pipe, whichever is greater.
Note on B7: Alexis Markstrum: If "Not Heated" is selected, gray out fields 03 - 08
Note on G15: Alexis Markstrum: Show Table 110.4-A (to the right) if selected
Note on B16: Alexis Markstrum: Triggers Rows 14, 15, and 16 from "Additional Requirements…" subtable below
Note on B17: 11.21.21: Triggers "Additional Requirements…" subtable below.

## K. NRCI
IK. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Nonresidential, Hotel/Motel, and High-rise Multifamily and Multifamily Mixed-use Certificates of Installation
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
n |  | NRCI-PLB-E - Must be submitted for all buildings
CEC, It looks like we didn't totally think this through for 2019 & these two NRCIs should not be listed here since they are related to HERS compliance options for the performance path only & therefore would not be triggered for prescriptive compliance. Please let me know if I'm misunderstanding or we need to do something different.
Note on B5: 9.9.21: Need to replace w updated URL
Note on B8: 1/9/23: Defaults to "Yes" and cannot be changed to "No."

## K. LMCI
IK. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Low-rise Multifamily and Multifamily Mixed-use Certificates of Installation
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
n |  | LMCI-PLB-E - Domestic Water Heating System
n |  | LMCI-PLB-01-E - Multifamily Central Hot Water System Distribution
n |  | LMCI-PLB-02-E - Individual Dwelling Unit Hot Water System Distribution
Note on B4: 9.10.21: This subtable is triggered if the "MF <= 3 stories" is selected in A03
Note on B5: 9.9.21: Need to replace w updated URL
Note on B8: 1/9/23: Defaults to "Yes" and cannot be changed to "No."
Note on B10: Trujillo, Charlie: Triggers Yes if B02 = "Individual Dwelling Unit System(s)" Otherwise = "No"

## L. NRCA
JL. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
There are no Certificates of Acceptance applicable to service water heating requirements.
CEC to confirm still no NRCA for PLB

## M. NRCV
KM. DECLARATION OF REQUIRED CERTIFICATES OF VERIFICATION
Nonresidential, Hotel/Motel, and High-rise Multifamily and Multifamily Mixed-use Certificates of Verification
There are no Certificates of Verification for nonresidential, hotel/motel, high-rise multifamily and mixed-use buildings complying prescriptively.
CEC, It looks like we didn't totally think this through for 2019 & these two NRCVs should not be listed here since they are related to HERS compliance options for the performance path only & therefore would not be triggered for prescriptive compliance. Please let me know if I'm misunderstanding or we need to do something different.
Note on B4: 9.9.21: Trigger this subtable if EITHER "High-rise Residential" OR "Hotel/Motel" from Table A.

## M. LMCV
KM. DECLARATION OF REQUIRED CERTIFICATES OF VERIFICATION
Low-rise Multifamily and Multifamily Mixed-use Certificates of Verification
There are no Certificates of Verification for low-rise multifamily and mixed-use buildings complying prescriptively.
CEC, Since the LMCVs are all related to HERS compliance options, I've put in that there are none. Please let me know if I'm misunderstanding or we need to do something different.
Note on B4: 9.10.21: This subtable is triggered if the "MF <= 3 stories" is selected in A03

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/AEA/ECC HERS Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Designer Name: | Responsible Designer Signature:
Responsible Person Scope:
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-PLB form.
?