## New Table Sequence
Label | Table Title | Trigger within: | Note:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Indoor Lighting Fixture Schedule | ALWAYS except for RPR | this table actually won't show up if table B only includes a Rated Power Reduction compliance method.
Table G | Modular Lighting Systems | Table F
Table H | Indoor Lighting Controls (Not Including PAFs) | If F is triggered, so is H.
Table I | Lighting Power Allowance: Complete Building or Area Category Methods | Table B
Table J | Additional Lighting Allowance: Area Category Method Qualifying System | Table I
Table K | Tailored Method General Lighting Power Allowance | Table B
Table L | Additional Lighting Allowance: Tailored Wall Display | Table K
Table M | Additional Lighting Allowance: Tailored Floor and Task Lighting | Table K
Table N | Additional Lighting Allowance: Tailored Ornamental/ Special Effects | Table K
Table O | Additional Lighting Allowance: Tailored Very Valuable Merchandise | Table K
Table P | Power Adjustment: Lighting Control Credit (PAF) | Table I & Table K
Table Q | Rated Power Reduction Compliance For Alterations | ??
Table R | 80% Lighting Power For Alterations | Table H
Table S | Daylighting Design Power Adjustment Factor (PAF) | Table P
Table T | Dwelling Unit Lighting | Table A
Table T U | Declaration of Required Certificates of Installation | ALWAYS
Table U V | Declaration of Required Certificates of Acceptance | ALWAYS
- | Documentation Author's Declaration Statement | ALWAYS

## Hyperlinks
Label | Tables
§110.9 | Header, H
§110.12(c) | Header
§130.0 | Header
§130.0(c) | F
§130.1 | Header
§140.6 | Header, B
§141.0(b)2 | Header, B
§140.6(a) | C, I
§140.6(a)2 | C, P
§140.6(b) | C, I
§140.6(c)1 | C
§140.6(c)2 | C
§140.6(c)3 | C, K
§140.6(c)2G | C
§140.6(a)4B | F
§140.6(a)3 | F
§130.0(c)6 | G
§130.1(a) | H
§130.1(b) | H
§130.1(c) | H
§130.1(d) | H
§130.1(d)2 | H
§140.6(d) | H
§140.6(a)1 | H
§140.6(c) | I
Table 140.6-C | J
§140.6(c)3J | O
Table 140.6-A | P
§140.3(d) | P, S
§141.0(b)2I(iii) | Q
Table 140.3-D | S

## NRCC Headers
| User input |  | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Indoor Lighting
NRCC-LTI-E (Created XX/XX) |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-LTI-E
This document is used to demonstrate compliance with requirements in §110.9, §110.12(c), §130.0, §130.1, §140.6, and §141.0(b)2 for indoor lighting scopes using the prescriptive path for nonresidential and hotel/motel occupancies. It is also used to document compliance with requirements in §160.5, §170.2(e) and §180.2(b)4 for indoor lighting scopes using the prescriptive path for multifamily occupancies. Multifamily includes dormitory and senior living facilities.
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Indoor Lighting
NRCC-LTI-E (Created XX/XX) |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-LTI-E
Project Name: |  | Remove this field on all but first page header |  |  | Report Page: | Page 2 of ??
Project Address: |  | Remove this field on all but first page header |  |  | Date Prepared:
CA Building Energy Efficiency Standards - 201922 Nonresidential Compliance: http://www.energy.ca.gov/title24/201922standards
Heading First Page Only
Heading All Other Pages
Footer All Pages

## LMCC Headers
| User input |  | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Indoor Lighting
LMCC-LTI-01-E (Created XX/XX) |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | LMCC-LTI-01-E
This document is used to demonstrate compliance with requirements in §110.9, §110.12(c), §130.0, §130.1, §140.6, and §141.0(b)2 for indoor lighting scopes using the prescriptive path for nonresidential and hotel/motel occupancies in low-rise multifamily mixed-use buildings. It is also used to document compliance with requirements in §160.5, §170.2(e) and §180.2(b)4 for indoor lighting scopes using the prescriptive path for multifamily occupancies. Multifamily includes dormitory and senior living facilities.
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Indoor Lighting
LMCC-LTI-01-E (Created XX/XX) |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | LMCC-LTI-01-E
Project Name: |  | Remove this field on all but first page header |  |  | Report Page: | Page 2 of ??
Project Address: |  | Remove this field on all but first page header |  |  | Date Prepared:
CA Building Energy Efficiency Standards - 2022 Nonresidential Compliance: http://www.energy.ca.gov/title24/2022standards
Heading First Page Only
Heading All Other Pages
Footer All Pages
Note on A7: 11.3.21: Update langauge to make it clear this form is for LRMF/LRMU only.
Note on A20: 8.16.21: Need to replace w 2022 Standards URL once available

## NRCC A. General Info
| User input |  | auto calculated |  | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 04 | Total Conditioned Floor Area (ft²)
02 | Climate Zone |  |  |  |  | 05 | Total Unconditioned Floor Area (ft²)
03 | Occupancy Types Within Project (select all that apply): |  |  |  |  | 06 | # of Stories (Habitable Above Grade)
¨ | Office | ¨ | Retail | ¨ | Warehouse | ¨ | Hotel/ Motel | ¨ | School | ¨ | Support Areas
¨ | High-Rise Residential Multifamily/ MF Mixed-use >= 4 stories (includes dormitory, senior living) |  |  | ¨ | Healthcare Facilities | ¨ | Parking Garage
|  |  |  | ¨ | Relocatable | ¨ | Other (Write In) All Others | ¨ | Theater | ¨ | Sports Arena
¨ | Auditorium | ¨ | Commercial/ Industrial | ¨ | Grocery Store | ¨ | Religious Facility | ¨ | Data Center | ¨ | Convention Center
¨ | Classroom | ¨ | Library | ¨ | Gymnasium | ¨ | Restaurant/ Commercial Kitchen | ¨ | Financial Institution | ¨ | Medical Clinic
Note on J4: Sally Blair: Table D checks if Conditioned and Unconditioned Floor Area entered here match what's entered in Table B, I and L. If "Rated Power Reduction" is chosen in Table B, this greys out and goes blank. Don't grey this out if Rated Power Reduction is chosen in Table B. column 02. It just remains as user-entry all the time.
Note on B8: 8.19.21: Triggers Table T if selected
Note on F8: Rebecca Rice: when Healthcare Facilities is checked, do not populate Table I. Instead show "This Section Does Not Apply"

## LMCC A. General Info
| User input |  | auto calculated |  | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 04 | Total Conditioned Floor Area (ft²)
02 | Climate Zone |  |  |  |  | 05 | Total Unconditioned Floor Area (ft²)
03 | Occupancy Types Within Project (select all that apply): |  |  |  |  | 06 | # of Stories (Habitable Above Grade)
¨ | Office | ¨ | Retail | ¨ | Warehouse | ¨ | Hotel/ Motel | ¨ | School | ¨ | Support Areas
¨ | Low-Rise Residential Multifamily/ MF Mixed-use < 4 stories (includes dormitory, senior living) |  |  | ¨ | Healthcare Facilities | ¨ | Parking Garage
|  |  |  | ¨ | Relocatable | ¨ | Other (Write In) All Others | ¨ | Theater | ¨ | Sports Arena
¨ | Auditorium | ¨ | Commercial/ Industrial | ¨ | Grocery Store | ¨ | Religious Facility | ¨ | Data Center | ¨ | Convention Center
¨ | Classroom | ¨ | Library | ¨ | Gymnasium | ¨ | Restaurant/ Commercial Kitchen | ¨ | Financial Institution | ¨ | Medical Clinic
Note on J4: Sally Blair: Table D checks if Conditioned and Unconditioned Floor Area entered here match what's entered in Table B, I and L. If "Rated Power Reduction" is chosen in Table B, this greys out and goes blank. Don't grey this out if Rated Power Reduction is chosen in Table B. column 02. It just remains as user-entry all the time.
Note on B8: 8.19.21: Triggers Table T if selected
Note on F8: Rebecca Rice: when Healthcare Facilities is checked, do not populate Table I. Instead show "This Section Does Not Apply"

## B. Project Scope
| User input | auto calculated |  | From another Table |  | From look up table
B. PROJECT SCOPE
This table includes any lighting systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.6/§170.2(e) or §141.0(b)2/§180.2(b)4 for alterations.
Scope of Work |  |  | Conditioned Spaces |  | Unconditioned Spaces
01 |  |  | 02 | 03 | 04 | 05
My Project Consists of (check all that apply): |  |  | Calculation Method | Area (ft²) | Calculation Method | Area (ft²)
New Lighting System
| New Lighting System- Parking Garage |  | only dropdown choice is "Complete Building" |  | only dropdown choice is "Complete Building"
Altered Lighting System
Total Area of Work (ft2) |  |  | 0 |  | 0
ALERT! The Rated Power Reduction Method for alterations may only be used for one-for-one luminaire alterations within a building or tenant space of 5,000 ft2 or less per §141.0(b)2Iiii/§180.2(b)4.
|  |  | Calculation Method |  | Calculation Method
|  |  | Complete Building | <<< | Complete Building | Triggers Table F, Table H, and Table I
|  |  | Area Category | <<< | Area Category | Triggers Table F, Table H, and Table I
|  |  | Tailored | <<< | Tailored | Triggers Table F, Table H, and Table K
|  |  | Area Category + Tailored | <<< | Area Category + Tailored | Triggers Table F, Table H, Table I, and Table K
|  | only shows up for alterations >> | Rated Power Reduction | <<< | Rated Power Reduction | Triggers Table Q
Add Altered Lighting System
Remove Last Altered System
Add Parking Garage- Complete Bldg Method
Remove Parking Garage
Row 14 shows up if user selects "Rated Power Reduction" in column 02 AND column 03 > 5000 OR if user selects "Rated Power Reduction" in column 04 AND column 05 > 5000 OR if user selects "Rated Power Reduction" in columns 02 and 04 AND column 03 + column 05 > 5000.
Note on I9: Sally Blair: Row 9 is what shows up if "Add Parking Garage" button is used
Note on G16: Sally Blair: This dropdown customizes- the only choice in this dropdown is "Complete Building" if column 02 is "Complete Building"

## C. Compliance
| User input | [9 empty] | From look up table
C. COMPLIANCE RESULTS
If any cell on this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D. for guidance.
Lighting in conditioned and unconditioned spaces must not be combined for compliance per §140.6(b)1/ §170.2(e). | Allowed Lighting Power per §140.6(b)/§170.2(e) (Watts) | [5 empty] | > | AdjustedLighting Power per §140.6(a)/§170.2(e) (Watts) |  |  |  | Compliance Results
| 01 | 02 | 03 | 04 | = | 05 |  | 06 | 07 | = | 08 | 09
| Complete Building §140.6(c)1 | Area Category §140.6(c)2/ §170.2(e)4 | Area Category Additional §140.6(c)2G/ §170.2(e)4Av (+) | Tailored §140.6(c)3/ §170.2(e)4B (+) |  | Total Allowed (Watts) |  | Total Designed (Watts) | Adjustments |  | Total Adjusted (Watts) *Includes Adjustments | 05 Must be >= 08 §140.6/§170.2(e)
PAF Lighting Control Credits §140.6(a)2/ §170.2(e)1B (-)
| (See Table I) | (See Table I) | (See Table J) | (See Table K) |  |  |  | (See Table F) | (See Table P)
Conditioned: | 0 | 0 | sum of Total Additional Allowance for whole table | #VALUE! | = | #VALUE! | > | 0 | 0 | = | 0 | #VALUE!
Unconditioned: | 0 | 0 | sum of Total Additional Allowance for whole table | #VALUE! | = | #VALUE! | > | 0 | 0 | = | 0 | #VALUE!
Controls Compliance (See Table H for Details) | [10 empty] | COMPLIES with Exceptional Conditions or COMPLIES or DOES NOT COMPLY
Rated Power Reduction Compliance (See Table Q for Details) | [10 empty] | COMPLIES or DOES NOT COMPLY or NOT APPLICABLE
Note on B11: Benjamin Park: column 01 to 09 should default to blank and grey. The background color of a cell will change to white when a relevant table is triggered. Same for Unconditioned Areas.
Note on N11: Sally Blair: Should default to blank. 1. Will change to "DOES NOT COMPLY" if 08>05. 2. Will change to COMPLIES if 08<=05. Same for Unconditioned Areas.
Note on L13: 10.01.20 (in bold) Controls Compliance section should default to grey and blank. 1 . Will change to "Does Not Comply" if Table H is triggered but the conditions below are not met, OR if ANY of the notes in Table D rows 17, OR 18, OR 19 have been triggered 2. Will change to "Complies" if H.01-H.10 has been completed 3. Will change to "Complies with Exceptional Conditions" if H.01-H.10 have been completed AND a choice with a * has been chosen AND notes have been entered for every notes row that is triggered.
Note on L14: Usability Update 7.19.19: Should default to "NOT APPLICABLE". 1. Will change to "Does Not Comply" when Table Q is triggered but has not been completed and/or Percent Power Reduction <0.4 2.Will change to "Complies" if Table Q.01 and Q.03- Q19 have been completed or greyed out/not triggered, and Percent Power Reduction >= 0.4. 3. Will change to "Complies" if Q01 and Q.02b (all spaces are excepted) are checked

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
The conditioned and/or unconditioned floor area entered in Table A. does not match the total areas entered in Table B or Table I.
Table H. indicates a control requiring a note describing the compliance approach, but no notes have been entered.
Track Lighting has been included in this project, details are provided in Table G.
Track lighting has been indicated on Table F, however Table G has not been completed to calculate the allowance.
User entered Notes in Table H will show up in Table D.
User entered Notes in Table Q will show up in Table D.
If the user changes radio button in Table U T, a note saying "Selections made in Table U T have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination." should show up in Table D.
If the user changes radio button in Table V U , a note saying "Selections made in Table V U have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination." should show up in Table D.
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project is an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, Total Adjusted Power > 0.8 x Total Allowed in Table C. |  |  |  |  | Indicates wither LP is over or under 80% for ONLY ALTERED scopes
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project includes an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, alteration lighting power documented in Table R. exceeds .8 |  |  |  |  | Indicates wither LP is over or under 80% for ALTERED AND NEW scopes
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project includes an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, Table R. has not been completed to demonstrate compliance.
Note on A17: Usability Update: Both notes about Table H. 80% LP options triggered in Table H.
Note on A18: Usability Update 7.19.19: The trigger for this note has been changed from the value 80 to .8 to be consistent throughout the form. The value in Table R displays its percetnage as a decimal so this needs to be triggered based on a decimal now
Note on A19: Usability Update: triggered by Table R.

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## F. Lighting Schedule
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
F. INDOOR LIGHTING FIXTURE SCHEDULE
This table includes all permanent designed lighting and all portable lighting in offices. This table includes all planned permanent and portable lighting other than dwelling unit/ hotel/ motel room lighting. Multifamily dwelling unit and hotel/motel room lighting is documented in Table T. If using Table T to document lighting in multifamily common use areas providing shared provisions for living, eating, cooking or sanitation, those luminaires are not included here.
Designed Wattage: Conditioned Spaces | [10 empty] | NA8 Default
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |  | Mfr. Spec¹
Name or Item Tag | Complete Luminaire Description | Modular (Track) Fixture | Small Aperture & Color Change1 | Watts per luminaire2 | How Wattage is Determined | Total Number Luminaires | Excluded per §140.6(a)3/ §170.2(e)2C | Design Watts | Field Inspector |  | Other
[9 empty] | Pass | Fail
|  | ¨ | dropdown |  | Dropdown |  | ¨ | 0 | ¨ | ¨
Total Designed Watts CONDITIONED SPACES: | [7 empty] | 0
Designed Wattage: Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Name or Item Tag | Complete Luminaire Description | Modular (Track) Fixture | Small Aperture & Color Change1 | Watts per luminaire2 | How Wattage is Determined | Total Number Luminaires | Excluded per §140.6(a)3/ §170.2(e)2C | Design Watts | Field Inspector
[9 empty] | Pass | Fail
|  | ¨ | dropdown |  | dropdown |  | ¨ | 0 | ¨ | ¨
Total Designed Watts UNCONDITIONED SPACES: | [7 empty] | 0
¹ FOOTNOTE: Design Watts for small aperture and color changing luminaires which qualify per §140.6(a)4B/§170.2(e)2D is adjusted to be 75%/80% of their rated wattage. Table F automatically makes this adjustment, the permit applicant should enter full rated wattage in column 05.
2 Authority Having Jurisdiction may ask for Luminaire cut sheets to confirm wattage used for compliance per §130.0(c)/§160.5(b). Wattage used must be the maximum rated for the luminaire, not the lamp.
How Wattage is Determined
IF column03 = Track: column06 = "See Table G" ELSE: column06 = enum("NA8 Default", Mfr. Spec¹, Other, "JA8 Lamp")
Wattage Dropdown
NA8 Default
Mfr Spec1
Other
JA8
Add Row
Remove Last
Reset
Add Row
Remove Last
Reset
Note on A5: Benjamin Park: this Conditioned part shows up if Area is entered for "Conditioned Spaces" in Table B. Same for Unconditioned Areas.
Note on A9: Benjamin Park: if the user changes the fixture name, dropdown list for "luminaire name or item tag" in Table J, K, N, O, P, Q, and R should be updated if exists. Same for Unconditioned Areas.
Note on C9: Benjamin Park: if this box is checked, Table G will be triggered. If this box is unchecked, the fixture in this row will be removed from Table G. If this fixture was the only fixture in Table G, Table G will be removed. Same for Unconditioned Areas.
Note on E9: Benjamin Park: If F03 Track is checked, G05 Track Wattage will be pulled. If the user changes this field, Watts per luminaire in Table J, K, N, O, P, Q, and R should be updated. Same for Unconditioned Areas
Note on L9: Benjamin Park: if this box is checked by the user, column 08 for this row should say "exempt" and not be included in the total. Same for Unconditioned Areas.
Note on D16: 8.19.21: If this is checked in either Conditioned or Unconditioned Space, the Design Watts for that luminaire in column 09 should be multiplied by 0.75. 10.11.21- APPLIES TO BOTH CONDITIONED AND UNCONDITIONED This changed to a dropdown because the value for NR and MF are not consistent. Dropdown choices should be: - "Used in Nonres occupancy" - "Used in multifamily occupancy" - "NA" If "NR occupancy" chosen, Design Watts in column 09 should be multiplied by 0.80. If "Multifamily occupancy" chosen, Design Watts in col09 should be multiplied by 0.75.

## G. Modular Lighting Systems
| User input | auto calculated |  |  |  | From another Table |  |  |  | From look up table
G. MODULAR LIGHTING SYSTEMS
This table calculates wattage for modular lighting systems/ track lighting fixtures indicated on Table F and transfers the wattage to Table F.
01 | 02 | 03 | [15 empty] | 04
Name or Item Tag | Complete Track Description | Calculation Method per §130.0(c)6 | [15 empty] | Track Wattage
autofill from Table F | autofill from Table F | ¨ | i | Installed Luminaires vs Default 30 W/ft | ¨ | ii | Current Limiter 1 |  |  | ¨ | iii | Overcurrent Protection Panel2 |  | ¨ | iv | Power supplied by driver, power supply or transformer1
This shows up if Method (i) is selected above>>> |  | Number of luminaires in system |  |  | x | Rated Watts per luminaire |  | = | Total Watts |  | OR | Linear ft of track or busway | x | Default W/LF |  | = | Total Watts | 0
[9 empty] | 0 |  |  |  |  | 30 |  |  | 0
This shows up if Method (ii) is selected above>>> |  | VA of current limiter | [15 empty] | 0
This shows up if Method (iii) is selected above>>> |  | Voltage of branch circuit | [8 empty] | x | Sum of Ampere ratings for all devices on panel | [5 empty] | 0
This shows up if Method (iv) is selected above>>> |  | Maximum rated input wattage per manufacturer | [15 empty] | 0
1 FOOTNOTE: For power-over-Ethernet lighting systems, power provided to installed non-lighting devices may be subtracted from the total power rating of the power-over-Ethernet system.
Once the track wattage is calculated in Table G, that value autofills the track "watts per luminaire" in Table F. The Table G options will have to be repeated for each track fixture type user input in Table F.

## H. Lighting Control
| User input |  |  | auto calculated |  | From another Table |  |  | From look up table
H. INDOOR LIGHTING CONTROLS (Not Including PAFs)
This table includes lighting controls for conditioned and unconditioned spaces. When a control having a * is shown, the notes section of this table provides more detail on how compliance is achieved. The lighting controls section of the Compliance Summary Table on the first page will show "DOES NOT COMPLY" if the notes are left blank. |  |  | Building Level Controls
|  |  | 01 |  |  |  |  | 02 |  |  |  |  | 03
|  |  | Mandatory Demand Response |  |  |  |  | Shut-off Controls |  |  |  |  | Field Inspector
|  |  | §110.12(c) |  |  |  |  | §130.1(c)/§160.5(b)4C |  |  |  |  | Pass | Fail
|  |  | See dropdown |  |  |  |  | See Dropdown |  |  |  |  | ¨ | ¨
Area Level Controls
04 | 05 | 06 |  |  | 07 |  | 08 |  |  | 09 | 10 | 11 | 12
Area Description | Complete Building or Area Category Primary Function Area | Manual Area Controls §130.1(a)/§160.5(b)4A |  |  | Multi-Level Controls §130.1(b)/§160.5(b)4B |  | Shut-Off Controls §130.1(c)/§160.5(b)4C |  |  | Primary/Skylit Daylighting | Secondary Daylighting | Interlocked Systems | Field Inspector
[10 empty] | §130.1(d)/§160.5(b)4D | §140.6(d) §130.1(d)/§160.5(b)4D | §140.6(a)1/§170.2(e)2A | Pass | Fail
| This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) | See Dropdown |  |  | See dropdown |  | See dropdown |  |  | See dropdown | See dropdown | ¨ | ¨ | ¨
* NOTES: Controls with a * require a note in the space below explaining how compliance is achieved. | [9 empty] | 13
EX: Conference 1: Primary/Skylit Daylighting: Exempt because less than 120 watts general lighting; EXCEPTION 1 to §130.1(d)2 | [9 empty] | Plan Sheet Showing Daylit Zones:
If user selects anything in the row for the space with a *, the Space Name (uneditable) should show up in Notes section. If they unselect the *, the space name should dissapear.
Text from this box should show up in the D. Exceptional Conditions box & the Controls Compliance in Table C. should say "Complies with Exceptional Conditions".
If a selection marked with * is made but the user does not input text into this box, the Controls Compliance in Table C. should say "DOES NOT COMPLY".
If the user does not select any * control but does complete at least 1 line on this table, Controls Compliance in Table C. should say "COMPLIES"
|  |  | Demand Response Dropdown |  |  |  |  | Shut-Off Controls (at Bldg)
|  |  | Required: >= 4,000W subject to multilevel for general lighting > 10,000SF |  |  |  |  | Whole Building Timeswitch
|  |  | Required: Using as PAF (Table P) |  |  |  |  | EMCS Whole Building "Other"*
|  |  | NA: <4,000W subject to multilevel Not Required < 10,000SF |  |  |  |  | See Area/ Space Level Controls
NA: per H&LS Not Required- Installing as PAF
NA: Licensed Healthcare Not Required- Building NA: Space <= 0.5 W/SF
NA: <= 80% LP (alt only)
|  | Area Dropdown |  |  | Multi-Level Dropdown |  | Shutoff Dropdown |  |  | Primary Daylight | Secondary Daylight
|  | Manual ON/OFF Readily Accessible |  |  | Dimmer |  | Occ. Sensor |  |  | Included | Included
|  | Auth. Personnel |  |  | Multilevel Bi-level switch |  | See Bldg Lvl |  |  | Exempt* | Exempt*
|  | Aunniciated* |  |  | NA: <= 80% LP (alt only) |  | Partial Off 130.1(c)/ 160.5(b)4C * |  |  | NA: <= 80% LP (alt only) | NA: <= 80% LP (alt only)
|  | Exempt* |  |  | Exempt* |  | Partial On 130.1(c)/160.5(b)4C * |  |  | NA: Rm < 24sf glazing | NA: Rm < 24sf glazing
|  | Other* |  |  | Other* |  | Vacancy |  |  | NA: Garage < 36sf opening | NA: Garage < 36sf opening
[5 empty] | NA: General Ltg <= 0.5 W/SF |  | Autotimeswitch |  |  | NA: Skylight shaded | NA: Skylight shaded
[5 empty] | NA: Enclosed area < 100sf |  | EMCS |  |  | NA: Overhang | NA: Overhang
[5 empty] | NA: Enclosed area w/ 1 inseparable SSL luminaire |  | Exempt* |  |  | NA: General Ltg < 120W | NA: General Ltg < 120W
[5 empty] | NA: Enclosed area w/ 1 luminaire <= 2 lamps |  | Other* |  |  | NA: Garage General Ltg < 60W | NA: Garage General Ltg < 60W
[5 empty] | NA: Restrooms |  | Countdown timer |  |  | NA: Garage daylight adaption zone | NA: Garage daylight adaption zone
[5 empty] | NA: Licensed Healthcare |  | NA: Licensed Healthcare |  |  | NA: Sidelit retail sales area | NA: Sidelit retail sales area
NA: Elec. equip. rm
NA: 24 hour/365 day
Add Row
Remove Last
Reset
Note on M8: Benjamin Park: if the user choose "See Area Level Controls" and all column 08 are any of the "NA" choices, "Exempt *" or "Other *", NRCA-LTI-02-E changes to "No."
Note on B14: 8.19.21: Please see new tables in Table I. If both "Area Category" and "Complete Building" have been chosen on Table B, List needs to combine just like in 2019.
Note on O14: "if all column 09 and 10 are any of the "NA" choices,"Exempt*" or "Other *", NRCA-LTI-03-A changes to "No."
Note on W14: Benjamin Park: if user checks the box, NRCA-LTI-04-E changes to "Yes"
Note on A17: 8.19.21: Getting rid of *Notes feature
Note on D24: 7.15.21: if the user choose "Required: ≥4,000 watts subject to multilevel" "Required > 10,000 SF" OR "Required: Using as PAF (Table P) "Not Required - Installing as PAF", NRCA-LTI-04-A chnages to "Yes"
Note on M25: 8.19.21: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on D29: Usability Update: If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 <= Table C column 05*0.8 then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on F35: 3/21/2022 If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 >= Table C column 05*0.8 then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R..
Note on O35: 3/21/2022 If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 >= Table C column 05*0.8 then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on S35: 3/21/2022 If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 >= Table C column 05*0.8 then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.

## I. Power Allowance
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
I. LIGHTING POWER ALLOWANCE: COMPLETE BUILDING OR AREA CATEGORY METHODS
Each area complying using the Complete Building or Area Category Methods per §140.6(b) are included in this table. Column 06 indicates if additional lighting power allowances per §140.6(c) or adjustments per §140.6(a) are being used.
Conditioned Spaces
01 |  |  | 02 | 03 | 04 | 05 | 06
Area Description |  |  | Complete Building or Area Category Primary Function Area | Allowed Density (W/ft2) | Area (ft²) | Allowed Wattage (watts) | Additional Allowance/ Adjustment
[7 empty] | Area Category | PAF
|  |  | This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) | From Table below |  | calculated as LPD x 04 (LPD is determined based on 02 selection) | Triggers Table J | Triggers Table P
|  |  |  | TOTALS: | 0 | 0 | See Tables J or P for detail
[7 empty] | Duplicate Row | Add Row
Unconditioned Spaces
01 |  |  | 02 | 03 | 04 | 05 | 06
Area Description |  |  | Complete Building or Area Category Primary Function Area | Allowed Density (W/ft2) | Area (ft²) | Allowed Wattage (watts) | Additional Allowance/ Adjustment
[7 empty] | Area Category | PAF
|  |  | This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) | From Table below |  | calculated as LPD x 04 (LPD is determined based on 02 selection) | Triggers Table J | Triggers Table P
|  |  |  | TOTALS: | 0 | 0 | See Tables J or P for detail
[7 empty] | Duplicate Row | Add Row |  |  | This table is for NONRESIDENTIAL | This table is for MF COMMON AREAS
2022 15 day language, confirm when adopted:
|  | Complete Building or Area Category Primary Function Area Dropdown List |  |  |  | LPD
|  | if(Calculation Method in Table B = "Complete Building"): |  |  |  | if (Calculation Method in Table B = "Complete Building"):
|  | Assembly Building |  |  |  | 0.70 0.65
|  | "Financial Center Building" |  |  |  | 0.65
|  | "Grocery Store Building" |  |  |  | 0.95 0.90
|  | Gymnasium Building |  |  |  | 0.65 0.60
|  | Healthcare Facility |  |  |  | 0.90
|  | Industrial Manufacturing Building |  |  |  | 0.60
|  | "Library Building" |  |  |  | 0.70
|  | Motion Picture Theater Building |  |  |  | 0.70 0.60
|  | Museum Building |  |  |  | 0.65
|  | "Office Building" |  |  |  | 0.65 0.60 | [6 empty] | <<< different than NR
|  | "Parking Garage Building" |  |  |  | 0.13 | [6 empty] | <<< different than NR
|  | Performing Arts Theater Building |  |  |  | 0.80 0.75
|  | "Religious Facility Building" |  |  |  | 0.70
|  | "Restaurant Building" |  |  |  | 0.70 0.65
|  | Retail Store Building |  |  |  | 0.90
|  | "School Building" |  |  |  | 0.65 0.60
|  | Sports Area Building |  |  |  | 0.75
|  | "All Other Building" |  |  |  | 0.40
else if (Calculation Method in Table B = "Area Category" or Calculation Method in Table B = "Area Category + Tailored"):
|  | Audience Seating Area |  |  |  | 0.60 0.50
|  | "Auditorium" |  |  |  | 0.70
|  | "Auto Repair" |  |  |  | 0.55 | [6 empty] | << Different than NR
|  | "Barber/Beauty Salon/Spa" |  |  |  | 0.80 0.70
|  | "Civic Meeting Place" |  |  |  | 1.00 0.90 | [6 empty] | << Different than NR
|  | "Classroom, Lecture, Training, Vocational" |  |  |  | 0.70 0.60
|  | Concourse and Atria Area |  |  |  | 0.60
|  | "Convention, Conference, Multipurpose, and Meeting Center" |  |  |  | 0.85 0.75
|  | "Commercial and Industrial Storage-Shipping" |  |  |  | 0.60
|  | Commercial and Industrial Warehouse |  |  |  | 0.45 0.40
|  | Copy Room |  |  |  | 0.50
|  | Corridor |  |  |  | 0.60 0.40
|  | Corridor (Low Vision) |  |  |  | 0.80 0.70
|  | Dining- Family |  |  |  | 0.50 0.40
|  | Dining- Fast Food |  |  |  | 0.40 0.45
|  | Dining- Bar/Fine |  |  |  | 0.55 0.45
|  | Dining (Low Vision) |  |  |  | 0.80
|  | "Electrical, Mechanical, Telephone Rooms" |  |  |  | 0.40
|  | "Exercise Center, Gymnasium" |  |  |  | 0.50
|  | "Exhibit, Museum" |  |  |  | 0.60
|  | "Financial Transaction" |  |  |  | 0.80 0.70
|  | "General Commercial and Industrial Work - Low Bay" |  |  |  | 0.60
|  | "General Commercial and Industrial Work - High Bay" |  |  |  | 0.65
|  | "General Commercial and Industrial Work - Precision" |  |  |  | 0.85
|  | "Grocery Sales" |  |  |  | 1.05 1.00
|  | Hospital- Exam/Treatment |  |  |  | 1.15
|  | Hospital- Imaging |  |  |  | 1.0 0.60
|  | Hospital- Med Supply |  |  |  | 0.55
|  | Hospital- Nursery |  |  |  | 0.95 0.80
|  | Hospital- Nurse Station |  |  |  | 0.75 0.85
|  | Hospital- Operating Rm |  |  |  | 1.90
|  | Hospital- Patient Rm |  |  |  | 0.55 0.70
|  | Hospital- Physical Therapy |  |  |  | 0.85 0.75
|  | Hotpital- Recovery |  |  |  | 0.90
|  | "Hotel Function" |  |  |  | 0.85
|  | "Kitchen, Food Preparation" |  |  |  | 0.95 | [6 empty] | << Different than NR
|  | "Laboratory Area, Scientific" |  |  |  | 1.0 0.90
|  | "Laundry" |  |  |  | 0.45
|  | "Library - Reading Area" |  |  |  | 0.80
|  | "Library - Stack Area" |  |  |  | 1.10 1.00 | [6 empty] | << Different than NR
|  | "Main Entry Lobby" |  |  |  | 0.85 0.70 | [6 empty] | << Different than NR
|  | Main Entry Lobby (Low Vision) |  |  |  | 0.85 | [6 empty] | << Different than NR
|  | Multipurpose Rm (Low Vision) |  |  |  | 0.95 0.85
|  | "Locker/Dressing Room" |  |  |  | 0.45
|  | "Lounge" |  |  |  | 0.65 0.55
|  | Lounge/ Waiting (Low Vision) |  |  |  | 0.75 0.80
|  | "Malls and Atria" |  |  |  | 0.90
|  | Museum Restoration |  |  |  | 0.75 0.70
|  | "Office (> 250 square feet)" |  |  |  | 0.65 0.60
|  | "Office (<= 250 square feet)" |  |  |  | 0.70 0.65
|  | Office (open) |  |  |  | 0.60
|  | "Parking Garage - Parking Area & Ramps" |  |  |  | 0.10
|  | "Parking Garage - Dedicated Ramps" |  |  |  | 0.25
|  | "Parking Garage - Daylight Adaption Zones" |  |  |  | 0.50 1.00
|  | Pharmacy |  |  |  | 1.10 1.00
|  | "Religious Worship" |  |  |  | 0.95
|  | Religious Worship (Low Vision) |  |  |  | 1.0
|  | Restroom |  |  |  | 0.65
|  | Restroom (Low Vision) |  |  |  | 0.80 1.0
|  | Retail Fitting Rm |  |  |  | 0.60
|  | "Retail Merchandise Sales, Wholesale Showroom" |  |  |  | 1.0 0.95
|  | Sports Arena- Class I |  |  |  | 2.25
|  | Sports Arena- Class II |  |  |  | 1.45
|  | Sports Arena- Class III |  |  |  | 1.10
|  | Sports Arena- Class IV |  |  |  | 0.75
|  | Stairwell |  |  |  | 0.50 0.60
|  | Stairwell (Low Vision) |  |  |  | 0.80
|  | Storage- MF common areas |  |  |  | 0.45
|  | "Theater - Motion Picture" |  |  |  | 0.60 0.50
|  | "Theater - Performance" |  |  |  | 1.0 0.80
|  | "Transportation - Concourse & Baggage" |  |  |  | 0.40
|  | "Transportation - Ticketing" |  |  |  | 0.45
|  | "Videoconferencing Studio" |  |  |  | 0.90
|  | "All Other Space Types" |  |  |  | 0.40
Note on D20: 7.20.21: Updated table per 140.6-B & 140.6-C
Reset
Add Row
Remove Last
Reset
Add Row
Remove Last

## K. Tailored Method
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
K. TAILORED METHOD GENERAL LIGHTING POWER ALLOWANCE
This table includes areas using the Tailored Method per §140.6(c)3/§170.2(e)4B. If additional Tailored Method "use it or lose it" allowances are used it is also indicated. Lighting that qualifies for one of the additional allowances shall not qualify for another additional allowance.
Conditioned Spaces
General Lighting Power Allowance | Additional "Use it or lose it" Allowances |  |  |  | 01
| ¨ Wall Display Lighting | ¨ Floor Display & Task Lighting | ¨ Ornamental Decorative & Special Effects | ¨ Very Valuable Merchandise | Total Allowed Watts using Tailored Method
Table K (below) | Table L | Table M | Table N | Table O | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Calculated General Lighting Power Allowance
02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Primary Function Area per Table 140.6-D/ 170.2-N |  | Illuminance Value (LUX) | Room Configuration | Allowed Density (W/ft²) | Area (ft²) | Extra Allowance (Watts) | Power Adjustment (See Table P)
| dropdown |  | autofilled by 03 dropdown |  | This value will be determined based on illuminance value and room cavity ratio |  | #VALUE! | ¨ PAF
These rows show up if Room Configuration is selected above>>> | IF column 05 = Rectangular: "Room Length (ft)" ELSE IF column 05 = Non-Rectangular: "Not Applicable" | IF column 05 = Rectangular: "Room Width (ft)" ELSE IF column 05 = Non-Rectangular: "Perimeter (ft)" | Room Height (ft) | Room Cavity Ratio (RCR)
IF 05="Rectangular" RCR = (5*Height*(Length+Width))/(Length*Width) ELSE: RCR = 2.5*Height*Width/07
Total General Power Allowance (Watts) CONDITIONED SPACES: | [6 empty] | #VALUE!
Unconditioned Spaces
General Lighting Power Allowance | Additional "Use it or lose it" Allowances |  |  |  | 01
| ¨ Wall Display Lighting | ¨ Floor Display & Task Lighting | ¨ Ornamental Decorative & Special Effects | ¨ Very Valuable Merchandise | Total Allowed Watts using Tailored Method
Table L (below) | Table L | Table M | Table N | Table O | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Calculated General Lighting Power Allowance
02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Primary Function Area per Table 140.6-D/ 170.2-N |  | Illuminance Value (LUX) | Room Configuration | Allowed Density (W/ft²) | Area (ft²) | Extra Allowance (Watts) | Power Adjustment (See Table P)
| dropdown |  | autofilled by 03 dropdown |  | This value will be determined based on illuminance value and room cavity ratio |  | #VALUE! | ¨ PAF
These rows show up if Room Configuration is selected above>>> | IF column 05 = Rectangular: "Room Length (ft)" ELSE IF column 05 = Non-Rectangular: "Not Applicable" | IF column 05 = Rectangular: "Room Width (ft)" ELSE IF column 05 = Non-Rectangular: "Perimeter (ft)" | Room Height (ft) | Room Cavity Ratio (RCR)
IF 05="Rectangular" RCR = (5*Height*(Length+Width))/(Length*Width) ELSE: RCR = 2.5*Height*Width/07
Total General Power Allowance (Watts) UNCONDITIONED SPACES: | [6 empty] | #VALUE!
This is for NONRESIDENTIAL
This table is for NONRESIDENTIAL
dropdown
Auditorium Area
Convention Area
Conference Area
Multifamily Conference Area
Multipurpose Area
Multifamily Multipurpose Area
Meeting Center Area
Multifamily Meeting Center Area
Dining Areas
Multifamily Dining Areas
Exhibit, Museum Areas
Hotel Ballroom/ Events
Hotel Lobby
Main Entry Lobby
Multifamily Main Entry Lobby
Religious Worship Area
Retail Sales - Grocery
Retail Merchandise Sales
Showroom Area
Motion Picture Theater
Performance Theater
This table is for MF COMMON AREAS
This table is for MF COMMON AREAS
Add Row
Remove Last
Add Row
Remove Last
Note on B6: Sally Blair: Checking these boxes triggers the associated table.
Note on D13: 10.11.21: if L03 = "Auditorium Area": lux = 300; if L03 = "Convention Area": lux = 300; if L03 = "Conference Area": lux = 300; if L03 = "MF Conference Area": lux = 300; if L03 = "Multipurpose Area": lux = 300; if L03 = "MF Multipurpose Area": lux = 300; if L03 = "Meeting Center Area": lux = 300; if L03 = "MF Meeting Center Area": lux = 300; if L03 = "Dining Areas": lux = 200; if L03 = "MF Dining Areas": lux = 200; if L03 = "Exhibit, Museum Areas": lux = 150; if L03 = "Hotel Ballroom/Events": lux = 400; if L03 = "Hotel Lobby": lux = 200; if L03 = "Main Entry Lobby": lux = 200; if L03 = "MF Main Entry Lobby": lux = 200; if L03 = "Religious Worship Area": lux = 300; if L03 = "Retail Sales - Grocery": lux = 600; if L03 = "Retail Merchandise Sales": lux = 500 if L03 = "Showroom Area": lux = 500; if L03 = "Motion Picture Theater": lux = 200; if L03 = "Performance Theater": lux = 200;
Note on F13: 7.20.21 if L04 = 150: if (rcr <= 2.0) { lpd = 0.35 0.40; } else if (rcr <= 3.5) { lpd = 0.40 0.45; } else if (rcr <=7.0) { lpd = 0.50 0.60; } else if (rcr > 7.0) { lpd = 0.65 0.75; } else if L04 = 200: if (rcr <= 2.0) { lpd = 0.40 0.45; } else if (rcr <= 3.5) { lpd = 0.50 0.55; } else if (rcr <=7.0) { lpd = 0.65 0.75; } else if (rcr > 7.0) { lpd = 0.85 1.00; } else if L04 = 300: if (rcr <= 2.0) { lpd = 0.55 0.65; } else if (rcr <= 3.5) { lpd = 0.70 0.80; } else if (rcr <=7.0) { lpd = 0.85 1.00; } else if (rcr > 7.0) { lpd = 1.20 1.40; } else if L04 = 400: if (rcr <= 2.0) { lpd = 0.65 0.78; } else if (rcr <= 3.5) { lpd = 0.80 0.98; } else if (rcr <=7.0) { lpd = 1.05 1.34; } else if (rcr > 7.0) { lpd = 1.25 2.08; } else if L04 = 500: if (rcr <= 2.0) { lpd = 0.80 0.90; } else if (rcr <= 3.5) { lpd = 0.90 1.05; } else if (rcr <=7.0) { lpd = 1.25 1.45; } else if (rcr > 7.0) { lpd = 1.55 1.85; } else if L04 = 600: if (rcr <= 2.0) { lpd = 0.90 1.08; } else if (rcr <= 3.5) { lpd = 1.05 1.24; } else if (rcr <=7.0) { lpd = 1.40 1.64; } else if (rcr > 7.0) { lpd = 2.00 2.38; }
Note on I13: Sally Blair: Triggers Table P
Note on B19: Sally Blair: Checking these boxes triggers the associated table.
Note on D26: 10.11.21: if L03 = "Auditorium Area": lux = 300; if L03 = "Convention Area": lux = 300; if L03 = "Conference Area": lux = 300; if L03 = "MF Conference Area": lux = 300; if L03 = "Multipurpose Area": lux = 300; if L03 = "MF Multipurpose Area": lux = 300; if L03 = "Meeting Center Area": lux = 300; if L03 = "MF Meeting Center Area": lux = 300; if L03 = "Dining Areas": lux = 200; if L03 = "MF Dining Areas": lux = 200; if L03 = "Exhibit, Museum Areas": lux = 150; if L03 = "Hotel Ballroom/Events": lux = 400; if L03 = "Hotel Lobby": lux = 200; if L03 = "Main Entry Lobby": lux = 200; if L03 = "MF Main Entry Lobby": lux = 200; if L03 = "Religious Worship Area": lux = 300; if L03 = "Retail Sales - Grocery": lux = 600; if L03 = "Retail Merchandise Sales": lux = 500 if L03 = "Showroom Area": lux = 500; if L03 = "Motion Picture Theater": lux = 200; if L03 = "Performance Theater": lux = 200;
Note on I26: Sally Blair: Triggers Table P
Note on B38: 10.11.21: Added MF options to accommodate changes in Tables L and M

## J. ACM Qualifying System
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
J. ADDITIONAL LIGHTING ALLOWANCE: AREA CATEGORY METHOD QUALIFYING LIGHTING SYSTEM
All areas indicated in Table I as using an additional allowance using the Area Category Method have been included in this table to calculate the additional allowance per Table140.6-C /170.2-M.
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Area Description | Primary Function Area | Applicable Qualifying Lighting System from Table 140.6-C | Allowed Density (W/ft²) or (W/lf) | Ltg Area, Length or ATM/ Mirror (ft², lf or #) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Total Design Watts
Auto fills from Tbl I. | Auto fills from Tbl I. | Dropdown (See below). Customize based on Function Area in 02 | autofilled by dropdown (see below for values) |  | calculated as 04x05 | drop down from Table F | Autofill from Table F based on 07 |  | calculated as 08x09
Total Design Watts: | Calculated Allowance (Watts): | Total Additional Allowance for this area:
sum of column 10 for space | sum of column 06 for space | autofill Total Design Watts or Calculated Allowance, whichever is less
11
Total Additional Allowance (Watts) CONDITIONED SPACES: |  | sum of Total Additional Allowance for whole table
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Area Description | Primary Function Area | Applicable Qualifying Lighting System from Table 140.6-C | Allowed Density (W/ft²) or (W/lf) | Ltg Area, Length or ATM/ Mirror (ft², lf or #) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Total Design Watts
Auto fills from Tbl I. | Auto fills from Tbl I. | Dropdown (See below). Customize based on Function Area in 02 | autofilled by dropdown (see below for values) |  | calculated as 04x05 | drop down from Table F | Autofill from Table F based on 07 |  | calculated as 08x09
Total Design Watts: | Calculated Allowance (Watts): | Total Additional Allowance for this area:
sum of column 10 for space | sum of column 06 for space | autofill Total Design Watts or Calculated Allowance, whichever is less
11
Total Additional Allowance (Watts) UNCONDITIONED SPACES: |  | sum of Total Additional Allowance for whole table
Add Footnote button to show up IF the primary function area is either "Retail Merchandise Sales, Wholesale Showroom" OR "Grocery Sales".
Pressing this button essentially duplicates the space in this table (but leaves columns 03-10 uncompleted for user to complete)- see pic below.
Allowed Density For Column 04 Autofill
Decorative Accent/ Display A | 0.15 0.20 (if "Exhibit, Museum" in 02 then 0.50)
Decorative/ Display B | 0.2
Decorative/ Display C | 0.25
Decorative/ Display D | 0.3
Decorative/ Display E | 0.35
Decorative/ Display F | 0.45
Ornamental | 0.30
Detailed Task A | 0.20
Detailed Task B | 0.3
Detailed Task C | 0.35
Chalk/ Whiteboard | 7 4.5 | 03 Dropdown
Precision Work | 0.70 | Accent/ Display Decorative/ Display F
Portable Office | 0.20 | Ornamental
ATM/ Ticket Machine | see note for column 06
Specialized Task | 0.35 | 03 Dropdown
Decorative | 0.15 | Detailed Task A
Mirror- Externally Lit | 40
Mirror- Internally Lit | 120 | 03 Dropdown
Tunable White | 0.10 | Ornamental Decorative/ Display C
Videoconferencing | 1.0
Transition OFF | 0.95 | 03 Dropdown
Detailed Task B
Ornamental Decorative/ Display C
03 Dropdown
Chalk/ Whiteboard
03 Dropdown
Accent/ Display Decorative/ Display B
03 Dropdown
Precision Work
03 Dropdown
Portable Office
Decorative/ Display B
03 Dropdown
ATM/ Ticket machine
03 Dropdown
Specialized Task
03 Dropdown
Accent/ Display Decorative/ Display E
Decorative
03 Dropdown
Mirror- Externally Lit
Mirror- Internally Lit
03 Dropdown
Tunable White
03 Dropdown
Tunable White
Decorative/ Display B
03 Dropdown
Tunable White
Decorative Decorative/ Display A
03 Dropdown
Videoconferencing
03 Dropdown
Ornamental Decorative/ Display D
Transition OFF
Tunable White
03 Dropdown
Decorative Decorative/ Display D
03 Dropdown
Tunable White
Detailed Task A
03 Dropdown
Detailed Task C
03 Dropdown
Tunable White
Decorative/ Display D
Add System
Add Luminaire
Remove Last
Add System
Add Luminaire
Remove Last
Note on G8: 2019 Update: if J03 is "ATM/ Ticket Machine", calculated as 100 + ((J05 - 1) * 50). else, calculated as 04 x 05. Same for Unconditioned Spaces.
Note on D37: 7.20.21: If column 02 is "Auditorium"; "Exhibit, Museum"
Note on D41: 7.20.21: If column 02 is "Auto Repair"; "Electrical, Mechanical, Telephone Rooms"; "General Commercial and Industrial Work- High Bay"; "General Commercial and Industrial Work- Low Bay"; "Museum Restoration";
Note on D44: 7.20.21 If column 02 is "Audience Seating Area"; "Civic Meeting Place"; "Malls Concourse & Atria"; "Convention, Conference, Multipurpose, and Meeting Center"; Corridor; "Dining- Fast Food"; "Dining- Family"; "Financial Transaction"; "Hotel Function"; "Library- Reading Area"; "Main Entry Lobby"; "Lounge"; "Religious Worship"; "Theater- Motion Picture"; "Theater- Performance"; "Dining- Bar/Fine"; "Lounge/Waiting (Low Vision)"; "Multipurpose Rm (Low Vision)"; "Religious Worship (Low Vision)"; "Dining (Low Vision)"
Note on D47: 2019 Update: If column 02 is "Beauty Salon"
Note on D51: 2019 Update: If column 02 is "Classroom, Lecture, Training, Vocational"
Note on D54: 7.20.21: If column 02 is "Exhibit, Museum"; "Transportation- Ticketing"; "Restroom (Low Vision)"
Note on D57: 2019 Update: If column 02 is "General Commercial and Industrial Work- Precision"
Note on D60: 2019 Update: If column 02 is "Office (> 250 square feet)"; "Office (<= 250 square feet)"; "Office (open)"
Note on D64: 7.20.21: If column 02 is " Parking Garage - Parking Area & Ramps"
Note on D67: 2019 Update: If column 02 is "Laboratory Area, Scientific"; "Pharmacy";
Note on D70: 7.20.21: If column 02 is "Grocery Sales"; "Retail Merchandise Sales, Wholesale Showroom"; "Restroom"; "Dining- Bar/Fine"; "Stairwell"
Note on D74: 2019 Update: If column 02 is "Retail- Fitting Rm"
Note on D78: 7.20.21: If column 02 is "Hospital- Nursery"; "Hospital- Nurse Station"; "Hospital- Physical Therapy"; "Hospital- Recovery"
Note on D81: 7.20.21: If column 02 is "Hospital- Imaging"
Note on D85: 2019 Update: If column 02 is "Hospital- Patient Rm"
Note on D89: 2019 Update: If column 02 is "Videoconferencing Studio"
Note on D92: 2019 Update: If column 02 is "Main Entry Lobby (Low Vision)"
Note on D97: 7.20.21: If column 02 is "Corridor (Low Vision)"; "Stairwell (Low Vision)"
Note on D100: 7.20.21: If column 02 is "Hospital- Nurse Station"
Note on D104: 7.20.21: If column 02 is "Museum Restoration"
Note on D107: 7.20.21: If column 02 is "Dining (Low Vision)"; "Lounge/Waiting (Low Vision)"; "Multipurpose Rm (Low Vision)"; "Religious Worship (Low Vision)";

## L. Tailored Wall Display
| User input |  | auto calculated |  | From another Table |  |  | From look up table
L. ADDITIONAL LIGHTING ALLOWANCE: TAILORED WALL DISPLAY
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Wall Display Length (lf) | Wall Display Density (W/lf) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F |  | i | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Wall Display Length (lf) | Wall Display Density (W/lf) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F |  | if (col06 == "≥ 16 feet"): "0.77"; else if (col06 == "12 to 16 feet"): "0.87"; else: "1"; | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
This table is for NONRESIDENTIAL
This table is for MF COMMON AREAS
This table is for MF COMMON AREAS
^^^
Lobby value not same as NR
Add Row
Remove Last
Add Row
Remove Last
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Remove Last
Note on C8: 10.11.21 if L03 = "Auditorium Area": = 3.00; if L03 = "Convention Area": = 2.00; if L03 = "Conference Area": = 2.00; if L03 = "MF Conference Area": = 2.00; if L03 = "Multipurpose Area": = 2.00; if L03 = "MF Multipurpose Area": = 2.00; if L03 = "Meeting Center Area": = 2.00; if L03 = "MF Meeting Center Area": = 2.00; if L03 = "Dining Areas": = 1.25; if L03 = "MF Dining Areas": = 1.25; if L03 = "Exhibit, Museum Areas": = 11.20 11.5 if L03 = "Hotel BAllroom/Events": = 1.80; if L03 = "Lobby": = 3.40 3.50; if L03 = "Main Entry Lobby": = 3.40 3.50; if L03 = "Main Entry Lobby": = 3.50; if L03 = "Religious Worship Area": = 1.30; if L03 = "Retail Sales - Grocery": = 6.60 6.80; if L03 = "Retail Merchandise Sales":= 11.50 11.80 if L03 = "Showroom Area": = 11.50 11.80; if L03 = "Motion Picture Theater": = 2.00; if L03 = "Performance Theater": = 7.30 7.50;
Note on G8: Rebecca Rice: 2019: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70
Note on K8: 01/11/21 L.11 = The smaller of: L.10 or (The following equation should be expanded depending on the # of luminaires per area. The example below is for three luminaires in one area.) (L.04 + (Fixture1DesignWatts(1-MHFactor1)) + (Fixture2DesignWatts(1-MHFactor2)) + (Fixture3Watts(1-MHFactor3)))....
Note on G16: Rebecca Rice: 2019: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70
Note on K17: 01/11/21 L.11 =The smaller of: L.10 or (The following equation should be expanded depending on the # of luminaires per area. The example below is for three luminaires in one area.) (L.04 + (Fixture1DesignWatts(1-MHFactor1)) + (Fixture2DesignWatts(1-MHFactor2)) + (Fixture3Watts(1-MHFactor3)))...

## M. Tailored Task Lighting
| User input |  | auto calculated |  | From another Table |  |  | From look up table
M. ADDITIONAL LIGHTING ALLOWANCE: TAILORED FLOOR AND TASK LIGHTING
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | See dropdown |  | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | See dropdown |  | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Mounting Height Dropdown
< 10'7"
10'7"-14'
> 14' - 18'
> 18'
This table is for NONRES
This table is for MF COMMON AREAS
^^None of these are same as NR
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Remove Last
Remove Last
Note on C8: 10.11.21 if L03 = "Auditorium Area": = 0.20 if L03 = "Convention Area": = 0.30 0.35; if L03 = "Conference Area": = 0.30 0.35; if L03 = "MF Conference Area": = 0.25; if L03 = "Multipurpose Area": = 0.30 0.35; if L03 = "MF Multipurpose Area": = 0.25; if L03 = "Meeting Center Area": = 0.30 0.35; if L03 = "MF Meeting Center Area": = 0.25; if L03 = "Dining Areas": = 0.45 0.50; if L03 = "MF Dining Areas": = 0.25; if L03 = "Exhibit, Museum Areas": = 0.70 0.80 if L03 = "Hotel BAllroom/Events": = 0.12; if L03 = "Lobby": = 0.20; if L03 = "Main Entry Lobby": = 0.20; if L03 = "MF Main Entry Lobby": = 0.25; if L03 = "Religious Worship Area": = 0.40; if L03 = "Retail Sales - Grocery": = 0.60 0.70; if L03 = "Retail Merchandise Sales": = 0.70 0.80 if L03 = "Showroom Area": = 0.70 0.80; if L03 = "Motion Picture Theater": = 0.20; if L03 = "Performance Theater": = 0.20;
Note on G8: Rebecca Rice: 2019 Updates: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70
Note on K8: 01/11/21 M.11 = The smaller of: M.10 OR (The following equation should be expanded depending on the # of luminaires per area. The example below is for three luminaires in one area.) (M.04 + (Fixture1DesignWatts(1-MHFactor1)) + (Fixture2DesignWatts(1-MHFactor2)) + (Fixture3Watts(1-MHFactor3)))....
Note on G17: Sally Blair: 2019 Updates: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70
Note on K17: 01/11/21 M.11 = The smaller of: M.10 or (The following equation should be expanded depending on the # of luminaires per area. The example below is for three luminaires in one area.) (M.04 + (Fixture1DesignWatts(1-MHFactor1)) + (Fixture2DesignWatts(1-MHFactor2)) + (Fixture3Watts(1-MHFactor3)))....

## N. Tailored Decorative
| User input |  | auto calculated |  | From another Table |  |  | From look up table
N. ADDITIONAL LIGHTING ALLOWANCE: TAILORED ORNAMENTAL DECORATIVE/SPECIAL EFFECTS
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | Autofill from Table F based on 05 |  | #VALUE! |  | This Table is for NONRES
Total Design Watts for this Area: | [6 empty] | #VALUE! | #VALUE!
[7 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [7 empty] | #VALUE!
[7 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [6 empty] | #VALUE! | #VALUE!
[7 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [7 empty] | #VALUE!
[7 empty] | Add Row | Remove Last
This table is for MF COMMON AREAS
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Remove Last
Note on A8: Rebecca Rice: areas need to be pulled in from Table K now (not Table L) everywhere referenced in this Table
Note on C8: 1.20.21: Lpd = 0.35 0.4; for all Primary Function areas
Note on C17: 1.20.21: Lpd = 0.35 0.4; for all Primary Function areas

## O. Very Valuable
| User input |  | auto calculated |  | From another Table |  |  | From look up table
O. ADDITIONAL LIGHTING ALLOWANCE: TAILORED VERY VALUABLE MERCHANDISE
This category includes case lighting in retail merchandise sales, museums, and religious settings, where lighting of small art objects, artifacts, or valuable collections is required. The display case shall contain jewelry, coins, fine china, fine crystal, precious stones, silver, small art objects or artifacts, and/or valuable collections the display of which involves customer inspection of very fine detail from outside of a locked case. Lighting in this category must comply with the applicable requirements in §140.6(c)3J/§170.2(e)4B.
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Area Description | Description of Display Case | QUALIFYING FLOOR AREA |  |  | QUALIFYING DISPLAY CASE AREA
|  | Area (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Area of Display Case (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts)
Dropdown from Tbl K. |  |  | 0.55 0.50 | #VALUE! |  | 8.0 7.0 | #VALUE!
|  | 09 | 10 | 11 | 12 | 13
|  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
|  | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
|  | pull down from Table F. | auto fill from Table F |  | #VALUE!
Total Design Watts for this Area: |  |  |  |  | #VALUE! | #VALUE!
[6 empty] | Add Luminaire | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [5 empty] | #VALUE!
[6 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Area Description | Description of Display Case | QUALIFYING FLOOR AREA |  |  | QUALIFYING DISPLAY CASE AREA
|  | Area (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Area of Display Case (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts)
Dropdown from Tbl K. |  |  | 0.55 0.50 | #VALUE! |  | 8.0 7.0 | #VALUE!
|  | 09 | 10 | 11 | 12 | 13
|  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
|  | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
|  | pull down from Table F. | auto fill from Table F |  | #VALUE!
Total Design Watts for this Area: |  |  |  |  | #VALUE! | #VALUE!
[6 empty] | Add Luminaire | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [5 empty] | #VALUE!
[6 empty] | Add Row | Remove Last
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Add Luminaire
Remove Last
Note on A9: Rebecca Rice: 2019: Logic needs to pull in Table K (not table L)

## P. PAFs
User input |  |  | auto calculated | [7 empty] | From another Table |  |  | From look up table
P. POWER ADJUSTMENT: LIGHTING CONTROL CREDIT (POWER ADJUSTMENT FACTOR (PAF))
This table includes all areas indicated in Table I or Table K as using a PAF credit described in §140.6(a)2/ §170.2(e)2B.
Conditioned Spaces
01 | 02 | [9 empty] | 03 | 04 | 05 | 06 | 07
Area Description | PAF per §140.6(a)2/§170.2(e)2B1 (*Can be used in conjunction with other PAF'S) | [9 empty] | Luminaires Controlled for PAF Credit |  |  |  | Additional Control Credit Allowance (Watts)
| 1 | 2A | 2B | 2C | 3A* | 3B* | 4* | 5* | 6* | 7* | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Lighting Controlled (Watts)
| Pick up to one |  |  |  | Pick up to one |  |  | Pick up to one2
autofill from Table I. or Table K. | [10 empty] | pull down from Table F. | auto fill from Table F based on 03 selection |  | #VALUE! | PAF x col06
[13 empty] | Add Luminaire |  | Remove Last
08 | [9 empty] | 09
o | All spaces applying PAF 5, 6, or 7 include a daylight design meeting requirements in §140.3(d). See Table S. | [8 empty] | Total Power Adjustment (Watts) CONDITIONED SPACES: |  |  |  |  | 0
Unconditioned Spaces
01 | 02 | [9 empty] | 03 | 04 | 05 | 06 | 07
Area Description | PAF per §140.6(a)2/§170.2(e)2B1 (*Can be used in conjunction with other PAF'S) | [9 empty] | Luminaires Controlled for PAF Credit |  |  |  | Additional Control Credit Allowance (Watts)
| 1 | 2A | 2B | 2C | 3A* | 3B* | 4* | 5* | 6* | 7* | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Lighting Controlled (Watts)
| Pick up to one |  |  |  | Pick up to one |  |  | Pick up to one2
autofill from Table I. or Table K. | [10 empty] | pull down from Table F. | auto fill from Table F based on 03 selection |  | #VALUE! | PAF x col06
[13 empty] | Add Luminaire |  | Remove Last
08 | [8 empty] | 09
o | All spaces applying PAF 5, 6, or 7 include a daylight design meeting requirements in §140.3(d). See Table S. | [7 empty] | Total Power Adjustments (Watts) UNCONDITIONED SPACES: | [5 empty] | 0
1 FOOTNOTES: PAFs outlined in Table 140.6-A/170.2-L include 1) Daylight continuous dimming plus OFF; 2A) Occupant sensors in offices with one sensor per < 125 ft2; 2B) Occupant sensors in offices with one sensor per from 126 - 250 ft2; 2C) Occupant sensors in offices from 251 - 500 ft2; 3A) Institutional tuning, non-daylit areas; 3B) Institutional tuning, daylit areas; 4) Demand response; 5) Clerestory fenestration; 6) Horizontal slats; 7) Light shelves.
2 Luminaires that qualify for PAF 5, 6, or 7 can be used in conjunction with PAF 1.
PAF Calculation
if PAF1 is checked: PAF += 0.10 if PAF2A is checked: PAF += 0.40 0.30 if PAF2B is checked: PAF += 0.30 0.20 if PAF2C is checked: PAF += 0.20 if PAF3A is checked: PAF += 0.10 if PAF3B is checked: PAF += 0.05 if PAF4 is checked: PAF += 0.05
if PAF5 is checked:
PAF +=0.05
if PAF6 is checked:
PAF +=0.05
if PAF7 is checked:
PAF +=0.10
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Note on F8: 7.20.21: Remove PAF 2C
Note on B10: Rebecca Rice: 2019: change logic to pull in Table K( instead of L)
Note on G10: 11.16.21 if checked, NRCA-LTI-05-A changes to "Yes" in Table V. Same for Unconditioned Spaces
Note on H10: 11.16.21 if checked, NRCA-LTI-05-A changes to "Yes" in Table V. Same for Unconditioned Spaces
Note on J10: 11.16.21 If 5*, 6* OR 7* are checked NRCA-ENV-03 moves to "Yes in Table V. Same for Unconditioned Spaces
Note on Q10: Benjamin Park: For instance, if user choose 2A and 3A, PAF = 0.3 + 0.1 = 0.4
Note on B12: 2019 Update: Column 08 will be greyed out unless ANY space under Conditioned Areas selects "5", "6" or "7" in column 02.
Note on C13: Update 5.31.19: If this column is un-greyed, Table S. expands for user input.
Note on F17: 7.20.21: Remove PAF 2C
Note on B21: 2019 Update: Column 08 will be greyed out unless ANY space under Unconditioned Areas selects "5", "6" or "7" in column 02.
Note on C22: Update 5.31.19 If this column is un-greyed, Table S. expands for user input.

## Q. Rated Pwr
| User input |  | auto calculated | [5 empty] | From another Table |  |  | From look up table
Q. RATED POWER REDUCTION COMPLIANCE FOR ONE-FOR-ONE ALTERATIONS
Indoor lighting alterations complying prescriptively with §141.0(b)2I(iii)/§180.2(b)4biv are documented in this table. Any control options having a * will include a note in the Notes section of this table detailing how compliance is achieved, otherwise the compliance status in Table C will say "DOES NOT COMPLY".
01 | ¨ | Alteration scope includes a one-for-one luminaire alteration within a building or tenant space of 5,000 ft2 or less per §141.0(b)2I(iii)/§180.2(b)4biv.
02 | ¨ | At least one complete floor or complete tenant space includes a one-for-one luminaire alteration of 50 or less luminaires, per annum. These spaces do not need to comply with Part 6 requirements and therefore do not need to be included in tables below per Exception 6 to §141.0(b)2I/§180.2(b)4biv. |  |  |  |  | Applicable Spaces |  | OR | ¨ | Exception 6 applies to all spaces within the permit application
Fixture Schedule (Incude all luminaires being altered in the project)
03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14
Pre-alteration Luminaire Information | [5 empty] | Post-alteration Luminaire Information
Name or Item Tag | Complete Luminaire Description | Watts per luminaire1 | How Wattage is Determined | Total number of Luminaires | Total Watts | Name or Item Tag | Complete Luminaire Description | Watts per luminaire1 | How Wattage is Determined | Total number of Luminaires | Total Watts
|  |  | see dropdown |  | 0 |  |  |  |  | 0 | 0
#VALUE! | Percent Power Reduction2 |  | Total Pre-alteration Wattage |  | sum of column 08 | Total Post-alteration Wattage |  |  |  |  | sum of column 14
1 FOOTNOTE: Authority Having Jurisdiction may ask for Luminaire cut sheets to confirm wattage used for compliance per §130.0(c)/§160.5(b)1
2 Must be at least 40% to comply with §141.0(b)2I(iii)/§180.2(b)4biv
Mandatory Controls
15 |  | 16 |  | 17 |  | 18 |  | 19
Area Description |  | Primary Function Area |  | Manual Area Controls §130.1(a)/§160.5(b)4A |  | Shut-Off Controls §130.1(c)/§160.5(b)4C |  | * NOTES: Controls with a * require a note in the space below explaining how compliance is achieved
|  | See dropdown |  | See dropdown |  | See dropdown
How Wattage Determined
NA8 Default
Mfr. Spec1
JA8 Lamp
Other
|  | Function Area Dropdown |  | Area Controls Dropdown |  | Shutoff Controls Dropdown
|  | Use Area Category List |  | Readily Accessible Manual ON/OFF |  | Whole Building: Auto Time Switch
|  |  |  | Authorized Personnel |  | Whole Building: EMCS
|  |  |  | Annunciated * |  | Whole Building: Occ Sensor
|  |  |  | Exempt* |  | Occ Sensor
|  |  |  | Other* |  | Partial Off 130.1(c)/ 160.5(b)4C *
Partial On 130.1(c)/160.5(b)4C *
Vacancy
Auto Time Switch
EMCS
Exempt*
Other*
Countdown timer
NA: Licensed Healthcare
NA: Elec. equip. rm
NA: 24 hour/365 day
Add Luminaire
Remove Last
Reset
Add Space
Remove Last
Reset
Note on C5: 11.16.21 Clicking this box opens the other rows in the fixture table for user input.
Note on L6: Sally Blair: If this is checked, all columns in the fixture table grey out & if Mandatory Controls table is completed and complies, Table C says "Complies with Exceptional Conditions" & Exceptional condition note in Table D should be triggered.
Note on B17: 11/17/21 Clarification Comment - The Mandatory Controls Table is always displayed and required if Table Q triggers
Note on J20: Sally Blair: Grey unless a choice with a * is selected in column 17 or 18.
Note on H30: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H31: Sally Blair: Triggers NRCI-LTI-02 to move from "No" to "Yes" in Table S.
Note on H32: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H33: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H37: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H38: Sally Blair: Triggers NRCI-LTI-02 to move from "No" to "Yes" in Table S.

## R. 80% Pwr Reduction
|  | User input |  | auto calculated |  | From another Table |  |  | From look up table
R. 80% LIGHTING POWER FOR ALTERATIONS- CONTROLS EXCEPTIONS
Indoor lighting alteration spaces complying prescriptively with §141.0(b)2I(ii)/§180.2(b)4Bivb are included in this table to document the power reduction. If the Percent of Indoor Lighting Power Allowance exceeds 80%, the compliance status in Table C for Controls will say "DOES NOT COMPLY".
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Complete Building or Area Category Primary Function Area | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS
|  | Area (ft²) | Allowed Density (W/ft²) | Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
| Same list as Table I column 02 |  | Autofill based on Primary Function (in 02) | #VALUE! | Drop down from Table F | Autofill from Table F based on 06 |  | #VALUE!
Total Allowance (Watts) for all Areas: |  |  |  | #VALUE! | Total Design Watts for all Areas: |  |  | #VALUE!
Percent of Indoor Lighting Power Allowance: | [7 empty] | #VALUE!
Add Luminaire
Remove Last
Add Row
Remove Last
Note on A3: Usability Update: If table triggered, but column 01-04 & 06 -08 aren't completed, trigger Table D row 19 note.
Note on D8: Sally Blair: Same allowed density as in Table I column 03, based on same Function Area list.
Note on I11: Usability Update 7.19.19: If > .8, trigger note in Table D row 18.

## S.Daylight PAF
S. DAYLIGHT DESIGN POWER ADJUSTMENT FACTOR (PAF)
This table documents clerestories, horizontal slats or light shelves meet the requirements in §140.3(d)/§170.2(e)2B if a Power Adjustment Factor was claimed on Table P. These features must be documented on the architectural plans or where appropriate within the construction documents. This PAF also must be verified in the field with an acceptance test per Table U.
01 | Compliance Strategy |  |  | see dropdown
Clerestory Fenestration
| Yes | Not Applicable | Requirement
02 | ¨ |  | Installed on East, West or South façade
03 | ¨ |  | Head height >= 10ft above finished floor
04 | ¨ |  | Glazing height >= 0.10 x head height
05 | ¨ | ¨ | Operable shading on clerestory is controlled seperately from other shading
Interior and Exterior Horizontal Slats
| Yes | Not Applicable | Requirement
06 | ¨ |  | Installed on East or West façade with 20-30% WWR and extend the entire height of vertical fenestration
07 | ¨ |  | Exterior slats level or sloped downward from fenestration. Interior slats level or sloped upward from fenestration. Slats are permanently mounted and not adjustable.
08 | ¨ |  | Slats have a Projection Factor per Table 140.3-E/170.2-N D Daylighting Devices and extend the entire height of the vertical fenestration and beyond each side of the window jamb by a distance >= their horizontal projection. Slats do not need to extend beyond the jamb if they are located entirely within the fenestration rough opening or a fin is located at the jamb and extends vertically the entire height of the jamb and horizontally the entire depth of the projection.
09 | ¨ | ¨ | Slats have a minimum Distance Factor of 0.3 calculated per §140.3(d)/§170.2(e)2Bxii
10 | ¨ |  | Slats have a minimum Visible Reflectance of 0.50 tested in accordance with ASTM E903, and are either opaque or have a maximum Visible Transmittance of 0.03 tested in accordance with ASTM E1175
11 | Location of slat design in construction documents:
Interior and Exterior Light Shelves
| Yes | Not Applicable | Requirement
12 | ¨ | ¨ | Where there is vertical fenestration area below the light shelf, both interior and exterior light shelves shall be installed.
13 | ¨ |  | Light shelves installed adjacent to clerestory fenestration on south façade with > 30% WWR and with a head height <= 1ft below the finished ceiling.
14 | ¨ |  | Exterior shelves level or sloped downward from fenestration. Interior shelves level or sloped upward from fenestration.
15 | ¨ |  | Shelves have a Projection Factor per Table 140.3-D Daylighting Devices and extend beyond each side of the window jamb by a distance >= their horizontal projection.
16 | ¨ | ¨ | Shelves have a minimum Distance Factor of 0.3 calculated per §140.3(d)/§170.2(e)2Bxii
17 | ¨ |  | Shelves have a top surface with a minimum Visible Reflectance of 0.50 tested in accordance with ASTM E903, or an exterior light shelf installed > 2ft below the clerestory sill.
18 | Location of light shelf design in construction documents:
Compliance Strategy Dropdown
|  |  |  | Clerestories | < Opens Clerestory "subtable" (rows 4-9) for user input
|  |  |  | Horizontal Slats | < Opens Horizontal Slats "subtable" (rows 10-16) for user input
|  |  |  | Light Shelves | < Opens Clerestory "subtable" (rows 4-9) AND Light Shelf subtable (Row 17-24) for user input
Note on E29: Sally Blair: User should be able to choose more than one.

## T. Dwelling Units
| User input |  |  |  | auto calculated | From another Table | From look up table
This entire table is new for 2022
T. DWELLING UNIT LIGHTING
This table documents compliance with mandatory requirements for dwelling unit indoor lighting per §160.5(a) and §180.2(b)4A for alterations. Lighting systems in common use areas providing shared provisions for living, eating, cooking, or sanitation to dwelling units that would otherwise lack these provisions may document compliance with §160.5(a) in this table or may document compliance with lighting for nonresidential occupancies in other tables of this form.
01 | Indicate lighting and electrical components included in multifamily dwelling units: |  |  | ¨ Luminaires
¨ Blank Electrical Boxes
Luminaires
| Yes | Not Applicable | Requirement
02 | ¨ |  | All installed luminaires shall meet the requirements in TABLE 160.5-A except lighting integral to exhaust fans, kitchen range hoods, bath vanity mirrors, and garage door openers, and non-removable lighting attached to ceiling fans; lighting internal to drawers, cabinetry, and linen closets with an efficacy of 45 lumens per watt or greater.
03 | ¨ | ¨ | Screw based luminaires shall contain lamps that comply with Reference Joint Appendix JA8.
04 | ¨ | ¨ | Recessed Downlight Luminaires other than those marked for use in fire-rated installations and other than recessed luminaires installed in non-insulated ceilings shall meet all of the following requirements: - Shall not contain screw base lamp sockets; and - Have a label that certifies the luminaire is airtight with air leakage less than 2.0 cfm at 75 Pascals when tested in accordance with ASTM E283. An exhaust fan housing with integral light shall not be required to be certified airtight; and - Be sealed with a gasket or caulk between the luminaire housing and ceiling, and have all air leak paths between conditioned and unconditioned spaces sealed with a gasket or caulk, or be installed per manufacturer’s instructions to maintain airtightness between the luminaire housing and ceiling; and - Meet the clearance and installation requirements of California Electrical Code Section 410.116 for recessed luminaires.
05 | ¨ | ¨ | Light Sources in Enclosed or Recessed Luminaires. Lamps and other separable light sources that are not compliant with the JA8 elevated temperature requirements, including marking requirements, shall not be installed in enclosed or recessed luminaires.
Lighting Controls
| Yes | Not Applicable | Requirement
06 | ¨ |  | Lighting shall have readily accessible wall-mounted controls that allow the lighting to be manually turned ON and OFF. Ceiling fans may provide control of integrated lighting via a remote control.
07 | ¨ |  | Lighting controls shall comply with the applicable requirements of Section 110.9.
08 | ¨ | ¨ | No controls shall bypass a dimmer, occupant sensor or vacancy sensor function where that dimmer or sensor has been installed to comply with Section160.5(a)2.
09 | ¨ | ¨ | An Energy Management Control System (EMCS) or a multiscene programmable controller may be used to comply with dimming, occupancy, and lighting control requirements in Section 160.5(a)2 if it provides the functionality of the specified controls in accordance with Section 110.9, and the physical controls specified in in Section 160.5(a)2A.
10 | ¨ |  | In bathrooms, garages, laundry rooms, utility rooms, and walk-in closets, at least one installed luminaire shall be controlled by an occupantcy or vacancy sensor providing automatic-off functionality.
11 | ¨ | ¨ | For lighting internal to drawers and cabinetry with opaque fronts or doors, controls that turn light off when the drawer or door is closed shall be provided.
12 | ¨ |  | Lighting in habitable spaces, including but not limited to living rooms, dining rooms, kitchens, and bedrooms, shall have readily accessible wall-mounted dimming controls that allow the lighting to be manually adjusted up and down OR luminaires must be controlled by an occupancy or vacancy sensor providing automatic-off functionality. Forward phase cut dimmers controlling LED light sources shall comply with NEMA SSL 7A. Ceiling fans may provide control of integrated lighting via a remote control. Lighting internal to drawers and cabinetry with opaque fronts or doors or with automatic off controls does not need to provide dimming controls.
13 | ¨ |  | Integrated lighting of exhaust fans shall be controlled independently from the fans. The following shall be controlled separately from ceiling-installed lighting such that one can be turned on without turning on the other: - Undercabinet lighting - Undershelf lighting - Interior lighting of display cabinets - Switched outlets
Blank Electrical Boxes
| Yes | Not Applicable | Requirement
14 | ¨ |  | The number of electrical boxes that are more than 5 feet above the finished floor and do not contain a luminaire or other device shall be no greater than the number of bedrooms. These electrical boxes must be served by a dimmer, vacancy sensor control, low voltage wiring or fan speed control.
Note on F5: Sally Blair: Triggers "Luminaires" & Lighting Controls subtables
Note on F6: Sally Blair: Triggers blank electrical box subtable

## U. NRCI
U T. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
NRCI-LTI-01-E - Must be submitted for all buildings
NRCI-LTI-02-E - Must be submitted for a lighting control system, or for an Energy Management Control System (EMCS), to be recognized for compliance.
NRCI-LTI-04-E - Must be submitted for two interlocked systems serving an auditorium, a convention center, a conference room, a multipurpose room, or a theater to be recognized for compliance.
NRCI-LTI-05-E - Must be submitted for a Power Adjustment Factor (PAF) to be recognized for compliance.
NRCI-LTI-06-E - Must be submitted for additional wattage installed in a video conferencing studio to be recognized for compliance.
Note on B4: Need to include new URL for Cert of install forms.
Note on B7: Sally Blair: Always Yes.
Note on B8: 2019 Usability updates 7.19.19: Should default no and trigger Yes if "EMCS" is chosen in any cell in Table H
Note on B9: 2019 Usability Updates 7.19.19: Should default no and move to yes if H11 is clicked
Note on B10: Sally Blair: Moves to Yes if Table P is triggered

## U. LMCI
U T. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
LMCI-LTI-01-E - Must be submitted for all buildings
NRCI-LTI-02-E - Must be submitted for a lighting control system, or for an Energy Management Control System (EMCS), to be recognized for compliance.
NRCI-LTI-04-E - Must be submitted for two interlocked systems serving an auditorium, a convention center, a conference room, a multipurpose room, or a theater to be recognized for compliance.
NRCI-LTI-05-E - Must be submitted for a Power Adjustment Factor (PAF) to be recognized for compliance.
NRCI-LTI-06-E - Must be submitted for additional wattage installed in a video conferencing studio to be recognized for compliance.
Note on B4: Need to include new URL for Cert of install forms.
Note on B7: Sally Blair: Always Yes.
Note on B8: 2019 Usability updates 7.19.19: Should default no and trigger Yes if "EMCS" is chosen in any cell in Table H
Note on B9: 2019 Usability Updates 7.19.19: Should default no and move to yes if H11 is clicked
Note on B10: Sally Blair: Moves to Yes if Table P is triggered

## V. NRCA
V U. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and any with "-A" in the form name must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
NRCA-LTI-02-A - Must be submitted for occupancy sensors and automatic time switch controls.
NRCA-LTI-03-A - Must be submitted for automatic daylight controls.
NRCA-LTI-04-A - Must be submitted for demand responsive lighting controls.
NRCA-LTI-05-A - Must be submitted for institutional tuning power adjustment factor (PAF).
NRCA-ENV-03-F - Must be submitted for daylighting design power adjustment factors (PAF).
Any n ew indoor lighting NRCA forms for 2022?
Note on D8: Usability Update: should start as "No" and move to "Yes" if Table H column 09 OR Table H column 10 says "included" for any row in Table H.
Note on C11: Usability Update: Starts as "No", moves to "Yes" if 5*, 6* OR 7* are checked in Table P for any row.

## V. LMCA
V U. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and any with "-A" in the form name must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
LMCA-LTI-02-A - Must be submitted for occupancy sensors and automatic time switch controls.
LMCA-LTI-03-A - Must be submitted for automatic daylight controls.
LMCA-LTI-04-A - Must be submitted for demand responsive lighting controls.
LMCA-LTI-05-A - Must be submitted for institutional tuning power adjustment factor (PAF).
LMCA-ENV-03-F - Must be submitted for daylighting design power adjustment factors (PAF).
Any new indoor lighting LMCA forms for 2022?
Note on D8: Usability Update: should start as "No" and move to "Yes" if Table H column 09 OR Table H column 10 says "included" for any row in Table H.
Note on C11: Usability Update: Starts as "No", moves to "Yes" if 5*, 6* OR 7* are checked in Table P for any row.

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/ HERS Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Designer Name: | Responsible Designer Signature:
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
[d:OnlyUI] The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-LTI form. [d:/OnlyUI]
Diane, in schema this needs to allow more than one responsible person.
?
Add Responsible Person
Note on F13: 2019 Update: This button should duplicate this table in the pdf, but the user input fields should be blank, but editable by the user.
Note on B15: UI Only: Table tip only applies to UI, does not apply to report generator.

## Dropdown Data
[10 empty] | 1 | 1 | Primary Function Area per Table 140.6-D | Room Configuration | Mounting Height (ft) | Primary Function Area per 140.6(c)3H | illuminance Value (LUX)
1 | 1 | 1 |  |  |  |  | Dropdown
Mandatory Demand Response | Shut-off Controls | Area Controls | Multi-Level | Shut-Off | 1 | Row | Area Controls | Multi-Level | Shut-Off | CEC Default | Retail (50%) | Auditorium Area | Rectangular | ≥ 16 feet | Exercise Center, Gymnasium | 50
[7 empty] | 1 | 1 | 1 | Other¹ | Office (50%) | Civic Meeting Place | Non-Rectangular | 12 to 16 feet | Medical and Clinical Care | 100
Required > 10,000 SF | Whole Building Timeswitch | Manual ON/OFF | Dimmer | Occ. Sensor | Included |  | 1 | 1 | 1 |  | Hotel (50%) | Convention Area |  | < 16 feet | Police Stations and Fire Stations | 150
Not Required < 10,000 SF | Whole Building "Other" * | Auth. Personel | Bi-level Switch | See Bldg Lvl | Exempt * |  | 1 | 1 | 1 |  | All Other (35%) | Conference Area |  |  | Public rest areas along state and federal roadway | 200
Not Required - Installing as PAF | See Area/Space Level Controls | Annunciated * | Exempt * | Partial Off * | N/A |  | 2 | 2 | 10 |  |  | Multipurpose Area |  |  | Other | 300
|  | Exempt * | Other * | Partial On * |  |  | 1 | 1 | 1 |  |  | Meeting Center Area |  |  |  | 400
|  | Other * |  | Vacancy |  |  | 1 | 1 | 1 |  |  | Dining Areas |  |  |  | 500
|  |  |  | Auto Timeswitch |  |  | 1 | 1 | 1 |  |  | Exhibit, Museum Areas |  |  |  | 600
|  |  |  | EMCS |  |  | 1 | 1 | 1 |  |  | Financial Transaction Area |  |  |  | 700
|  |  |  | Exempt * | [7 empty] | Grocery Store Area |  |  |  | 800
|  |  |  | Other * | [7 empty] | Hotel Function Area |  |  |  | 900
[12 empty] | Hotel Lobby |  |  |  | 1000
Main Entry Lobby
Lounge Area
Malls and Atria
Religious Worship Area
Retail Merchandise Sales
Showroom Area
Motion Picture Theater
Performance Theater
Transportation Function Area
Waiting Area