## New Table Sequence
Label | Table Title | Trigger within: | Note:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Domestic Hot Water Equipment | Table B.
Table G | Domestic Hot Water Distribution Systems | Table B.
Table H | Domestic Hot Water System Controls | Table B.
Table I | Declaration of Required Certificates of Installation | ALWAYS
Table J | Declaration of Required Certificates of Acceptance | ALWAYS
- | Documentation Author's Declaration Statement | ALWAYS

## Hyperlinks
Section | Applicable Tables
110.1 | header, F
110.3 | header, F, H
120.3 | header, G
140.5 | header, B, G
141.0 | header
141.0(a) | header, B
150.0 | header, G
150.1(c)8 | header, B, F, H
150.2 | header, F, H
141.0(b)2N | B
150.1(c)8Ai | F
§150.2(b)1H | F
150.2(b)1G | F
150.0(n)1 | F
150.0(a)1 | F
110.3(c)3/4 | F
110.3(c)5 | F
110.3(c)6 | D
110.3(c) | G
110.3(c)4A/B/C/D/E/F | G
150.1 | G
110.3(c)5 | G
150.1(c)8Bii | G, H
RA3.6.9 | G
RA4.4.6 | G
150.1(c)8Aii | G
150.1(c)8Aiv | G
150.1(c)14 | G
150.1(c)8Av | G
RA4.4.16 | G
150.1(c)8Aiii | G
Table 120.3-A | G
150.0(j)2A | G
150.0(j)3 | G
110.3(a) | H
110.3(c)1/2 | H
RA4.4.9 | H
110.12(a) | H
150.2(b)1Hiii

## NRCC Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Domestic Water Heating System
NRCC-PLB-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-PLB-E
This document is used to demonstrate compliance for nonresidential occupancies with requirements in §110.1, §110.3, §120.3, and §140.5, and with requirements in §141.0 for additions and alterations, for domestic water heating scopes using the prescriptive path. For high-rise residential and hotel/motel occupancies, compliance is demonstrated with requirements in §110.1, §110.3, §160.4 and §170.2(d) §120.3, §150.0 and §150.1(c)8, and with requirements in §150.2 §180.1 for additions and §180.2 for alterations.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Domestic Water Heating System
NRCC-PLB-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-PLB-E
Project Name: |  |  |  | Report Page: | Page 2 of ??
Project Address: |  |  |  | Date Prepared:
CA Building Energy Efficiency Standards - 201922 Nonresidential Compliance: http://www.energy.ca.gov/title24/2019standards
Heading First Page Only
Heading All Other Pages
Footer All Pages
Note on A20: 8.24.21: Update with new URL

## LMCC Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Domestic Water Heating System
LMCC-PLB-01-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | LMCC-PLB-01-E
This document is used to demonstrate compliance for nonresidential occupancies with requirements in §110.1, §110.3, §120.3, and §140.5, and with requirements in §141.0 for additions and alterations, for domestic water heating scopes systems serving nonresidential occupancies within low-rise mixed use buildings using the prescriptive path. For high-rise low-rise residential and hotel/motel occupancies, compliance is demonstrated with requirements in §110.1, §110.3, §160.4 and §170.2(d) §120.3, §150.0 and §150.1(c)8, and with requirements in §150.2 §180.1 for additions and §180.2 for alterations.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Domestic Water Heating System
LMCC-PLB-01-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | LMCC-PLB-01-E
Project Name: |  |  |  | Report Page: | Page 2 of ??
Project Address: |  |  |  | Date Prepared:
CA Building Energy Efficiency Standards - 201922 Nonresidential Compliance: http://www.energy.ca.gov/title24/2019standards
Heading First Page Only
Heading All Other Pages
Footer All Pages
Note on A20: 8.24.21: Update with new URL

## NRCC A. General Info
| User input |  | auto calculated |  | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 02 | Climate Zone |  | Dropdown
03 | Occupancy Types Within Project (select all that apply):
¨ | Nonresidental Office | ¨ | High-Rise Residential Multifamily > 4 stories | ¨ | Relocatable | ¨ | School | ¨ | Restaurant/ Commercial Kitchen | ¨ | Religious Facility
¨ | State Building | ¨ | Healthcare Facility | ¨ | Hotel/ Motel | ¨ | Other (Write In) All Others | ¨ | Convention Center | ¨ | Medical Clinic
¨ | Auditorium | ¨ | Parking Garage | ¨ | Warehouse | ¨ | Retail | ¨ | Sports Arena | ¨ | Gymnasium
¨ | Classroom | ¨ | Library | ¨ | Theater | ¨ | Data Center | ¨ | Support Areas | ¨ | Financial Institution
¨ | Commercial/ Industrial | ¨ | School | ¨ | Grocery Store
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on F10: 11.4.21: Only occupancies that have been selected by the user as included in the project will show up on the pdf form.

## LMCC A. General Info
| User input |  | auto calculated |  | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 02 | Climate Zone |  | Dropdown
03 | Occupancy Types Within Project (select all that apply):
¨ | Nonresidental Office | ¨ | Low-Rise Residential Multifamily <= 3 stories | ¨ | Relocatable | ¨ | School | ¨ | Restaurant/ Commercial Kitchen | ¨ | Religious Facility
¨ | State Building | ¨ | Healthcare Facility | ¨ | Hotel/ Motel | ¨ | Other (Write In) All Others | ¨ | Convention Center | ¨ | Medical Clinic
¨ | Auditorium | ¨ | Parking Garage | ¨ | Warehouse | ¨ | Retail | ¨ | Sports Arena | ¨ | Gymnasium
¨ | Classroom | ¨ | Library | ¨ | Theater | ¨ | Data Center | ¨ | Support Areas | ¨ | Financial Institution
¨ | Commercial/ Industrial | ¨ | School | ¨ | Grocery Store
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on F10: 11.4.21: Only occupancies that have been selected by the user as included in the project will show up on the pdf form.

## NRCC B. Project Scope
|  | User input |  | auto calculated | from another table |  |  | From look up table
B. PROJECT SCOPE
This table identifies any domestic water heating systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive paths outlined in §140.5/ §170.2(d), §150.1(c)8, and §141.0(a)/ §180.1, or §141.0(b)2N/ §180.2 for additions or alterations. Solar water heating systems should be documented on the NRCC-SRA SAB compliance document. Combined hydronic water heating systems should be documented on the NRCC-MCH compliance document.
01 |  |  |  | 02 | 03
My project consists of (check all that apply): |  |  |  | System Type1,2 | System Components
¨ | New System (DHW system being installed for the first time in newly constructed building) |  |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls
[6 empty] | Add New System | Remove Last
¨ | System Alteration (equipment, distribution or controls) |  |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls
[6 empty] | Add Alteration | Remove Last
ALERT! Gas or propane central water heating systems serving multiple dwelling units require a solar water heating system per §150.1(c)8B §170.2(d)3. Solar water heating systems are documented on the NRCC-SRA SAB compliance document. If solar water heating systems are used in conjunction with non-solar systems to meet the water heating needs of the building, document the non-solar systems on this compliance document. | [7 empty] | << triggers exception condition in Table D. See Table D row 9
ALERT! Combined domestic and hydronic water heating systems are documented on the NRCC-MCH compliance document. If combined hydronic water heating systems are used in conjunction with domestic only systems to meet the water heating needs of the building, document the domestic only systems on this compliance document. | [7 empty] | << triggers exception condition in Table D. See Table D row 10
1 FOOTNOTE: Point of use water heaters, or other non-central systems used to serve nonresidential spaces, are considered individual systems.
2 Dwelling units refers to hotel/ motel guest rooms and units in a high-rise multifamily residential occupancy.
3 DHW systems serving 2 or more dwelling units are considered "Central Systems" for multifamily occupancies.
System Type Dropdown
|  |  | triggers "Recirculation Loops in Central Systems…" section in Table G.>> | Central System (serving nonresidential spaces)
Individual System (serving nonresidential spaces)1
|  |  | triggers the ALERT! note in row 11 AND "Recirculation Loops in Central Systems…" section in Table G>> | Central System (serving 2+ dwelling units)2, 3
|  |  | triggers "Individual Dwelling Units" sections in Table F & Table G >> | Individual Dwelling Unit System(s)2
|  |  | triggers the "ALERT!.." note in row 11 >> | Dwelling Unit Solar Thermal System
|  |  | triggers the "ALERT!.." note in row 12 >> | Combined Hydronic System
Note on I8: Sally Blair: These buttons duplicate/ remove Row 7
Note on G9: Sally Blair: Any selection of "Equipment" in column 03 opens Table F.
Note on H9: Sally Blair: Any selection of "Distribution" in column 03 opens Table G.
Note on I9: Sally Blair: Any selection of "Controls" in column 03 opens Table H.
Note on I10: Sally Blair: These buttons duplicate/ remove Row 9
Note on D17: Sally Blair: these triggers are secondary to column 03. For example, if distribution is NOT checked in column 03, the Table G is not triggered. If it is checked, this selection in column 02 would open the triggered section. Let me know if you need clarification.

## LMCC B. Project Scope
|  | User input |  | auto calculated | from another table |  |  | From look up table
B. PROJECT SCOPE
This table identifies any domestic water heating systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive paths outlined in §140.5/ §170.2(d), §150.1(c)8, and §141.0(a)/ §180.1, or §141.0(b)2N/ §180.2 for additions or alterations. Solar water heating systems should be documented on the LMCC-SRA SAB compliance document. Combined hydronic water heating systems should be documented on the LMCC-MCH compliance document.
01 |  |  |  | 02 | 03
My project consists of (check all that apply): |  |  |  | System Type1,2 | System Components
¨ | New System (DHW system being installed for the first time in newly constructed building) |  |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls
[6 empty] | Add New System | Remove Last
¨ | System Alteration (equipment, distribution or controls) |  |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls
[6 empty] | Add Alteration | Remove Last
ALERT! Gas or propane central water heating systems serving multiple dwelling units require a solar water heating system per §150.1(c)8B §170.2(d)3. Solar water heating systems are documented on the LMCC-SRA SAB compliance document. If solar water heating systems are used in conjunction with non-solar systems to meet the water heating needs of the building, document the non-solar systems on this compliance document. | [7 empty] | << triggers exception condition in Table D. See Table D row 9
ALERT! Combined domestic and hydronic water heating systems are documented on the LMCC-MCH compliance document. If combined hydronic water heating systems are used in conjunction with domestic only systems to meet the water heating needs of the building, document the domestic only systems on this compliance document. | [7 empty] | << triggers exception condition in Table D. See Table D row 10
1 FOOTNOTE: Point of use water heaters, or other non-central systems used to serve nonresidential spaces, are considered individual systems.
2 Dwelling units refers to hotel/ motel guest rooms and units in a high-rise multifamily residential occupancy.
3 DHW systems serving 2 or more dwelling units are considered "Central Systems" for multifamily occupancies.
System Type Dropdown
|  |  | triggers "Recirculation Loops in Central Systems…" section in Table G.>> | Central System (serving nonresidential spaces)
Individual System (serving nonresidential spaces)1
|  |  | triggers the ALERT! note in row 11 AND "Recirculation Loops in Central Systems…" section in Table G>> | Central System (serving 2+ dwelling units)2, 3
|  |  | triggers "Individual Dwelling Units" sections in Table F & Table G >> | Individual Dwelling Unit System(s)2
|  |  | triggers the "ALERT!.." note in row 11 >> | Dwelling Unit Solar Thermal System
|  |  | triggers the "ALERT!.." note in row 12 >> | Combined Hydronic System
Note on I8: Sally Blair: These buttons duplicate/ remove Row 7
Note on G9: Sally Blair: Any selection of "Equipment" in column 03 opens Table F.
Note on H9: Sally Blair: Any selection of "Distribution" in column 03 opens Table G.
Note on I9: Sally Blair: Any selection of "Controls" in column 03 opens Table H.
Note on I10: Sally Blair: These buttons duplicate/ remove Row 9
Note on D17: Sally Blair: these triggers are secondary to column 03. For example, if distribution is NOT checked in column 03, the Table G is not triggered. If it is checked, this selection in column 02 would open the triggered section. Let me know if you need clarification.

## C. Compliance
| User input |  |  | From look up table
C. COMPLIANCE RESULTS
Table Instructions: Table C will indicate if the project data input into the compliance document is compliant with water heating requirements. This table is not editable by the user. If this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D., or the table indicated as not compliant for guidance.
01 |  | 02 | 03 | 04
Domestic Hot Water Equipment |  | Distribution Systems | Controls | Compliance Results
Table F |  | Table G | Table H
YES |  |  |  | COMPLIES, COMPLIES with Exceptional Conditions or DOES NOT COMPLY
Note on A9: 9.1.21 Says "YES" if all of the below conditions are met: 1. If "Equipment Schedule: Individual Systems" is triggered for user input, F05>=F06 2. If "Equipment Schedule: Water Heater Efficiency and Standby Loss Central Systems" is triggered for user input, EITHER: - column 05 is not checked AND - F11 >= F12 if not gray AND - F14 <= F15 if not gray OR - column 05 is checked AND - col 06 >= 90% AND - F11 >= F12 if not gray & col 10 <= 100,000 AND - F14 < F15 if not gray 3. If "Equipment in Individual Dwelling Units" is triggered for user input, F17 is "Y" or "NA" 4. F18, F19 anf F20 and F21 are all either "Y" or "NA" 5. Otherwise says "NO" Grey out if Table F not triggered
Note on C9: Katie Gustafson: Says "YES" if no "No" have been checked AND if all triggered rows for Mandatory Pipe Insulation have been checked. Otherwise, says "NO" Grey out if Table G not triggered.
Note on E9: Sally Blair: Says "YES" if no "No" have been checked. Otherwise, says "NO" Grey out if Table H not triggered.
Note on F9: Sally Blair: Says "COMPLIES" if all columns which are not greyed out say "YES". Says "COMPLIES with Exceptional Conditions" if all columns which are not greyed out say "YES" AND an exceptional condition is triggered in Table D. Otherwise, says "DOES NOT COMPLY"

## NRCC D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Table B indicates a solar water heating system will be used to comply with Title 24, Part 6. These systems shall be documented on the NRCC-SRA SAB-E compliance document. |  |  |  |  | << triggered if Table B row 13 "Alert…" is triggered
Table B indicates a combined hydronic system will be used to comply with Title 24, Part 6. These systems shall be documented on the NRCC-MCH-E compliance document. |  |  |  |  | << triggered if Table B row 14 "Alert…" is triggered
Tables A and B indicate the project is a new State building. This requires 60% of energy for service water heating from site solar energy or recovered energy per §110.3(c)6. |  |  |  |  | << triggered if Table A says "State Building" in column 03 AND "New System" is selected in Table B column 01
Table F indicates a heat pump water heater replacement in Climate Zone 16. In addition to meeting the minimum Uniform Energy Factor (UEF), this requires a solar water heating system with solar savings fraction > 0.4. Document the solar water heating system on the NRCC-SRA compliance document. |  |  |  |  | << triggered by Table F column 02 Equipment Type
Table F indicates an electric water heater is being used because natural gas is not available to the water heater location to replace an existing electric resistance water heater. |  |  |  |  | << Triggers when F16e_EquipmentTypeApplies = "Yes"

## LMCC D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Table B indicates a solar water heating system will be used to comply with Title 24, Part 6. These systems shall be documented on the LMCC-SRA SAB-E compliance document. |  |  |  |  | << triggered if Table B row 13 "Alert…" is triggered
Table B indicates a combined hydronic system will be used to comply with Title 24, Part 6. These systems shall be documented on the LMCC-MCH-E compliance document. |  |  |  |  | << triggered if Table B row 14 "Alert…" is triggered
Tables A and B indicate the project is a new State building. This requires 60% of energy for service water heating from site solar energy or recovered energy per §110.3(c)6. |  |  |  |  | << triggered if Table A says "State Building" in column 03 AND "New System" is selected in Table B column 01
Table F indicates a heat pump water heater replacement in Climate Zone 16. In addition to meeting the minimum Uniform Energy Factor (UEF), this requires a solar water heating system with solar savings fraction > 0.4. Document the solar water heating system on the NRCC-SRA compliance document. |  |  |  |  | << triggered by Table F column 02 Equipment Type
Table F indicates an electric water heater is being used because natural gas is not available to the water heater location to replace an existing electric resistance water heater. |  |  |  |  | << Triggers when F16e_EquipmentTypeApplies = "Yes"

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## F. Equipment
F. DOMESTIC HOT WATER EQUIPMENT
Table Instructions: Complete the following table to demonstrate compliance with mandatory equipment requirements in §110.1 and §110.3. For high-rise residential and hotel/motel occupancies, cCompliance with prescriptive requirements in §150.1(c)8 §140.5(c)/§170.2(d) must also be demonstrated and with §150.2 §141.0/§180.1/§180.2 for addition and alteration scopes.
Equipment Schedule: Individual Systems
01 | 02 |  | 03 | 04 | 05 | 06
Name or Item Tag | Equipment Type |  | Volume (gal) | Max GPM/ First Hour Rating (FHR) | Rated Uniform Energy Factor (UEF) | Minimum Required Uniform Energy Factor (UEF)1
| See dropdown |  | See dropdown | See dropdown |  | Ben, values come from CEC Water Heater Efficiency Guide, screenshot below in blue
1 FOOTNOTE: Compliant equipment may be found in the Modernized Appliance Efficiency Database System (MAEDBS) on the Energy Commission website: https://cacertappliances.energy.ca.gov/Pages/Search/AdvancedSearch.aspx | [5 empty] | Reset Table | Add Row | Remove Last
Equipment Schedule: Central Systems Water Heater Efficiency and Standby Loss
03 |  | 04 |  |  | 05 |  | 06
System Name: |  | Exception to §140.5(c)/§170.2(d)3: |  | dropdown | ¨ | Capacity-weight efficiencies for gas systems >= 1MMBtu/h1 | Capacity-weighted Average Efficiency (%) | Note: this is a calculated field per the comment
07 | 08 | 09 | 10 |  | 11 | 12 | 13 | 14 | 15
Name or Item Tag | Equipment Type | Volume (gal) | Rated Input Capacity (Btu/h) | Max GPM/ First Hour Rating (FHR) | Rated Efficiency (%) | Minimum Efficiency Required (%) | Efficiency Unit | Designed Standby Loss | Maximum Standby Loss
| See dropdown |  |  | See Dropdown |  | Ben, values come from Table F-4 OR Table 110.2-KJ OR S140.5(c) (see column P) depending on column 08 |  |  | See Table F-4 in column P
1 FOOTNOTE: In systems >= 1MMBtu/h with multiple units, gas water heaters with input capacity > 100,000 Btu/h may meet the 90% Et requirement via an input capacity-weighted average. | [5 empty] | Add System | Add Water Heater | Remove Last
2 FOOTNOTE: Compliant equipment may be found in the Modernized Appliance Efficiency Database System (MAEDBS) on the Energy Commission website: https://cacertappliances.energy.ca.gov/Pages/Search/AdvancedSearch.aspx
Exception Dropdown
25% of the annual service water-heating requirement is provided by site-solar energy or site-recovered energy.
Adding gas SWH system >= 1MMBtu/h input capacity to existing building
Heat pump system serves multifamily dwelling units only (§170.2(d)2)
Gas system serves multifamily dwelling units only in CZ 10-16
Exceptions Do Not Apply
Water Heating Equipment in Individual Dwelling Units1
Equipment Type (select all that apply):
16 | ¨ | Gas/propane instantaneous water heater with input rating ≤ 200,000 BTUH and no storage tank. Note: Can not comply using the prescriptive path with a storage tank per §150.1(c)8Ai §170.2(d)1C (New Construction and Additions Only)
| ¨ | A single 240 volt heat pump water heater serving the dwelling unit. (New Construction and Additions Only) Gas/propane storage type water heater with input rating ≤ 75,000 BTUH
|  | ¨ | Rated volume ≤ 55 gal
|  | ¨ | Rated volume > 55 gal
| ¨ | A single heat pump water heater with storage tank located in the garage or conditioned space. (New Construction Only) that meets the requirements of NEEA Advanced Water Heater Specification Tier 3 or higher.
|  | ¨ | Water heater meets the requirements of NEEA Advanced Water Heater Specification Tier 3 or higher.
| ¨ | A single heat pump water heater with storage tank located in the garage or conditioned space and be placed on an incompressible, rigid insulated surface with minimum R-10. The water heater shall be installed with a communication interface that meets either the requirements of 110.12(a) or has a ANSI/CTA-2045-B communication port . (Alterations in climate zones 1-15 Only)
|  | ¨ | Water heater meets the requirements of NEEA Advanced Water Heater Specification Tier 3 or higher.
| ¨ | No gas connection to existing water heater location for replacement water heater. If the existing water heater is an electric resistance water heater, a consumer electric water heater. Consumer electric water heater must meet Title 20 Appliance Efficiency requirements (see Equipment Schedule above) per §150.2(b)1H. (Alterations only)
| ¨ | Replacement or altered gas or propane water heater (Alterations only)
17 | Yes | No | Not Applicable | Requirement
| ¨ | ¨ | ¨ | For gas or propane water heaters serving individual dwelling units, the follow components are included in the design per §150.0(n)1 §160.4: (New Construction and Additions only) - Dedicated 125V, 20 amp electrical receptacle that is connected to the panel with a 120/240V 3 conductor, 10 AWG copper branch circuit within 3 ft from the water heater that's accessible and with both ends of the unused conductor labeled with the word "spare" and be electrically isolated. A single pole circuit breaker space in the panel adjacent to the circuit breaker for the branch circuit is provided labeled with the word "future 240V use"; and - Category III or IV vent, or Type B vent with straight pipe between the outside termination and where the water heater is installed; and - Condensate drain that is no more than 2in higher than the base of the water heater and drains without pump assistance; and - Gas supply line with a capacity of at least 200,000 BTUH
1 FOOTNOTE: Dwelling units refers to hotel/ motel guest rooms and units in a high-rise multifamily residential occupancy.
Water Heating Equipment All Occupancies
| Yes | No | Not Applicable | Requirement
18 | ¨ | ¨ | ¨ | Unfired storage tank insulation shall have Internal + External ≥ R-16 OR External ≥ R-12 3.5. Label required per §110.3(c)3
19 | ¨ | ¨ | ¨ | New state buildings 60% of energy for service water heating from site solar energy or recovered energy per §110.3(c)5 | [6 empty] | << Applies to 300kBtu/h - <1MMBtu/h
20 | ¨ | ¨ | ¨ | Isolation valves for instantaneous water heater with input rating > 6.8 kBTUH or 2 kW has been specified per §110.3(c)6 | [6 empty] | << Applies to >= 1MMBtu/h if exception selected in col 05
21 | ¨ | ¨ | ¨ | School buildings < 25,000ft2 and < 4 stories must install a heat pump water heating system per §140.5(a)1. Water heating systems serving an individual bathroom space may be an instantaneous electric water heater.
Water Heating Equipment for Central Systems Serving Dwelling Units §170.2(d)2&3
Equipment Type (select all that apply):
22 | ¨ | Heat pump Water Heater (New Construction and Additions Only) | [7 empty] | S140.5(c)
|  | ¨ | For systems with single pass primary heat pump water heater, the primary thermal storage tanks shall be piped in series if multiple tanks are used. For systems with multi-pass primary heat pump water heater, the primary thermal storage tanks shall be piped in parallel if multiple tanks are used. | [7 empty] | << 90% Et applies to >= 1MMBtu/h if "Exception does not apply" selected in col 05
|  | ¨ | The primary storage tank temperature setpoint shall be at least 135°F.
|  | ¨ | The recirculation loop tank temperature setpoint shall be at least 10°F lower than the primary thermal storage tank temperature setpoint such that hot water from the recirculation loop tank is used for the temperature maintenance load before engaging the recirculation loop tank heater.
|  | ¨ | The minimum heat pump water heater compressor cut-off temperature shall be equal to or lower than 40°F ambient air temperature.
|  | ¨ | Design documentation shall specify the operating conditions at which the primary heat pump water heater can supply hot water at design outlet water temperature without engaging auxiliary heating mechanism.
| ¨ | Gas/propane water heater (New Construction and Additions Only)
|  | ¨ | A solar water-heating system meeting the installation criteria specified in Reference Residential Appendix RA4 and with a minimum solar savings fraction of 0.20 in Climate Zones 1 through 9 or a minimum solar savings fraction of 0.35 in Climate Zones 10 through 16. This system should be documented on the NRCC-SAB form OR;
|  | ¨ | A solar water-heating system meeting the installation criteria specified in Reference Residential Appendix RA4 and with a minimum solar savings fraction of 0.30 in Climate Zones 10 through 16. This system should be documented on the NRCC-SAB form. AND, a drain water heat recovery system that is field verified as specified in the Reference Appendix RA3.6.9.
| Equipment Type Dropdown for Column 08 |  | Volume Dropdown for Column 03 | Max/ FHR Dropdown (Col 04)
UEF requirements from Water Heater Efficiency Guide | Consumer Rated Gas-Fired Instantaneous (50,000-200,000 BTUH) |  | < 2 | 0 < GPM <1.7
| Consumer Rated Gas-Fired Storage (< 75,000 BTUH) |  | Volume Dropdown for Column 03 | 1.7 < GPM <2.8
| Residential-Duty Commercial Gas-Fired Storage (75,000-105,000 BTUH) |  | <30 | 2.8 < GPM < 4.0
| Consumer Rated Electric Instantaneous (<12kW) |  | 31-40 | GPM > 4.0
| Residential-Duty Commercial Electric Instantaneous (12-58.6kW) |  | 41-50 | Max/ FHR Dropdown (Col 04)
| Consumer Rated Electric Storage |  | 51-55 | 0 < FHR < 18
| Consumer Rated Electric Tabletop Water Heater |  | 56-60 | 18 < FHR < 51
| Replacement with Heat Pump Water Heater |  | 61-75 | 51 < FHR < 75
Table F-4 | Commercial Gas Storage Water Heater |  | >75 | FHR > 75
| Commercial Gas Instantaneous Water Heater |  | Volume Dropdown for Column 03
| Commercial Gas Hot Water Supply Boilers |  | <50
| Commercial Electric Storage Water Heater |  | 51-60
Table 110.2-KJ | Residential-duty Gas Hot Water Supply Boilers (<300k Btu/h) |  | 61-75
| Commercial Package Gas Hot Water Supply Boilers (300k-2.5 <1MM Btu/h) |  | >75
S140.5(c) | Commercial Package Gas Hot Water Supply Boilers (>= 1MM Btu/h) |  | Volume Dropdown for Column 03
| NA: Central Heat Pump Water Heater (See Other Table) |  | <30
>30
Replacement Heat Pump WHs
CZ | Min Req. UEF
1 | 2.82
2 | 2.82 |  | 2019 VERSION- CEC CONFIRMED NUMBERS AREN"T GOING TO CHANGE THAT WOULD IMPACT THE FORM FOR 2022.
3 | 2.82
4 | 2.87
5 | 2.82
6 | 2.47 | << triggers exceptional condition note in Table D. Table D tab row 12
7 | 2.61
8 | 2.47
9 | 2.47
10 | 2.47
11 | 2.61
12 | 2.87
13 | 2.61
14 | 2.61
15 | 2.47
16 | 3
1
Note on A3: 4.21.22: This table is being combined with the Central Systems Table below.
Note on A9: 9.3.21 Rows 9-13 COlumns 03-06 expand for user input if "Central System (serving nonresidential spaces)" OR "Central System (serving dwelling units)" is Selected in Table B column 02. Otherwise, these rows stay minimized (or we can put NA, whatever is easier.) Columns 07-15 always expand when Table F is triggered.
Note on I11: 8.31.21 Only populates if Col 05 is true equals (sum (Rated Efficiency x input capacity))/ total input capacity of water heaters > 100,000Btu/h in col 10
Note on C13: 4.21.22: Ben, opens for user input when column 08 selection is any of the following, Otherwise, grey this column out: - Gas Storage Water Heater - Gas Instantaneous Water Heater - Gas Hot Water Supply Boilers - Electric Storage Water Heater This needs to be the dropdowns from col 03 above in the Individual table when the Equipment type is one of the "Consumer Rated" choices & it needs to be a user-entry (like this original field) when the Equipment type is one of the "Commercial" choices. If we can't toggle the type of field this is, we'll need to split it into two rows and have the top be the dropdown that activates when needed and the bottom be the user-entry that activates when needed.
Note on B14: 4.21.22: Dropdown has changed for 2022 to combine all equipment types.
Note on D14: 4.21.22: This only opens if a "Commercial" equipment type is selected in Col 08, otherwise just "NA"
Note on E14: 4.21.22: This is the same dropdowns and same logic from Individual Table col 04 above. This only opens if a "Consumer Rated" equipment type is selected in Col 08, otherwise just "NA"
Note on G14: 8.31.21: Values for Table 110.2-J changed for 2022 + new efficiency req in S1405.(c) for >=1MMbtu/h, pls review table in column P Need to add the UEF values from Individual Table col 06 above when "Consumer Rated" equipment type in col 08.
Note on H14: 4.21.22: Values come from Table F-4 OR Table 110.2-KJ or S140.5(c) (see column P) depending on column 08 for any "Commerical" choices in col 08. Value is "UEF2" for any "Consumer Rated" choices in col 08.
Note on J14: Sally Blair: Ben, columns 10, 14 & 15 grey out if there is no standby loss req. in table F-4. For the equation in F-4, Q is from column 10 & Vm or Vr is from column 09.
Note on G15: 8.31.21: Adding a new system duplicates columns 03-15. Adding a Water Heater duplicated col 07-15 under the same system.
Note on I15: Sally Blair: Ben, these buttons will duplicate or remove row 12 11&14. Reset table deletes all data in row 12 11&14.
Note on A23: 9.9.21: Ben, Rows 15-25 22-33 expand for user input if "Individual Dwelling Unit System(s)" is Selected in Table B column 02. Otherwise, these rows stay minimized.
Note on C25: 2019 Logic Update: This is active for user input if "New System" is selected in Table B. Otherwise, grey out this whole row
Note on C26: Sally Blair: Ben, This is active for user input if "New System" is selected in Table B. Otherwise, grey out this whole row (& rated vol sub rows)
Note on C29: 9.9.21: This is active for user input if "New System" is selected in Table B. Otherwise, grey out this whole row & subrow Always active if this subtable is triggered.
Note on C31: 2019 Update: This is active for user input if "System Alteration" is selected in Table B. Otherwise, grey out this whole row & subrow
Note on C33: Sally Blair: Ben, This is active for user input if "Alteration" is selected in Table B. Otherwise, grey out this whole row. Also, the selection of this by the user triggers the exceptional condition note in Row 14 of Table D.
Note on C34: 9.9.21: This is active for user input if "System Alteration" is selected in Table B. Otherwise, grey out this whole row & subrow
Note on E36: Sally Blair: Ben, This is active for user input if "New Construction" is selected in Table B. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E42: Katie Gustafson: Ben, This is active for user input if "New System" is selected in Table B AND "State Building" from Table A. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E44: 8.31.21: Trigger this row if "School" is selected in A03.
Note on A46: 9.9.21: Expands for user input if "Central System (Serving Individual Dwelling Units)" is Selected in Table B column 02. Otherwise, these rows stay minimized.
Note on C48: 2019 Logic Update: This is active for user input if "New System" is selected in Table B. Otherwise, grey out this whole row
Note on C54: 2019 Logic Update: This is active for user input if "New System" is selected in Table B. Otherwise, grey out this whole row
Note on B58: 4.21.22: Combined col02 & col08 equipment type dropdowns.
Note on D58: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Gas-Fired Instantaneous -Electric Instantaneous -Residential-Duty Commercial Electric Instantaneous
Note on E58: Sally Blair: dropdown when column 02 selection is any of the following: - Gas-Fired Instantaneous - Electric Instantaneous - Residential-Duty Commercial Electric Instantaneous - Electric Tabletop
Note on D60: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Gas-Fired Storage -Electric Storage
Note on E63: Sally Blair: dropdown when column 02 selection is any of the following: - Gas-Fired Storage - Residential-Duty Commercial Gas-Fired Storage - Electric Storage
Note on B66: 4.6.22 Ben, if this is selected by the user, columns 03 & 04 grey out and column 06 is based on table below & CZ from Table A. This was in the 2016 Standards Water Efficiency Guide. It was removed for 2019 Standards.
Note on D68: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Residential-Duty Commercial Gas-Fired Storage
Note on B70: 10/23/20: When Electric Storagae Water Heater is selected in F.08, F.11 and F.12 should gray out.
Note on A71: 8.31.21: These two are the Gas Fired Hot Water Supply Boiler I've highlighted on Table 110.2-KJ.
Note on D73: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Electric Tabletop Water Heater
Note on B74: 4.12.22: Greys out col 09-15 because no efficiency requirements.

## G. Dist Syst
G. DOMESTIC HOT WATER DISTRIBUTION SYSTEM
Table Instructions: Complete the following table to demonstrate compliance for nonresidential occupancies with distribution requirements in §120.3 and §140.5. For high-rise residential multifamily and hotel/motel occupancies, compliance is demonstrated with requirements in §110.3(c), §120.3 §160.4 and §150.0 §170.2(d), §150.1.
Recirculation Loops in Central Systems Serving Dwelling Units or Nonresidential Spaces
| Yes | No | Not Applicable | Requirement
01 |  |  |  | Air release valve or verticle pump installation per §110.3(c)4A
02 |  |  |  | Check valve or similar located between recirculation pump and water heating equipment to prevent backflow per §110.3(c)4B
03 |  |  |  | Hose bibb installed between pump and equipment and isolation valve between hose bibb and equipment per §110.3(c)4C
04 |  |  |  | Isolation valves on both sides of the pump per §110.3(c)4D
05 |  |  |  | Cold water and recirculation loop piping shall not be connected to the hot water storage tank drain port per §110.3(c)4E
06 |  |  |  | Check valve installed on cold water supply between hot water system and next closest tee on cold water supply per §110.3(c)4F
07 |  |  |  | DWELLING UNITS ONLY: For central systems serving multiple dwelling units, design includes two or more a recirculation system loops serving separate dwelling units per §150.1(c)8Bii §170.2(d) unless building has < 8 dwelling units.
08 |  |  |  | DWELLING UNITS ONLY: For heat pump water heating systems, the hot water return from the recirculation loop shall connect to a recirculation loop tank and shall not directly connect to the primary heat pump water heater inlet or the primary thermal storage tanks per §170.2(d)2A.
09 |  |  |  | DWELLING UNITS ONLY: For heat pump water heating systems, the fuel source for the recirculation loop tank shall be electricity if auxiliary heating is needed. The recirculation loop heater shall be capable of multi-pass water heating operation per §170.2(d)2B.
Distribution in of Individual System(s) serving Dwelling Units
| Yes | No | Not Applicable | Requirement
08 10 |  |  |  | The dwelling unit is designed to have fenestration products with a weighted average U-factor < 0.24 plus one of the following options per §150.1(c)8Aii: (New Construction Only) Single 240 volt heat pump water heaters serving dwelling units must also include systems with:
|  |  |  | ¨ | Compact hot water distribution system field verified by a HERS Rater per as specified in Reference Appendix RA4.4.16 in climate zone 1 & 16; AND
|  |  |  | ¨ | A drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9 in climate zone 16.
09 11 |  |  |  | One of the following options is included in the design per §150.1(c)8Aiv: (New Construction Only) A drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9 in climate zone 16.
|  |  |  | ¨ | Compact hot water distribution system field verified by a HERS Rater per Reference Appendix RA4.4.6 and a drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9.
|  |  |  | ¨ | A photovoltaic system capacity of 0.3 kWdc (for climate zones 2-15) or 1.1 kWdc (for climate zones 1 & 16) larger than the requirement specified in §150.1(c)14.
10 12 |  |  |  | One of the following options is included in the design per §150.1(c)8Av: (New Construction Only) For recirculation distribution systems serving individual dwelling units, only Demand Recirculation Systems with manual on/off control as specified in the Reference Appendix RA4.4.9 shall be used.
|  |  |  | ¨ | Compact hot water distribution system per Reference Appendix RA4.4.6 for projects in climate zones 1 and 16.
|  |  |  | ¨ | A photovoltaic system capacity of 0.3 kWdc (for climate zones 1 & 16) larger than the requirement specified in §150.1(c)14.
Mandatory Pipe Insulation All Occupancies
11 13 | ¨ | For systems serving dwelling units and common areas, pipe insulation must meet the minimum insulation requirements in Table 160.4-A (see below) except: - Piping that penetrates framing members shall not be required to have pipe insulation for the distance of the framing penetration. Piping that penetrates metal framing shall use grommets, plugs, wrapping or other insulating material to assure that no contact is made with the metal framing. Insulation shall abut securely against all framing members. - Piping installed in interior or exterior walls shall not be required to have pipe insulation if all of the requirements are met for compliance with Quality Insulation Installation (QII) as specified in the Reference Residential Appendix RA3.5. - Piping surrounded with a minimum of 1 inch of wall insulation, 2 inches of crawlspace insulation, or 4 inches of attic insulation, shall not be required to have pipe insulation. for the following applications is specified to have a minimum wall thickness of 1 in or a minimum R-value of 7.7 per §150.0(j)2A: - The first 5 ft of cold water pipes from storage tank - All hot water piping with nomial diameter of 3/4 in - 1 in - All hot water piping with nomial diameter < 3/4 in associated with DHW recirculation systems - Piping with nomial diameter < 3/4 from heating source to storage tank or btween tanks - Piping with nomial diameter < 3/4 buried below grade - All hot water pipes with nomial diameter < 3/4 from heating source to kitchen fixtures | [6 empty] | << CEC, Gina is saying this exception only applies to low-rise (because QII), but the code doesn't specify that. Should we leave it in here available to Low and High-rise, even tho High-rise will likely not use it? Easier to leave it in & I think more technically correct.
12 14 | ¨ | For systems serving nonresidential spaces, pipe insulation for the following applications is specified to comply with Table 120.3-A (see below) per §120.3: - Recirculating system piping, including supply and return piping of the water heater - The first 8 ft of hot and cold outlet piping, including between storage tank and heat trap, for a nonrecirculating storage system - Pipes that are externally heated
13 15 | ¨ | Insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Insulation exposed to weather shall be installed with a cover suitable for outdoor service per §120.3(b)/ §160.4(f). and §150.0(j)3 Pipe insulation buried below grade must be installed in a water proof and non-crushable casing or sleeve.
TABLE 120.3-A/ 160.4-A PIPE INSULATION THICKNESS
Fluid Temperature Range (oF) |  | Conductivity Range (Btu-in per hour per ft2 per oF) | Insulation Mean Rating Temp (oF) |  | Nominal Pipe Diameter (in)
[5 empty] | < 1 | 1 to < 1.5 | 1.5 to < 4 | 1.5 to < 4 Multifamily & Hotel/Motel
Minimum Insulation Required
105-140 |  | 0.22-0.28 | 100 |  | 1.0 in or R-7.7 | 1.5 in or R-12.5 | 1.5 in or R-11 | 2 in or R-16
[9 empty] | 160.4 for Multifamily & hotel/motel | Note this is different than NR^^
120.3 for Nonresidential
Note on A3: 9.9.21: Ben, Rows 3-12 13 expand for user input if "Central serving dwelling units" OR "Central system (serving nonresidential spaces)" is selected in Table B column 02. Otherwise, these rows stay minimized.
Note on E11: Sally Blair: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Central serving dwelling units" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E12: 9.9.21: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Heat pump water heater" is selected in Table F column 22. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E13: 9.9.21: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Heat pump water heater" is selected in Table F column 22. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E17: 9.9.21: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if the row 19 25 on table F (< 55gal 240V HP) is marked. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E20: 9.9.21: Ben, "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if Row 21 28 on Table F (single HP water heater NEEA tier 3) is marked, and B01 s "new system" but the subrow on Row 22 is NOT. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E23: 9.9.21: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out - if Row 21 on Table F (single HP water heater) AND the subrow on Row 22 on Table F is marked. OR Otherwise, grey out this whole row & mark "Not Applicable". Always leave this row open for Y/N/NA if this subtable is triggered.
Note on C27: Sally Blair: Ben, this row is for Dwelling Units and expands for user input if "Individual Dwelling Unit System(s)" OR "Central Dwelling Units" is Selected in Table B column 02. Otherwise, it's minimized. CEC, it is unclear to me whether S160.4(f) applies to hotel/motel DHW systems as well? Please clarify. All the other dwelling unit requirments apply to H/M, but S160.4(f) says "Piping for multifamily domestic hot water systems" and does not say dwelling units. S160.4(f) applies to dwelling and common use areas and any NR occupancies in mixed-use would follow S120.3?
Note on C28: Sally Blair: Ben, this row is for nonresidential Systems and expands for user input if "Central System (serving nonresidential spaces)" OR "Individual System (serving nonresidential spaces)" is Selected in Table B column 02. Otherwise, it's minimized.

## H. Controls
H. DOMESTIC HOT WATER SYSTEM CONTROLS
Table Instructions: Complete the following table to demonstrate compliance with controls requirements in §110.3 for all occupancies. For high-rise multifamily residential and hotel/motel occupancies, compliance is demonstrated with requirements in §160.4(e) and §150.1(c)8 §170.2(d).
| Yes | No | Not Applicable | Requirement
01 | ¨ | ¨ | ¨ | Construction documents require manufacturer certification that service water-heating systems are equipped with automatic temperature controls capable of adjusting temperature settings per §110.3(a).
02 | ¨ | ¨ | ¨ | Systems with capacity > 167,000 BTUH equipped with outlet temperature controls per §110.3(c)1 unless covered by California Plumbing Code Section 613.0.
03 | ¨ | ¨ | ¨ | Controls for circulating pumps or electrical heat trace systems are capable of automatically turning off the system per §110.3(c)2 unless system serves healthcare facility.
04 | ¨ | ¨ | ¨ | For recirculation systems serving multiple dwelling units, design includes automatic pump controls per §150.1(c)8Bii §170.2(d), or §150.2 §180.1(b)3 for additions or alterations.
05 | ¨ | ¨ | ¨ | For recirculation systems serving individual dwelling units, design includes manual on/off controls as specified in Reference Appendix RA 4.4.9 per §150.1(c)8 §170.2(d).
06 | ¨ | ¨ | ¨ | For replacement single heat pump water heaters serving individual dwelling units in climate zones 1-15, design includes communication interface that meets demand responsive control requirements of §110.12(a) per §150.2(b)1Hiii.
06 | ¨ | ¨ | ¨ | Combustion air positive shut-off shall be provided per §160.4(e) on all newly installed commercial boilers as follows: - Boiler with input capacity >= 2.5 MMBtu/h, in which the boiler is designed to operate with a nonpositive vent static pressure - Boilers where one stack serves two or more boilers with a total combined input capacity per stack of 2.5 MMBtu/h.
07 | ¨ | ¨ | ¨ | Boiler combustion air fans with motors >= 10 hp shall meet one of the following for newly installed boilers: - The fan motor shall be driven by a variable speed drive OR - The fan motor shall include controls that limit the fan motor demand to <= 30% of the total design wattage at 50% of the design air volume.
08 | ¨ | ¨ | ¨ | Newly installed boilers with an input capacity >= 5 MMbtu/h and a steady state full-load combustion efficiency < 90% shall maintain excess (stack-gas) oxygen concentrations <= 5% by volume on a dry basis over firing rates of 20-100%. Combustion air volume shall be controlled with respect to firing rate or flue gas oxygen concentration. Use of a common gas and combustion air control linkage or jack shaft is prohibited.
Note on E4: Sally Blair: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Central system (serving nonresidential space)" OR "Individual System (serving nonresidential spaces)" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E7: Sally Blair: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Central serving dwelling units" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E8: Sally Blair: "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Individual Dwelling Units" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E9: 9.1.21 "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if Row 23 on Table F (single HP water heater) is marked, but the subrow on Row 24 is NOT. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E10: 9.1.21: This is triggered if "mutifamily" is selected in A03 CEC, does this also apply for "hotel/motel"?
Note on E11: 9.1.21: This is triggered if "mutifamily" is selected in A03
Note on E12: 9.1.21: This is triggered if "mutifamily" is selected in A03

## I. NRCI
I. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Nonresidential, Hotel/Motel, and High-rise Multifamily and Multifamily Mixed-use Certificates of Installation
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
n |  | NRCI-PLB-01-E - Must be submitted for all buildings
¨ | n | NRCI-PLB-02 21-E HERS - Must be submitted for high-rise residential and hotel/ motel central hot water distribution systems to be recognized for compliance.
¨ | n | NRCI-PLB-03 22-E HERS - Must be submitted for high-rise residential and hotel/ motel single dwelling unit hot water distribution systems to be recognized for compliance.
CEC, It looks like we didn't totally think this through for 2019 & these two NRCIs should not be listed here since they are related to HERS compliance options for the performance path only & therefore would not be triggered for prescriptive compliance. Please let me know if I'm misunderstanding or we need to do something different.
Note on B5: 9.9.21: Need to replace w updated URL
Note on C9: 9.9.21: NRCI-PLB-02 21 move to "Yes" if either "High-rise Residential" OR "Hotel/Motel" from Table A. AND "Central System" in Table B02 are selected. Otherwise, stays as "No". NRCI-PLB-03 22 move to "Yes" if either "High-rise Residential" OR "Hotel/Motel" from Table A. AND "Individual Dwelling Unit System" in Table B02 are selected. Otherwise, stays as "No".

## I. LMCI
I. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Low-rise Multifamily and Multifamily Mixed-use Certificates of Installation
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
n |  | LMCI-PLB-01-E - Must be submitted for all buildings
Note on B4: 9.10.21: This subtable is triggered if the "MF <= 3 stories" is selected in A03
Note on B5: 9.9.21: Need to replace w updated URL

## J. NRCA
J. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
There are no Certificates of Acceptance applicable to service water heating requirements.
CEC to confirm still no NRCA for PLB

## K. NRCV
K. DECLARATION OF REQUIRED CERTIFICATES OF VERIFICATION
Nonresidential, Hotel/Motel, and High-rise Multifamily and Multifamily Mixed-use Certificates of Verification
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ There are no Certificates of Verification for nonresidential, hotel/motel, high-rise multifamily and mixed-use buildings complying prescriptively.
YES | NO | Form/Title | Systems To Be Field Verified | Field Inspector
|  |  |  | Pass | Fail
m | m | NRCV-PLB-21-H High-rise Residential Central Hot Water Distribution HERS Verification |  | o | o
m | m | NRCV-PLB-22-H High-rise Residential Individual Dwelling Unit Hot Water Distribution HERS Verification |  | o | o
CEC, It looks like we didn't totally think this through for 2019 & these two NRCVs should not be listed here since they are related to HERS compliance options for the performance path only & therefore would not be triggered for prescriptive compliance. Please let me know if I'm misunderstanding or we need to do something different.
Note on B4: 9.9.21: Trigger this subtable if EITHER "High-rise Residential" OR "Hotel/Motel" from Table A.
Note on C8: Sally Blair: Starts as "No", moves to "Yes" if "Central System (serving dwelling units)" is selected in Table B column 02.
Note on C9: Sally Blair: Starts as "No", moves to "Yes" if "Individual Dwelling Unit System(s)" is selected in Table B column 02.

## K. LMCV
I. DECLARATION OF REQUIRED CERTIFICATES OF VERIFICATION
Low-rise Multifamily and Multifamily Mixed-use Certificates of Verification
There are no Certificates of Verification for low-rise multifamily and mixed-use buildings complying prescriptively.
CEC, Since the LMCVs are all related to HERS compliance options, I've put in that there are none. Please let me know if I'm misunderstanding or we need to do something different.
Note on B4: 9.10.21: This subtable is triggered if the "MF <= 3 stories" is selected in A03

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/ HERS Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Designer Name: | Responsible Designer Signature:
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-PLB form.
?