## New Table Sequence
Label | Table Title | Trigger within:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Refrigerated Warehouses | Table B
Table G | Commercial Refrigeration | Table B
Table H | Enclosed Parking Garage Exhaust | Table B
Table I | Process Boilers | Table B
Table J | Compressed Air Systems | Table B
Table K | Elevators | Table B
Table L | Escalators and Moving Walkway Controls | Table B
Table M | Computer Room Equipment | Table B
Table N | Commercial Kitchen Ventilation | Table B
Table O | Laboratory Exhaust | Table B
Table P | Controlled Environment Horticulture | Table B
Table Q | Steam Traps | Table B
Table R | Pool/ Spas | Table B
Table P S | Declaration of Required Certificates of Installation | ALWAYS
Table Q T | Declaration of Required Certificates of Acceptance | ALWAYS
| Signature Page | ALWAYS

## Code References
Section
§120.6 | Header, B, C, F
140.9 | Header, B, C
120.6(a) | B, C
120.6(b)
120.6(c)
120.6(d)/(e)
120.6(f)/(g)
140.9(a) | B, C
140.9(b)
140.9(c)
TABLE 120.6-A | F
120.6(a)2 | F
§120.6(a)3A | F
§120.6(a)3B | F
§120.6(a)3C | F
§120.6(a)4D/E | F
§120.6(a)4B | F
§120.6(a)4G | F
§120.6(a)5A/B/C | F
§120.6(a)6 | F
120.6(f)2
120.6(f)3
160.7

## NRCC Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Process Systems
NRCC-PRC-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-PRC-E
Table Instructions: Include This form is used to document any process systems that are within the scope of the permit application and are demonstrating compliance with mandatory requirements in §120.6/ §160.7, or prescriptive requirements in §140.9. This compliance document is used for newly constructed, addition and alteration projects.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
The project name and date prepared is a user input on the first page, but will populate the heading on all other pages.
STATE OF CALIFORNIA
Process Systems
NRCC-PRC-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-PRC-E
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
Footer on all pages:
CA Building Energy Efficiency Standards - 201922 Nonresidential Compliance: http://www.energy.ca.gov/title24/201922standards
First Page Heading
Heading for all other pages

## LMCC Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Process Systems
LMCC-PRC-01-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | LMCC-PRC-01-E
Table Instructions: Include This form is used to document any process systems that are within the scope of the permit application and are demonstrating compliance with mandatory requirements in §120.6/ §160.7, or prescriptive requirements in §140.9. This compliance document is used for newly constructed, addition and alteration projects.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
The project name and date prepared is a user input on the first page, but will populate the heading on all other pages.
STATE OF CALIFORNIA
Process Systems
LMCC-PRC-01-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | LMCC-PRC-01-E
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
Footer on all pages:
CA Building Energy Efficiency Standards - 201922 Nonresidential Low-rise Multifamily/Mixed-use Compliance: http://www.energy.ca.gov/title24/201922standards
First Page Heading
Heading for all other pages

## NRCC A. General Info
|  | User input | auto calculated |  |  |  | From another Table |  |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  | 04 | Total Conditioned Floor Area
02 | Climate Zone |  | Dropdown |  | 05 | Total Unconditioned Floor Area
03 | Occupancy Types Within Project: |  |  |  | 06 | # of Stories (Habitable Above Grade)
¨ | Office |  | ¨ | Retail | ¨ | Non-refrigerated Warehouse |  | ¨ | Grocery
¨ | Hotel/ Motel |  | ¨ | School or Classroom | ¨ | Healthcare facility |  | ¨ | Financial Institution
¨ | High-Rise Residential |  | ¨ | Relocatable Class Bldg Public School | ¨ | All Other Occupancy Types (Write In) |  | ¨ | Unleased Tenant Space
¨ | Auditorium |  | ¨ | Library | ¨ | Restaurant |  | ¨ | Parking Garage
¨ | Convention Center |  | ¨ | Medical Office Bldg/ Clinic | ¨ | Theater |  | ¨ | Religious Facility
¨ | Commercial Industrial |  | ¨ | Data Center | ¨ | Gymnasium |  | ¨ | Support Area
Alert! Healthcare Facilities do not have to meet the elevator, computer room, commercial kitchen, or lab exhaust requirements under Title 24, Part 6 and therefore are not documented on the NRCC-PRC-E. The corresponding tables (K,M,N,O) say "This section does not apply" when healthcare facility has been chosen as an occupancy within Table A. Systems serving these spaces shall meet the requirements of the Appliance Efficiency Regulations for walk-in coolers or freezers contained in the Appliance Efficiency Regulations (California Code of Regulations, Title 20, Sections 1601 through 1608).
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on B6: 11.23.21: Only the occupancy types selected by the user will display on the form with a checked box. Occupancy types not selected will not show.
Note on H8: 11.21.21: When A.03 = "Healthcare Facility" then Tables K,M,N,O do not trigger and say "This section does not apply" This overrides any other trigger logic for these Tables
Note on B13: 2019 Updates: This note is triggered when A.03 = "healthcare facility"

## LMCC A. General Info
|  | User input | auto calculated |  |  |  | From another Table |  |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  | 04 | Total Conditioned Floor Area
02 | Climate Zone |  | Dropdown |  | 05 | Total Unconditioned Floor Area
03 | Occupancy Types Within Project: |  |  |  | 06 | # of Stories (Habitable Above Grade)
¨ | Office |  | ¨ | Retail | ¨ | Non-refrigerated Warehouse |  | ¨ | Grocery
¨ | Hotel/ Motel |  | ¨ | School or Classroom | ¨ | Healthcare facility |  | ¨ | Financial Institution
¨ | High Low-Rise Residential |  | ¨ | Relocatable Class Bldg Public School | ¨ | All Other Occupancy Types (Write In) |  | ¨ | Unleased Tenant Space
¨ | Auditorium |  | ¨ | Library | ¨ | Restaurant |  | ¨ | Parking Garage
¨ | Convention Center |  | ¨ | Medical Office Bldg/ Clinic | ¨ | Theater |  | ¨ | Religious Facility
¨ | Commercial Industrial |  | ¨ | Data Center | ¨ | Gymnasium |  | ¨ | Support Area
Alert! Healthcare Facilities do not have to meet the elevator, computer room, commercial kitchen, or lab exhaust requirements under Title 24, Part 6 and therefore are not documented on the NRCC-PRC-E. The corresponding tables (K,M,N,O) say "This section does not apply" when healthcare facility has been chosen as an occupancy within Table A. Systems serving these spaces shall meet the requirements of the Appliance Efficiency Regulations for walk-in coolers or freezers contained in the Appliance Efficiency Regulations (California Code of Regulations, Title 20, Sections 1601 through 1608).
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on B6: 11.23.21: Only the occupancy types selected by the user will display on the form with a checked box. Occupancy types not selected will not show.
Note on H8: 11.21.21: When A.03 = "Healthcare Facility" then Tables K,M,N,O do not trigger and say "This section does not apply" This overrides any other trigger logic for these Tables
Note on B13: 2019 Updates: This note is triggered when A.03 = "healthcare facility"

## NRCC B. Project Scope
|  | User input |  | auto calculated | From another Table | From look up table
B. PROJECT SCOPE
This table includes proccess systems that are within the scope of the permit application and are demonstrating compliance with mandatory requirements in §120.6/§160.7 or prescriptive requirements in §140.9.
My project consists of (check all that apply):
01 |  | 02
¨ | Refrigerated Spaces <3,000 ft2 Total (no Title 24, Pt 6 requirements) | ¨ | Escalator & Moving Walkway Speed Controls (mandatory §120.6(g))
¨ | Refrigerated Spaces >=3,000 ft2 Total (mandatory §120.6(a)) | ¨ | Controlled Environment Horticulture (mandatory §120.6(h))1
¨ | Food/Beverage Stores > 8,000ft2 cfa (mandatory §120.6(b)) | ¨ | New Steam Traps (mandatory §120.6(i))
¨ | Enclosed Parking Garage Exhaust >= 10,000 cfm (mandatory §120.6(c)) | ¨ | Computer Rooms > 20 W/ft2 Power Density (mandatory §120.6(j) & prescriptive §140.9(a))1
¨ | Newly Installed Process Boilers (mandatory §120.6(d)) | ¨ | Commercial Kitchen Ventilation/Exhaust (prescriptive §140.9(b))1
¨ | Compressed Air Systems Combined HP >= 25 (mandatory §120.6(e)) | ¨ | Laboratory Exhaust/Factory Exhuast & Fume Hood (prescriptive §140.9(c))1
¨ | Elevator Lighting & Ventilation Controls (mandatory §120.6(f)/§160.7) | ¨ | Pool/Spa (mandatory §110.4/§160.7)
1 FOOTNOTE: These building features can comply using the performance method. If using the performance method for these features, compliance should be demonstrated on the NRCC-PRF-E compliance document.
Alert! Refrigerated Warehouses and refrigerated spaces that are less than 3,000 square feet do not have requirements under Title 24, Part 6 and therefore are not documented on the NRCC-PRC-E. Systems serving these spaces shall meet the requirements of the Appliance Efficiency Regulations for walk-in coolers or freezers contained in the Appliance Efficiency Regulations (California Code of Regulations, Title 20, Sections 1601 through 1608).
Note on A5: Sally Blair: Selections made here trigger the corresponding Tables in the form.
Note on B7: Katie Gustafson: Triggers Note in row 16 below

## LMCC B. Project Scope
|  | User input |  | auto calculated | From another Table | From look up table
B. PROJECT SCOPE
This table includes proccess systems that are within the scope of the permit application and are demonstrating compliance with mandatory requirements in §120.6/§160.7 for multifamily occupancies or prescriptive requirements in §140.9 for nonersidential occupancies in mixed-use buildings.
My project consists of (check all that apply):
01 |  | 02
¨ | Refrigerated Spaces <3,000 ft2 Total (no Title 24, Pt 6 requirements) | ¨ | Escalator & Moving Walkway Speed Controls (mandatory §120.6(g))
¨ | Refrigerated Spaces >=3,000 ft2 Total (mandatory §120.6(a)) | ¨ | Controlled Environment Horticulture (mandatory §120.6(h))1
¨ | Food/Beverage Stores > 8,000ft2 cfa (mandatory §120.6(b)) | ¨ | New Steam Traps (mandatory §120.6(i))
¨ | Enclosed Parking Garage Exhaust >= 10,000 cfm (mandatory §120.6(c)) | ¨ | Computer Rooms > 20 W/ft2 Power Density (mandatory §120.6(j) & prescriptive §140.9(a))1
¨ | Newly Installed Process Boilers (mandatory §120.6(d)) | ¨ | Commercial Kitchen Ventilation/Exhaust (prescriptive §140.9(b))1
¨ | Compressed Air Systems Combined HP >= 25 (mandatory §120.6(e)) | ¨ | Laboratory Exhaust/Factory Exhuast & Fume Hood (prescriptive §140.9(c))1
¨ | Elevator Lighting & Ventilation Controls (mandatory §120.6(f)/§160.7) | ¨ | Pool/Spa (mandatory §110.4/§160.7)
1 FOOTNOTE: These building features can comply using the performance method. If using the performance method for these features, compliance should be demonstrated on the NRLMCC-PRF-E compliance document.
Alert! Refrigerated Warehouses and refrigerated spaces that are less than 3,000 square feet do not have requirements under Title 24, Part 6 and therefore are not documented on the NRCC-PRC-E. Systems serving these spaces shall meet the requirements of the Appliance Efficiency Regulations for walk-in coolers or freezers contained in the Appliance Efficiency Regulations (California Code of Regulations, Title 20, Sections 1601 through 1608).
Note on A5: Sally Blair: Selections made here trigger the corresponding Tables in the form.
Note on B7: Katie Gustafson: Triggers Note in row 16 below

## C. Compliance
|  | auto calculated |  | From another Table |  | From look up table |  | From look up table
C. COMPLIANCE RESULTS
Results in this table are automatically calculated from data input and calculations in Tables F through OR. Note: If any cell on this table says "COMPLIES with Exceptional Conditions" refer to Table D. Exceptional Conditions for guidance or see the applicable Table referenced below.
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 11 14
Refrigerated Warehouse/ Space §120.6(a) | Commercial Refrigeration §120.6(b) | Parking Garage Exhaust §120.6(c) | Process Boilers §120.6(d) | Compressed Air Systems §120.6(e) | Elevators §120.6(f)/ §160.7 | Escalators & Moving Walkways §120.6(g) | Computer Rooms §140.9(a) | Commercial Kitchens §140.9(b) | Laboratory/Factory Exhaust §140.9(c) | Controlled Environment Horticulture §120.6(h) | Steam Traps §120.6(i) | Multifamily Pool/Spa §160.7 | Compliance Results
(See Table F) | (See Table G) | (See Table H) | (See Table I) | (See Table J) | (See Table K) | (See Table L) | (See Table M) | (See Table N) | (See Table O) | (See Table P) | (See Table Q) | (See Table R)
Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | Yes/No | COMPLIES or "COMPLIES WITH EXCEPTIONAL CONDITIONS" or DOES NOT COMPLY
Note on A6: 2019 Updates: If any of 01-10 13 corresponding tables do not expand and instead say this section does not apply then the corresponding column in table C should be blank and grey.
Note on N7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will the processes not included in the LMCC version be greyed out or just not show up at all? Reply: My plan is they would just be greyed out because they wouldn't apply.
Note on A9: 11.23.21 Says "Yes" if: - Ext. Surface Ins subtable col 01 checked AND - Underslab Heating subtable all fields completed AND - Fan Power Evap subtable all fields completed which aren't grey AND - Condensers subtable 01 completed + Air-cooled Cond. all columns 11 say "Yes" if triggered + Water/Evap Cond. all col 10 say "Yes" if triggered + Adiabatic Cond. all col 09 say "Yes" if triggered AND - Compressors subtable 01 completed & 02-05 completed if expanded AND - Infiltration Barrier subtable 01 & 02 -03 completed AND - Transcritical CO2 Gas Cooler subtable 01 completed + all columns 09 say "Yes" if triggered
Note on B9: 11.23.21 Says "Yes" if: - 01 completed AND - Condensers subtable 01 OR 02 checked OR all column 11 say "yes" if subtable applies AND - Compressor & Cond. Units subtable 01 checked OR 02-04 05 completed if subtable applies AND - Refrigerated Display Cases subtable 02 OR 03 checked if subtable applies AND - Heat Recovery Subtable 01 checked OR 02 completed if subtable applies AND - Transcritical CO2 Gas Cooler subtable 01 completed + all columns 09 say "Yes" if triggered Otherwise says "No"
Note on C9: 2019 Update: 03 says "Yes" if - EITHER 01 OR 02 = "yes" OR - 3-9 are completed and 14 says "complies" for ALL fans added to Table H. Otherwise 03 says "No"
Note on D9: Sally Blair: Says "Yes" if: - 01-05 completed if not grey
Note on E9: 11.21.21: Says "Yes" if: - 01-03 07 completed
Note on F9: 2019 Updates: Updated 6/23/20 06 says "Yes" if - sum of column 06 <= sum of column 07 AND - EITHER 10 = "Yes" OR 13<=14 AND - everything not grey is completed Otherwise 06 says "no"
Note on G9: Sally Blair: Says "Yes" if: - 01 completed
Note on H9: 11.21.21: Says "Yes" if: In HVAC subtable - 01-09 completed if not grey AND - 06 <= 07 AND In UPS Subtable - 02 completed AND - 06>=05 if not grey
Note on I9: 2019 Update: Updated 3.1.21 09 says "yes" if - kitchen ventilation 01 is checked OR -02,03,05 have been completed AND kitchen exhuast 01 -07 have been completed if not grey, AND 07<=08 if 08 not grey Otherwise says no
Note on J9: 2019 Update: Says "Yes" if columns 01-05 are completed if table is triggered. Otherwise says "No"
Note on K9: 11.23.21: Says "Yes" if - HVAC Subtable columns 01-02 are completed AND - Ltg Subtable 01-06 complete if not grey AND - Env Subtable 01-04 complete if not grey Otherwise says "No"
Note on L9: 11.23.21: Says "Yes" if columns 01-03 are completed if table is triggered. Otherwise says "No"
Note on M9: 11.23.21: Says "Yes" if columns 01-08 are completed AND 09-15 completed if triggered. Otherwise says "No"
Note on N9: Sally Blair: 1. Says "COMPLIES" if no other cells in row 9 say "No" & no exceptional conditions have been triggered in Table D. 2. Says "COMPLIES WITH EXCEPTIONAL CONDITIONS" if no other cells in row 9 say "No" & an exceptional conditioned has been triggered in Table D. 3. Says "DOES NOT COMPLY" if one of the cells in row 9 says "No"

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Table M indicates a computational fluid dynamics (CFD) analysis was performed to meet computer room containment requirements in §140.9(a)6. Authority Having Jurisdiction may ask for calculations to confirm compliance at their discretion.
Table K indicates one or more elevators which have designed lighting power greater than the Maximum Power Allowed. Please revise Table K to demonstrate compliance.
Table K indicates one or more elevators which have designed ventilation Watts/cfm greater than the maximum Watts/cfm allowed. Please revise Table K to demonstrate compliance.
Selections made in Table P S have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination.
Selections made in Table Q T have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination.

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## F. Refrigerated Warehouse
|  |  |  | User input |  |  | auto calculated |  | From another Table |  | From look up table
F. REFRIGERATED WAREHOUSES/SPACES
This table includes all refrigerated warehouses > 3,000ft2 and refrigerated spaces with a sum total of > 3,000 ft2 served by the same refrigeration system. The inputs within Table F are used to demonstrate compliance with the requirements of §120.6(a).
Warehouse Exterior Surface Insulation | [5 empty] | << ALWAYS OPEN WHEN TABLE F IS TRIGGERED
01 | ¨ | Exterior surfaces of refrigerated warehouses/spaces are specified to be insulated at least to the R-values in TABLE 120.6-A (see below) per §120.6:
TABLE 120.6-A REFRIGERATED WAREHOUSE/SPACE INSULATION
Space |  |  | Surface |  | Minimum R-Value
Freezers |  |  | Roof/ Ceiling |  | 40
|  |  | Wall |  | 36
|  |  | Floor |  | 35
|  |  | Floor with all heating from productive refrigeration capacity1 |  | 20
Coolers |  |  | Roof/ Ceiling |  | 28
|  |  | Wall |  | 28
1 FOOTNOTE: All underslab heating is provided by a heat exchanger that provides refrigerant subcooling or other means that result in productive refrigeration capacity on the associated refrigerated system.
Underslab Heating | [6 empty] | << ALWAYS OPEN WHEN TABLE F IS TRIGGERED
01 | 02
Room ID/ Description | Compliance Method §120.6(a)2
Dropdown
|  |  |  | Reset | Add Room | Remove Last
Method Dropdown
Using electric resistance with thermostatic control to be off during summer on-peak time periods.
NA: not using electric resistance heat for underslab heating
NA: no underslab heating
Fan Powered Evaporators | [11 empty] | << ALWAYS OPEN WHEN TABLE F IS TRIGGERED
01 | 02 | 03 |  | 04 |  | 05 |  |  | 06
Name or Item Tag | Fan Motor Efficiency §120.6(a)3A |  |  |  |  | Fan Controls §120.6(a)3B & §120.6(a)3C
| HP | Phase |  | Type or Efficiency |  | Evaporator Fans Served By |  |  | Compliance Method
| Dropdown | Dropdown |  | Dropdown |  | Dropdown |  |  | Dropdown
| Motor HP | Phase |  | Type or Efficiency |  | Fans Served By |  |  | Fan Controls
| <1 HP | Single Phase < 460V |  | ECM |  | Suction group with multiple compressors |  |  | Variable Speed based on Temp
| >= 1 HP | Three Phase |  | >=70% Efficiency |  | Single compressor with variable capacity capability |  |  | Variable Speed based on Humidity
[6 empty] | Single compressor without variable capacity |  |  | Fan Controls
[6 empty] | NA: Not alterating/replacing all of the evaporators in an existing refrigerated space that do not have fan speed-controls. |  |  | Reduce airflow ≥ 40 % for ≥ 75% of time when compressor is not running.
NA: Products stored require constant operation at 100 % of the design airflow certified by licensed engineer.
NA: Areas designed solely for quick chilling/freezing of products.
Condensers | [9 empty] | << ALWAYS OPEN WHEN TABLE F IS TRIGGERED
01 | Indicate condenser types included in the project:1 |  |  | ¨ Air-Cooled (new only) | ¨ Evaporative-cooled (new only) | ¨ Water-cooled (new only) | ¨ Adiabatic (new only) | ¨ Altered/replacement or existing condensers only
1 FOOTNOTE: Altered/replacement or existing condensers do not have Title 24, Part 6 requirements.
Air-Cooled Condensers
02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Name or Item Tag | Condenser Location | Variable Speed Control §120.6(a)4D | Temp Setpoint Controls §120.6(a)4E | Design Condensing Temperatures §120.6(a)4B | Condenser Efficiency §120.6(a)4G |  |  | Fin Density §120.6(a)4H | Complies?
[5 empty] | Refrigerant Type | Minimum Efficiency Required (Btuh/W) | Efficiency per Design (Btuh/W)
| Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | lookup |  | Dropdown | Yes/ No
[8 empty] | Add Condenser | Remove Last
| Condenser Location | VS Dropdown | Temp Setpoint Control dropdown | Design Temp dropdown | Refrig type dropdown |  |  | Fin Density dropdown
| Indoor | Variable speed fan(s) provided controlled per §120.6(a)4D | Designed to <= 70 @ ambient db temp | Designed per §120.6(a)4B | Ammonia |  |  | <= 10 fins/in
| Outdoor | NA: Transcritical CO2 refrigeration | NA: Transcritical CO2 refrigeration | NA: Total HP < 100 | Halocarbon |  |  | NA: Using microchannel condenser
|  |  |  | NA: > 20% for quick chilling/freezing or cooling another refrigerated space | NA: Transcritical CO2 refrigeration
NA: Transcritical CO2 refrigeration
Water-Cooled and Evaporative-Cooled Condensers
02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Name or Item Tag | Condenser Location | Variable Speed Control §120.6(a)4D | Temp Setpoint Controls §120.6(a)4E | Design Condensing Temperatures §120.6(a)4A | Condenser Efficiency §120.6(a)4G |  |  | Complies?
[5 empty] | THR Capacity | Minimum Efficiency Required (Btuh/W) | Efficiency per Design (Btuh/W)
| Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | lookup |  | Yes/ No
[7 empty] | Add Condenser | Remove Last
| Condenser Location | VS Dropdown | Temp Setpoint Control dropdown | Design Temp dropdown | THR Cap dropdown
| Indoor | Variable speed fan(s) provided controlled per §120.6(a)4D | Designed to <= 70 @ ambient wb temp | Designed per §120.6(a)4A | > 8,000 MBH
| Outdoor | NA: Transcritical CO2 refrigeration | NA: Transcritical CO2 refrigeration | NA: > 20% for quick chilling/freezing or cooling another refrigerated space | < 8,000 MBH
|  |  |  | NA: Transcritical CO2 refrigeration | NA: Transcritical CO2 refrigeration
Adiabatic Condensers
02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Name or Item Tag | Variable Speed Control §120.6(a)4D | Temp Setpoint Controls §120.6(a)4E | Design Condensing Temperatures §120.6(a)4C | Condenser Efficiency §120.6(a)4G |  |  | Complies?
|  |  |  | Refrigerant Type | Minimum Efficiency Required (Btuh/W) | Efficiency per Design (Btuh/W)
| Dropdown | Dropdown | Dropdown | Dropdown | lookup |  | Yes/ No
[6 empty] | Add Condenser | Remove Last
| VS Dropdown | Temp Setpoint Control dropdown | Design Temp dropdown | Refrig type dropdown
| Variable speed fan(s) provided controlled per §120.6(a)4D | Designed to <= 70 @ ambient db temp | Designed per §120.6(a)4C | Ammonia
| NA: Transcritical CO2 refrigeration | NA: Transcritical CO2 refrigeration | NA: > 20% for quick chilling/freezing or cooling another refrigerated space | Halocarbon
|  |  | NA: Transcritical CO2 refrigeration | NA: Transcritical CO2 refrigeration
Compressors | [6 empty] | << ALWAYS OPEN WHEN TABLE F IS TRIGGERED
01 | Indicate compressor types included in the project:1 |  |  | ¨ Compressor (new only) | o Altered or existing compressors only
02 |  | 03 | 04 |  |  | 05
Name or Item Tag |  | Design Condensing Temp §120.6(a)5A&B | Variable Speed Control §120.6(a)5BC |  |  | Variable Volume Ratio §120.6(a)5CD
|  | Dropdown | Dropdown |  |  | Dropdown
1 FOOTNOTE: Altered/replacement or existing compressors do not have Title 24, Part 6 requirements. |  |  |  |  | Add Compressor | Remove Last
|  | Cond Temp Dropdown | VS Control |  |  | Var Vol Ratio dropdown
|  | Min condensing temp <=70 deg | Controls compressor speed in response to refrigeration load |  |  | Auto vary volume ratio in response to operating pressure
|  | Transcritical CO2 w SST < 30deg: Min condensing temp <= 60 deg | NA: Not new open-drive screw compressor w SST <= 28deg |  |  | NA: Not screw compressor w > 150 HP motor
NA: > 1 dedicated compressor per suction group
NA: > 20% for quick chilling/freezing or cooling another refrigerated space
Infiltration Barriers and Automatic Door Closers | [6 empty] | << ALWAYS OPEN WHEN TABLE F IS TRIGGERED
01 | 02 |  |  | 03
Room ID/ Description | Infiltration Compliance Method §120.6(a)6 |  |  | Door Closure Compliance Method §120.6(a)9
| Dropdown |  |  | Dropdown
|  |  |  | Reset | Add Room | Remove Last
| Infiltration Method Dropdown |  |  | Door Closure Method Dropdown
| Passageway between freezers and non-refrigerated spaces shall include infiltration barriers per §120.6(a)6 |  |  | Passageway between freezers & higher temp. spaces/ coolers and non-refrigerated spaces shall include automatic door closures per §120.6(a)9
| NA: openings < 16ft2 |  |  | NA: Room doesn't include people passageways between freezers/ higher temp./coolers/non-refrigerated spaces
NA: Dock doorway for trailers
NA: Room doesn't include passageways between freezers and non-refrigerated spaces
THIS ENTIRE SUBTABLE IS NEW FOR 2022
Transcritical CO2 Fan-powered Gas Coolers | [9 empty] | << ALWAYS OPEN WHEN TABLE F IS TRIGGERED
01 | Indicate gas cooler types included in the project:1 |  |  | ¨ Air-cooled (new only) | ¨ Adiabatic (new only) | ¨ Altered/replacement or existing gas coolers only |  | ¨ No Transcritical CO2 refrigeration/ no fan-powered gas coolers
1 FOOTNOTE: Altered/replacement or existing gas-coolers do not have Title 24, Part 6 requirements.
Alert! Air-cooled gas coolers are prohibited in climate zones 9-15 per §120.6(a)8A.
02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Name or Item Tag | Design Leaving Gas Temperature §120.6(a)8B&C | Variable Speed Control §120.6(a)8D | Gas Cooler Pressure Controls §120.6(a)8E&F | Design Condensing Temperatures §120.6(a)8G | Condenser Efficiency §120.6(a)8H |  | Complies?
[5 empty] | Minimum Efficiency Required (Btuh/W) | Efficiency per Design (Btuh/W)
| Dropdown | Dropdown | Dropdown | Dropdown | lookup |  | Yes/ No
[6 empty] | Add Gas Cooler | Remove Last
| Gas Temp | VS Dropdown | Pressure Control dropdown | Design Temp dropdown
| Designed per §120.6(a)8B or C | Variable speed fan(s) provided controlled per §120.6(a)8D | Condensing temp reset per §120.6(a)4F and cooler pressure setpoint maximizes efficiency | Min condensing temp <=70 60 deg
Transcritical CO2 w SST < 30deg: Min condensing temp <= 60 70 deg
Note on J36: Sally Blair: Gray out column 06 if any "NA" choices selected in column 05
Note on J38: Sally Blair: Custom dropdown if Suction Group or Single w variable capacity chosen in column 05.
Note on B40: Sally Blair: 03-04 Greyed out if >1hp
Note on C40: Sally Blair: 04 Greyed out if Three Phase is selected
Note on J41: Sally Blair: Custom dropdown if Single w/o variable capacity chosen in column 05.
Note on F48: Sally Blair: These selections expand appropriate sub sections. Altered box doesn't open anything.
Note on G54: Sally Blair: 75 if outdoor in column 03 & ammonia in column 07. 65 if outdoor in column 03 & halocarbon in column 07.
Note on J54: Sally Blair: If all columns which are not grey are completed & column 09 per design >= column 08
Note on B57: Sally Blair: greys out columns 07-09
Note on F59: 2019 Update: Greys out columns 08-09
Note on G65: Sally Blair: = 350 if outdoor in column 03 & > 8,000 in column 07. = 160 if outdoor in column 03 & <8,000 in column 07. = 160 if indoor in column 03
Note on I65: Sally Blair: If all columns which are not grey are completed & column 09 per design >= column 08
Note on B68: Sally Blair: if selected, column 07 greys out
Note on F70: 2019 Update: Greys out columns 08-09
Note on F76: Sally Blair: 45 if halocarbon in column 06.
Note on H76: Sally Blair: If all columns which are not grey are completed & column 08 per design >= column 07
Note on E79: 2019 Update: Greys out columns 07-08
Note on E81: 2019 Update: Greys out columns 07-08
Note on E85: Sally Blair: This selection expands rows below for user input.
Note on F85: Ben Lalor: This selection 02-05 = blank/grayed out
Note on E113: 11.14.21: Triggers "Alert!.." note if checked AND A03 = CZ 9-15
Note on F113: 11.14.21: Both "Air-cooled" and "Adiabatic" choices trigger columns 02-09
Note on G113: 11.14.21: Both "Altered/replacement…" and "No Transcritical CO2…" checkboxes do not expand any more rows in this subtable (but footnote still shows)
Note on F119: 11.14.21: If "Air-cooled" in col01, this = 160 If "Adiabatic" in col01, this = 90
Note on H119: Sally Blair: Says "Yes" If all columns are completed & column 08 per design >= column 07 Else says "No"

## G. Commercial Refrig
G. COMMERCIAL REFRIGERATION | [9 empty] | << Rows 2-4 are open when Table G is triggered.
This table includes all refrigeration equipment being utilized for refrigerated display cases or walk in coolers/freezers, located in a retail food/beverage store with 8,000 ft or more of conditioned floor area. The inputs within Table G are used to demonstrate compliance with the requirements of §120.6(b).
01 | Indicate components of the refrigeration system included in the project: |  |  |  | ¨ Condensers | ¨ Compressors | ¨ Refrigerated Display Cases |  | ¨ Heat Recovery
Condensers Serving Refrigeration System
01 | ¨ | The project includes replacement condensers that meet the following conditions: - attached compressor system Total Heat of Rejection does not increase and; - less than 25 percent of both the attached compressors and the attached display cases are new.
02 | ¨ | All equipment, appliances and components serving the refrigeration system have been certified by the Energy Commission as compliant with Title 20 and listed in the Modernized Appliance Efficiency Database System.1
03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Name or Item Tag | Condenser Type | Variable Speed Control §120.6(b)1A | Temp Setpoint Controls §120.6(b)1B, C, D, F | Condenser Specific Efficiency §120.6(b)1G |  |  | Fin Density §120.6(b)1H | Complies?
|  |  |  | Specific Efficiency Compliance Method | Minimum Specific Efficiency Required (Btuh/W) | Specific Efficiency per Design (Btuh/W)
| Dropdown | Dropdown | Dropdown | Dropdown | 65 if aircooled in col 02; 160 if evap cooled; 45 if adiabatic |  |  | Yes/ No
1 FOOTNOTE: Compliant equipment may be found in the Modernized Appliance Efficiency Database System (MAEDbS) on the Energy Commission website: https://cacertappliances.energy.ca.gov/Pages/Search/AdvancedSearch.aspx | [5 empty] | Reset | Add Condenser | Remove Last
| Condenser Type | VS Dropdown | Temp Setpoint Control dropdown | Exceptions dropdown |  |  | Fin Density dropdown
| Air Cooled | Variable speed fan(s) provided controlled per §120.6(b)1A | Air cooled: designed to <= 70 @ ambient db temp | No exceptions apply |  |  | <= 10 fins/in
| Evaporative Cooled |  | Evap cooled: designed to <= 70 @ ambient wb temp | NA: Total Heat Rejection Capacity <150kBtuh |  |  | NA: Using microchannel condenser
| Adiabatic |  | Adiabatic: designed to < 70 @ ambient db temp | NA: Located in CZ 1 |  |  | NA: Existing condenser being reused
|  |  | NA: Adiabatic in Climate Zone 16 | NA: Existing condenser being reused
|  |  | NA: Transcritical CO2 refrigeration | NA: Transcritical CO2 refrigeration
Compressors and Condensing Units Serving Refrigeration System
01 | ¨ | All compressors being used for the refrigeration system are being reused.
02 |  | 03 |  |  | 04 | 05
Name or Item Tag |  | Saturation suction temperature control (SST) §120.6(b)2A |  |  | Liquid Subcooling Compliance Method §120.6(b)2B | Transcritical CO2 Min Condensing Temp §120.6(b)2C
|  | Dropdown |  |  | Dropdown | Dropdown
[5 empty] | Add Compressor | Remove Last
|  | Saturation Suction Temperature Control |  |  | Compliance Method Dropdown | Condensing Temp Dropdown
|  | Floating suction pressure logic used to reset target SST |  |  | No exceptions apply | Min condensing temp <=60 deg
|  | NA: Single compressor system with no variable capacity capability |  |  | NA: Design cooling <100kBtuh per §120.6(b)2B | SST < 30deg: Min condensing temp <= 70 deg
|  | NA: Suction group with design SST >= 30°F |  |  | NA: Cascade system per Exception §120.6(b)2B | NA: Not Transcritical CO2
|  | NA: Suction group comprises of the high stage of a two-stage or a cascade system |  |  | NA: Not low temp compressor
|  | NA: Suction group serves the secondary cooling fluid chiller |  |  | NA: Transcritical CO2 refrigeration
Refrigerated Display Cases
01 | Design includes lighting controls for refrigerated display cases including illuminated glass doors of walk-in coolers/freezers per §120.6(b)3. Select method(s) being utilized below:
02 | o | Timeclock: Turn off lighting power automatically during non-business hours
03 | ¨ | Motion Sensor: Reduce lighting power by at least 50% within 30 minutes after the nearby area is vacated
Heat Recovery of Refrigeration System
01 | ¨ | All HVAC/ refrigeration systems are being reused.
02
Compliance Method1 §120.6(b)4
Dropdown
1 FOOTNOTE: Authority Having Jurisdiction may ask for calculations to confirm compliance.
Method Dropdown
Heat recovery provided using 25% or more of Total Heat of Rejection and will not increase HFC refrigerant charge more than 0.35 lb/kBtuh of heat recovery heating capacity per §120.6(b)4
NA: No individual refrigeration systems > 150kBtuh
NA: Located in CZ 15
NA: Stores where the design Total Heat of Rejection of all refrigeration systems is less than or equal to 500,000 Btu/h.
THIS ENTIRE SUBTABLE IS NEW FOR 2022
Transcritical CO2 Fan-powered Gas Coolers | [9 empty] | << ALWAYS OPEN WHEN TABLE G IS TRIGGERED
01 | Indicate gas cooler types included in the project:1 |  |  | ¨ Air-cooled (new only) | ¨ Adiabatic (new only) | ¨ Altered/replacement or existing gas coolers only |  | ¨ No Transcritical CO2 refrigeration/ no fan-powered gas coolers
1 FOOTNOTE: Altered/replacement or existing gas-coolers do not have Title 24, Part 6 requirements.
Alert! Air-cooled gas coolers are prohibited in climate zones 10-15 per §120.6(b)5A.
02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Name or Item Tag | Design Leaving Gas Temperature §120.6(b)5B&C | Variable Speed Control §120.6(b)5D | Gas Cooler Pressure Controls §120.6(b)5E&F | Design Condensing Temperatures §120.6(b)5G | Condenser Efficiency §120.6(b)5H |  | Complies?
[5 empty] | Minimum Efficiency Required (Btuh/W) | Efficiency per Design (Btuh/W)
| Dropdown | Dropdown | Dropdown | Dropdown | lookup |  | Yes/ No
[6 empty] | Add Gas Cooler | Remove Last
| Gas Temp | VS Dropdown | Pressure Control dropdown | Design Temp dropdown
| Designed per §120.6(b)5B or C | Variable speed fan(s) provided controlled per §120.6(b)5D | Condensing temp reset per §120.6(b)1A and cooler pressure setpoint maximizes efficiency | Min condensing temp <=60 deg
Transcritical CO2 w SST < 30deg: Min condensing temp <= 70 deg
Note on G4: Sally Blair: These selections expand appropriate sub sections.
Note on B6: Sally Blair: If checked, columns 03-11 grey out.
Note on B7: 2019 Update: If checked, columns 03-11 grey out.
Note on H11: Sally Blair: greys out if col 04 = evap cooled OR Adiabatic
Note on I11: Sally Blair: If all columns which are not grey are completed & column 09 >= column 08
Note on E15: Sally Blair This selection or one of the two below greys out column 08-09
Note on B22: Sally Blair: If checked, columns 02-04 grey out.
Note on B47: Sally Blair: If checked, column 02 greys out.
Note on E63: 11.14.21: Triggers "Alert!.." note if checked AND A03 = CZ 10-15 NOTE: In Table F, the CZ is 9-15, here it's 10-15
Note on F63: 11.14.21: Both "Air-cooled" and "Adiabatic" choices trigger columns 02-09
Note on G63: 11.14.21: Both "Altered/replacement…" and "No Transcritical CO2…" checkboxes do not expand any more rows in this subtable (but footnote still shows)
Note on F69: 11.14.21: If "Air-cooled" in col01, this = 160 If "Adiabatic" in col01, this = 90
Note on H69: Sally Blair: Says "Yes" If all columns are completed & column 08 per design >= column 07 Else says "No"

## H. Garage Exhaust
[5 empty] | User input |  | auto calculated | From another Table | From look up table
H. ENCLOSED PARKING GARAGE EXHAUST
This table includes all newly installed mechanical ventilation systems which serve parking garages and have a design exhuast rate greater than or equal to 10,000 cfm. The inputs of Table H are used to demonstrate compliance with the requirments of §120.6(c).
| Yes | Exceptions
01 | ¨ | Garage is expected to have vehicles with non-gasoline combustion engines for > 20% of the parked vehicles per Exception 1 to §120.6(c)
02 | ¨ | Project scope includes an addition or alteration to an existing garage where < 10,000 cfm of new exhaust capacity is being added Exception 2 to §120.6(c)
| Yes | Requirements
03 | ¨ | Exhaust fan control modulates airflow rates <= 50% design capacity when contaminant levels are maintained per §120.6(c)1
04 | ¨ | Fan control or device allows fan motor demand ≤ 30% design wattages at 50% of design airflow per §120.6(c)2
05 | ¨ | Design includes monitoring CO with a sensor density >= 1 per 5,000 ft2 per §120.6(c)3
06 | ¨ | CO sensors are located in the highest expected concentration locations, with at least two per proximity zone per §120.6(c)3
07 | ¨ | Design CO sensor setpoint <= 25 ppm per §120.6(c)4
08 | ¨ | Occupied garage design maintains negative pressurization per §120.6(c)6
09 | ¨ | Designed occupied total ventilation rate >= 0.15 CFM/ ft2 §120.6(c)5
|  | 10 | 11 | 12 | 13 | 14
|  | Fan Name | Parking Garage Area (ft2) | Ventilation Fan Rate (CFM) | Minimum Ventilation Rate Required (CFM) | Compliant?
[5 empty] | 0 | Yes/No
[5 empty] | Add Ventilation Fan | Remove Last
15 | Indicate where in the construction documents these requirements can be verified
Note on B7: 2019 Updates: If Yes is checked in 01 or 02 then row 3-13 grey out
Note on H18: Sally Blair: "Yes" if column 12>= column 13
Note on G19: Sally Blair: would duplicate user input rows on row 18

## I. Process Boiler
|  | User input |  |  | auto calculated | From another Table | From look up table
I. PROCESS BOILER
This table includes all process boilers within the the scope of the permit application to demonstrate compliance with the requirements of §120.6(d).
01 | 02 | 03 | 04 | 05
Name or Item Tag | Rated Input Capacity per Boiler (Btu/h) | Combustion Air Shutoff §120.6(d)1 | Fan Controls §120.6(d)2 | Stack Design and Controls §120.6(d)3 & §120.6(d)4
| Dropdown | Dropdown | Dropdown | Dropdown
|  |  | Add Boiler | Remove Last
| Input Capacity | Combustion shut-off dropdown | Control Type | Control Type
| < 2.5 MMBtuh per boiler | Combustion air positive shut-off provided | Variable speed drive provided | Designed and controlled per §120.6(d)
| >= 2.5 to <5 MMBtuh per boiler | NA: combined rated input of all boilers per stack < 2.5 MMBtuh | Controls limit fan motor demand to <= 30% of the total design wattage at 50% of design air volume provided | NA: Steady state full-load combustion efficiency >=90%
| >= 5 to <10 MMBtuh per boiler |  | NA: Combustion air fan < 10 HP
>= 10 MMBtuh per boiler
Note on C13: Sally Blair: If selected, columns 04 & 05 grey out
Note on B14: 11.14.21: This and > 10 MMBtuh selection opens column 05, otherwise greys out

## J. Compressed Air
|  | User input |  |  | auto calculated |  | From another Table | From look up table
J. COMPRESSED AIR SYSTEMS
This table includes all new or altered compressed air systems with a combined HP of 25 or greater. The inputs within Table J are used to demonstrate compliance with the requirements of §120.6(e).
01 | 02 | 03 | 04 | 05 | 06 | 07
System Name/ Description | Trim Compressor Compliance Method §120.6(e)1 | Controls §120.6(e)2 | Monitoring §120.6(e)3 | Compressed Air Piping > 50 Adjoining ft in Length §120.6(e)5
|  |  |  | Service Line Size1 | Section Average Velocity | Total Pressure Drop
| Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
1 FOOTNOTE: Service line piping are pipes that deliver compressed air from distribution piping to end uses. |  |  |  |  | Add System | Remove Last
| Trim Compressor Dropdown | Controls Dropdown | Monitoring Dropdown | Line Size Dropdown | Avg Velocity Dropdown | Pressure Dropdown
| Variable Speed Drive Compressor provided per §120.6(e)1A | Design includes sensor/controllor capable of using most efficient combination of compressors to meet load | Includes monitoring, data logging/storage and display system for pressure, amps/power, airflow per §120.6(e)3. | Inner diameter >= 3/4 in | Inerconnection/main header piping <= 20fps and distribution piping <= 30 fps. | Frictional pressure loss < 5% operating pressure per §120.6(e)5C
| Dedicated trim compressor provided per §120.6(e)1B | NA: Do not have > 1 3 compressors online | NA: < 100 combined HP rating | NA: Adjoining length <= 50ft
| NA: Not adding or replacing > 50% of online system capacity | NA: < 100 combined HP rating
| NA: Medical gas serving Healthcare facility | NA: Medical gas serving Healthcare facility
NA: Alt. where total added/replaced compressor hp < avg. per compressor hp of all compressors in system
NA: Alt. where added/replaced compressors are VSD & system includes primary storage >= 1g/acfm of largest trim compressor
NA: Alt. of system that includes >= 1 centrifugal compressor

## K. Elevator
|  | User input |  |  | auto calculated |  | From another Table | From look up table
K. ELEVATOR LIGHTING AND VENTILATION
This table includes all elevator lighting and ventilation systems within the scope of the permit application to show compliance with the requirements of §120.6(f)/ §160.7.
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Lighting §120.6(f)1 & §120.6(f)3 / §160.7
Elevator Name or Item Tag | Elevator Area (ft2) | Fixture Name or Item Tag | Watts per Fixture | Number of Fixtures | Power per Design (W) | Maximum Power Allowed1 (W) | Controls
[5 empty] | (equals 04*05) | = '0.6*B8 | Dropdown
[5 empty] | (equals 04*05) | (grey and blank) | Dropdown
|  | Total Design Watts |  |  | (= sum of column 06) | (= sum of column 07)
[5 empty] | Add Fixture | Remove Last Fixture
09 | 10 | 11 | 12 | 13 | 14 | 15
Name or Item Tag | Conditioned Cab? | Ventilation §120.6(f)2 & §120.6(f)3/ §160.7 |  |  |  |  | Controls
|  | Fan Power (Watts) | Design Airflow (CFM) | Design Watts per CFM | Maximum Watts per CFM Allowed | Controls | Occupancy sensors provided
pull from 01 | Dropdown |  |  | #DIV/0! | 0.33 | Dropdown
1 FOOTNOTE: 0.6 watts per ft2 allowed per §120.6(f)1. Interior signal lighting and display lighting not included in power density calculation. |  |  |  |  | Add Elevator | Remove Last
16 | Indicate where in the construction documents these requirements can be verified
Occupancy sensors provided
Occupancy sensors provided
| Conditioned Drpdn |  |  |  |  | Controls
| Yes |  |  |  |  | Occupancy sensors provided
No
Note on G8: Sally Blair: If 07<06 trigger note in Table D row 9.
Note on G9: October 2019 Update: When the "Add Fixture" button is used the "maxiumum power allowed" cell in the added row should be gray with no value. The sum of the "maximum power allowed" should match the value in the first row of K.07
Note on F11: 2019 Update: ability to add (and remove) multiple fixtures incase elevator has more than one fixture type. Table can now expand columns 2-7 and sum up columns 5 and 6
Note on A15: Ben Lalor: Should pull elevator ID not fixture ID
Note on F15: Sally Blair: If 14<13 trigger note in Table D row 10.
Note on F16: Sally Blair: Duplicates columns 01-08 and 09-15
Note on B30: Sally Blair: grey out columns 11-15 if selected.

## L. Escalator
| User input | auto calculated | From another Table | From look up table
L. ESCALATORS AND MOVING WALKWAYS SPEED CONTROLS
This table includes all escalators and moving walkway controls neccesary to demonstrate compliance with the requirements of §120.6(g).
01
Compliance Method §120.6(g)
Dropdown
Method Dropdown
Escalators and moving walkways are designed to automatically slow when not conveying passengers per §120.6(g).
NA: Project does not include an airport, hotel, or transportation function area.

## M. Computer Room
| User input |  | auto calculated | [6 empty] | From another Table | From look up table
M. COMPUTER ROOM SYSTEM SUMMARY
This table contains all computer room systems with power density greater than 20 W/ft^2 to demonstrate compliance with mandatory requirements of §120.6(j) and the prescriptive requirments of §140.9(a). Prescriptive requirements only apply to computer rooms with a power density greater than 20 W/ft2.
Computer Room HVAC
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Computer Room Name/ ID | Economizer Compliance Method §140.9(a)1 | Reheat §140.9(a)2 §120.6(j)1 | Humidification §140.9(a)3 §120.6(j)2 | Fan Power §140.9(a)4 2 |  |  | Fan Controls §140.9(a)5 §120.6(j)3 | Air Containment §140.9(a)6 3
|  |  |  | Sensible Cooling Capacity1 (kBtuh) | Total Fan System Power per Design (Watts) | Maximum Fan System Power Allowed (Watts)
| Dropdown | Dropdown | Dropdown |  |  | 0 | Dropdown | Dropdown
1 FOOTNOTE: Refers to net sensible cooling capacity at design conditions. | [6 empty] | Add Computer Room | Remove Last
| Economizer Compliance Method | Reheat | Humidification |  |  |  | Fan Controls | Containment
| Integrated air economizer designed to partial cooling and provide 100% of cooling load @ OSA 55 65deg db and below 50deg wb and below & includes FDD per §120.2(i) | Zone controls designed provided to prevent reheat | None Provided |  |  |  | Variable airflow controls/ devices provided per §140.9(a)5 §120.6(j)3 | Air barrier provided per §140.9(a)6 3
| Integrated water economizer designed to partial cooling and provide 100% of cooling load @ OSA 40 50deg db and 35 45deg wb and below |  | Adiabatic system (non-adiabatic not allowed) |  |  |  | NA: Not Unitary AC System > 60kBtuh or CHW Fan System | NA: Not air-cooled computers where ITE process design load > 175 10 kW per room
| NA: Computer room ITE design load < 5 tons & building HVAC does not have any economizers | [6 empty] | NA: Expansion of existing computer rooms
| NA: New cooling systems serving an existing computer room in an existing building up to a total of 50 tons of new cooling equipment per building | [6 empty] | NA: Computer racks with a design load less than 1 kW/rack
| NA: New cooling systems serving a new computer room in an existing building up to a total of 20 tons of new cooling equipment per building. | [6 empty] | NA: Equivalent energy performance based on computational fluid dynamics or other analysis. | << triggers exceptional condition to provide analysis See Table D row 8
| NA: A computer room being served by a fan system (not economizer) meeting the requirements of Exception 4 2 to §140.9(a)1. | [6 empty] | NA: Rm power density <= 20 W/ft2
NA: Rm power density <= 20 W/ft2
THIS ENTIRE SUBTABLE IS NEW FOR 2022
Computer Room Uniterruptible Power Supply (UPS)
01 | 02 | 03 | 04 | 05 | 06
Computer Room Name/ ID | Alternating Current Output UPS Compliance Method §140.9(a)4 | Type of UPS | UPS Rated Output Power (W) | Minimum Efficiency Required Table 140.9-B | Design Efficiency Specified
From Computer Rm HVAC col01 above | Dropdown | Dropdown
|  |  |  | Add UPS | Remove Last
| UPS Compliance Method | Type Dropdown
| Systems meet or exceed min efficiency per Table 140.9-B | Voltage & Frequency Dependent
| NA: Rm power density <= 20 W/ft2 | Voltage Independent
| NA: UPS utilizes standardized NEMA 1-15P or NEMA 5-15P input plug | Voltage & Frequency Independent
Note on C13: Sally Blair: Diane, IDK if this was picked up in 2019 or if it is because of NRCI. Pls check schema.
Note on B19: 11.20.21: Greys out columns 05-07
Note on A26: GINA: Could there be more than one UPS per room? Do we need the ability to add UPSs to a room? GR: I really have no idea, but it would be better to allow the to add different systems. Think we should also let them provide information if more than one of the same type (multiples)
Note on E27: 11.21.21: Equation depends on col03 & col04. See Table 140.9-B to right for equation. EMOD = 0.004 always Note "ln" is just the log of Power in col04. So if ln is in the equation, it just mathmatically = "log(col04)"
Note on F27: 11.21.21: Both col05 & col06 should be rounded to the third decimal place for compliance evaluation & reporting.
Note on B32: 11.20.21: Both NA options grey out columns 03-06

## N. Commercial Kitchen
0 | User input |  |  |  |  | auto calculated |  |  | From another Table | From look up table
N. COMMERCIAL KITCHEN EXHAUST AND VENTILATION
This table contains all new or replacement hoods being installed within the scope of the permit application. The inputs within Table N are used to demonstrate compliacne within §140.9(b).
Kitchen Ventilation §140.9(b)2
01 | ¨ | Existing kitchen hoods not being replaced as part of an addition or alteration (do not need to meet requirements) | [6 empty] | << Greys out entire table
Requirements
02 | Replacement Air to Hood Compliance Method §140.9(b)1A
Dropdown
03 | Mechanically cooled or heated makeup air delivered to any space with a kitchen hood is designed per 140.9(b)2A to not exceed the greater of:
Dropdown
04 | Location that is supplying transfer air:
05 | The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and is designed to have one of the following per 140.9(b)2B:
Dropdown
Kitchen Exhaust: Airflow Rate §140.9(b)1B
01 | Kitchen Name or Tag |  | Compliance Method per §140.9(b)1B |  |  | Dropdown
02 | 03 | 04 | 05 | 06 | 07 | 08
Name or Item Tag | Hood Type1 | Hood Style | Hood Length (ft) | Equipment Duty | Design Hood Exhaust Rate CFM | Max Hood Exhaust Rate Allowed CFM
| Dropdown | Dropdown |  | Dropdown
<< Example of add hood button
[7 empty] | Add Hood | Remove Last
1 FOOTNOTE: Type II hoods do not have a max hood exhaust air rate per Part 6 §140.9(b)1B. | [6 empty] | Add Kitchen | Remove Last
Equipment Duty
Light Duty
| Hood Type | Hood Style |  | Medium Duty
| Type I | Wall-mounted Canopy |  | Heavy Duty |  | Compliance Method Dropdown 01
| Type II | Single Island |  | Extra Heavy Duty |  | Type I hood design exhaust rates do not exceed the maximum allowed per §140.9(b)1 as documented below.
|  | Double Island |  |  |  | NA: Kitchen/ dining facility has a total Type I and Type II hood exhaust rate < 5,000 cfm.
|  | Eyebrow |  | Equipment Duty |  | NA: 75% of the total Type I and Type II exhaust replacement air is transfer air that would otherwise be exhausted.
|  | Backshelf / Passover |  | Light Duty |  | NA: Existing hoods are being replaced as part of an addition or alteration.
Medium Duty
Equipment Duty
Light Duty
Medium Duty
Heavy Duty
N.02 Compliance Method Dropdown
Providing replacement air directly to the hood(s) that does not exceed 10% of the hood(s) exhaust rate.
Not providing replacement air directly to the hood(s)
N.03 Dropdown
The supply flow required to meet the space heating and cooling load
The hood exhaust flow minus the available transfer air from adjacent spaces.
NA: Make up air is not mechanically cooled or heated
N.05 Dropdown
At least 50% of all replacement air is transferred air that would otherwise be exhausted
Demand ventilation system(s) on at least 75% of the exhaust air per 140.9(b)2Bii
Listed energy recovery devices with a sensible heat recovery effectiveness of > 40 on at least 50% of the total exhaust airflow
A minimum of 75% of makeup air volume having a total of no more than 60°F and uncooled or cooled without the use of mechanical cooling
NA: Not a kitchen /dining facility having a total Type I and Type II kitchen hood exhaust airflow rate > 5,000 cfm
Note on A4: 2019 Updates: 6.9.20 Update: keeping Kitchen Exhaust Section initially triggered with Table N. When Table N is triggered only N.01,02,03,05 and the kitchen exhaust section are initially triggered. N.04 is triggered through the choices made in this table.
Note on C7: 2019 Updates: When user selects 01, the rest of the table should grey out, all requirements are NA
Note on A17: 2019 Updates: Triggers only when 03 = "not exceed the hood exhaust flow minus the available transfer air…"
Note on G28: 11.21.21: See Table 140.9-A C for rate, then multiply by column 05.
Note on H31: Ben Lalor: ability to add a kitchen, instead of just adding a new row like the add hood button, add kitchen would replicate 01-08 and add hood remove hood buttons, only one set of add kitchen buttons should stay with the top kitchen.
Note on E32: Sally Blair: Custom drropdown for the following selections in column 04: - Wall Mounted Canopy - Single Island - Double Island
Note on B36: Sally Blair: This selection should grey out columns 04-06 & 08
Note on G37: Sally Blair: All 3 of these "NA" options should grey out columns 04-06 & 08
Note on E38: Sally Blair: Custom drropdown for the following selections in column 04: - Eyebrow
Note on E42: Sally Blair: Custom drropdown for the following selections in column 04: - Backshelf/ Passover

## O. Lab Exhaust
|  | User input | auto calculated |  | From another Table
O. LABORATORY AND FACTORY EXHAUST AND FUME HOODS
This table includes all laboratory and factory exhaust and fume hoods within the scope of the permit application. The inputs within Table O are used to demonstrate compliance with the requirements within §140.9(c). Licensed Healthcare facilities are exempt from these requirements.
01 | 02 |  | 03 | 04 | 05
Zone/System or Item Tag | Airflow Reduction Compliance Method §140.9(c)1 |  | Transfer Air Compliance Method §140.9(c)2 | Fan Power Compliance Method §140.9(c)3 | Hood Sash Closure Compliance Method §140.9(c)4
| Dropdown |  | Dropdown | Dropdown | Dropdown
Dropdown
|  |  | Reset | Add Zone/System | Remove Last
| Airflow Reduction Method Dropdown |  | Transfer Air Method Dropdown | Fan Power Upper Dropdown | Hood Sash Dropdown
| Exhaust airflow capable of reducing exhaust and make-up air to min circulation/pressurization rate |  | Conditioned supply air delivered to any space with mechanical exhaust is designed per §140.4(o) | System meets discharge requirements in ANSI Z9.5-2012 | Hood sash closure system design controlled per §140.9(c)4
| NA: Constant volume system required by AHJ or Environmental, Health & Safety |  | NA: Laboratory is classified as biosafety level >= 3 | NA: Newly installed exhaust system <= 10,000 cfm | NA: Not VAV hood with vertical sashes in hood intensive lab
| NA: New zones on an existing constant volume system |  | NA: Serving vivarium space
| NA: Systems designed for > 10 ACH |  | NA: Space required to be at positive pressure
|  |  | NA: Space required to be at negative pressure and where highest amount of transfer air used for make-up exceeds available transfer airflow rate | Fan Power Lower Dropdown
Max 0.85 W/cfm for systems with air treatment (filters, etc.)
Max 0.65 W/cfm for systems without air treatment
Volume flowrate @ stack controlled by anemometer per §140.9(c)3C
Volume flowrate @ stack controlled by contaminant sensor per §140.9(c)3D
NA: Newly installed exhaust system <= 10,000 cfm

## P. CEH
| User input |  | auto calculated |  |  |  | From another Table | From look up table
THIS ENTIRE TABLE IS NEW FOR 2022
P. CONTROLLED ENVIRONMENT HORTICULTURE
This table documents compliance with mandatory controlled environment horticulture requirments of §120.6(h).
Space Conditioning for Plant Production §120.6(h)1 and 5 |  |  | << Subtable always triggered with Table P.
01 | 02 | 03
System Name/ Description | Dehumidification System for Indoor Grow CEH Compliance Method §120.6(h)1 | HVAC System Compliance Method §120.6(h)5
| Dropdown | Dropdown
| Dehumid Compliance Method | HVAC Compliance Method
| Dehumidifiers regulated by Federal Appliance Standards | HVAC Systems comply via Performance Path and are documented on NRCC-PRF-E document.
| HVAC has onsite heat recovery for >=75% of dehumidification reheat | HVAC Systems comply via Prescriptive Path and are documented on NRCC-MCH-E document.
| CHW system has onsite heat recovery for >=75% of dehumidification reheat | NA: No HVAC system for CEH
Dessicant dehumidification for dewpoint <= 50degF
NA: No dehumidification systems or Greenhouse
Lighting and Electrical Systems §120.6(h)2, 3 and 6 | [5 empty] | << Subtable always triggered with Table P.
01 | 02 | 03 | 04 | 05 | 06
System Name/ Description | Indoor or Greenhouse Space | Photosynthetic Photon Efficacy (PPE) §120.6(h)2A & 6A | Lighting Controls §120.6(h)2B&C and 6B&C |  | Electrical System Monitoring Capability §120.6(h)3
|  |  | Timeswitch | Multilevel
| Dropdown | Dropdown |  |  | Dropdown
|  |  |  | Add System | Remove Last
| Space | PPE Dropdown if "Indoor" in col02 | Timeswitch | Multilevel | EPD Monitoring Dropdown
| System serves indoor horticulture | System PPE ANSI/ASABE S640 rated for wavelengths 400-700 nanometers AND integrated, non-serviceable luminaire PPE >= 1.9 micromoles per joule | EMCS | Dimmer | Electrical system designed for capability to monitor electrical energy usage of horticulture lighting load
| System serves greenhouse horticulture | System PPE ANSI/ASABE S640 rated for wavelengths 400-700 nanometers AND serviceable lamp PPE >= 1.9 micromoles per joule | Autotimeswitch | Multilevel Switching
| NA: System has < 40kW of aggregate horticulture lighting load |  | Countdown timer
PPE Dropdown if "Greenhouse" in col02
System PPE ANSI/ASABE S640 rated for wavelengths 400-700 nanometers AND integrated, non-serviceable luminaire PPE >= 1.7 micromoles per joule
System PPE ANSI/ASABE S640 rated for wavelengths 400-700 nanometers AND serviceable lamp PPE >= 1.7 micromoles per joule
Opaque and Non-Opaque Envelopes |  |  |  | << Subtable always triggered if Table P triggered.
This table documents mandatory requirements for envelope assemblies in conditioned greenhouses. Envelope assemblies in Indoor Grow Facilities should be documented on the NRCC-ENV for prescriptive compliance or NRCC-PRF for performance compliance.
01 | 02 | 03 | 04
Tag/Plan Detail ID | Assembly Type | Non-Opaque Envelope Compliance Method §120.6(h)4B | Opaque Envelope Compliance Method §120.6(h)4A
| Dropdown | Dropdown | Dropdown
| Aeembly Type Dropdown | NOE Compliance Method | OE Compliance Method
| Opaque Roof | Has >= 2 glazings separated by air or gas | Envelope complying via Performance Path and is documented on NRCC-PRF-E document.
| Opaque Wall |  | Envelope complying via Prescriptive Path and is documented on NRCC-ENV-E document.
Non-opaque envelope
Note on B30: 11.14.21: Greys outcolumns 03-06
Note on D39: CEC: I was conflicted about what to do here. If we document this on the PRC, we would have to copy all the tables for Roof and Wall Assemblies, including all the JA4 & weighted-area stuff from the ENV here & that feels silly. It also feels silly to have this stuff on the PRC, because if the PE is plan checking ENV, it should all be together on the PRF or ENV. So this is what I'm proposing, similar to HVAC systems above. I'd have to check with Nikhil to make sure CBECC can handle CEH space types with the mandatory value backstop (I think there is already a mandatory backstop in CBECC, so won't be a big deal.) Do you think this is reasonable?
Note on B44: 11.20.21: Both Opaque Roof and Opaque Wall selections grey out col03
Note on B46: 11.20.21: selection greys out col04

## Q. Steam Trap
| User input |  | auto calculated | From another Table | From look up table
THIS ENTIRE TABLE IS NEW FOR 2022
Q. STEAM TRAPS IN INDUSTRIAL FACILITIES
This table documents compliance with mandatory steam trap requirements of §120.6(i). Steam traps with operating pressure greater than 15 psig and a total combined connected boiler input rating greater than 5 Million Btu/hr shall meet the requirements. Steam trap replacements or steam traps added to support replacement process equipment do not have requirements under Title 24, Part 6 and are not included in the table below.
01 | 02 | 03
Fault Detection Diagnostics Monitoring |  | Strainer Installation
Update Interval | Alarm Display
Dropdown | Dropdown | Dropdown
Interval Dropdown | Alarm Dropdown | Strainer Dropdown
Status updates at <= 8 hr intervals | Alarm displays which steam trap has fault | Steam traps are equipped with an integral strainer and blow-off valve
NA: Steam is diverted to a steam system of lower pressure for use when the steam trap fails open. | NA: Steam is diverted to a steam system of lower pressure for use when the steam trap fails open. | Steam traps are installed downstream within 3 ft of a strainer and blow-off valve
NA: Steam is diverted to a steam system of lower pressure for use when the steam trap fails open.

## R. PoolSpa
| User input |  | auto calculated |  |  |  | From another Table | From look up table
THIS ENTIRE TABLE IS NEW FOR 2022
R. POOL & SPAs
This table documents compliance with mandatory pool/spa requirments in §110.4/§160.7.
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Pool/ Spa Description | Pool/Spa Service Type | Efficiency1 | On/Off Control | Instructions & Covers | Electric Resistance Heating | Piping | Pool Directional Inlets & Pump Control
| Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
1 FOOTNOTE: CEC's appliance efficiency database, the Modernized Appliance Efficiency Database System (MAEDBS), is available online at https://cacertappliances.energy.ca.gov/Pages/ApplianceSearch.aspx.
| Type Dropdown | Efficiency dropdown | Control Dropdown | Cover Dropdown | Elec Resistance Dropdown | Piping Dropdown | Inlet Dropdown
| Serves multiple tenants or public | Equipment subject to State/federal appliance efficiency standards is in the CEC's directory of certified equipment | Includes on-off switch mounted on outside of heater allowing shutting off heater without adjusting thermostat | Heated outdoor pools/spas must include cover and weatherproof instruction for proper care of when cover is used | No electric resistance heating used | >= 36 in of pipe installed between filter & heater or dedicated suction and return lines to allow for the future addition of solar heating equipment | Has directional inlets to mix the pool water & control mechanism to allow pumps to run only during off-peak electric demand period and for min time necessary
| Serves one tenant |  |  | NA: Pool/spa not heated | Listed package units with fully insulated enclosures, and with tight-fitting covers that are insulated to at least R-6 | Built-in/built-up connections installed to allow for future addition of solar heating equipment | NA: Spa
Pools/spas where >= 60% of annual heating energy is from site solar energy or recovered energy
Additional Requirements for Pool/ Spa Serving One Tenant §150.0(p)
| Yes | Not Applicable | Requirement
09 | ¨ |  | All pump flow rates shall be calculated using H = C × F2 WHERE: H is the total system head in feet of water F is the flow rate in gallons per minute (gpm) C is a coefficient based on the volume of the pool (0.0167 for pools less than or equal to 17,000 gallons & 0.0082 for pools greater than 17,000 gallons)
10 | ¨ |  | Filtration pumps shall be sized, or if programmable, shall be programmed, so that the filtration flow rate is not greater than the rate needed to turn over the pool water volume in 6 hours or 36 gpm, whichever is greater.
11 | ¨ |  | Pump motors used for filtration shall meet the applicable federal standard in 10 CFR 431.465.
12 | ¨ | ¨ | Each auxiliary pool load shall be served by either separate pumps or the system shall be served by a multispeed pump if pump hp >= 1. - Multispeed pumps shall have controls which default to the filtration flow rate when no auxiliary pool loads are operating; and - For multispeed pumps, the controls shall default to the filtration flow rate setting within 24 hours and shall have an override capability for servicing.
13 | ¨ |  | System Piping must meet the following requirements: - A length of straight pipe that is greater than or equal to at least 4 pipe diameters shall be installed before the pump; and - Pool piping shall be sized so that the velocity of the water at maximum flow for auxiliary pool loads does not exceed 8 feet per second in the return line and 6 feet per second in the suction line; and - All elbows shall be sweep elbows or of an elbow-type that has a pressure drop of less than the pressure drop of straight pipe with a length of 30 pipe diameters.
14 | ¨ |  | Filters shall be at least the size specified in NSF/ANSI 50 for public pool intended applications.
15 | ¨ |  | Minimum diameter of backwash valves shall be 2 inches or the diameter of the return pipe, whichever is greater.
Note on B12: 11.21.21: Triggers "Additional Requirements…" subtable below.

## S. NRCI
| User input |  |  | auto calculated |  | From another Table | From look up table
P S. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ |  |  |  |  | fds
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | NRCI-PRC-01-E Covered Process | o | o
Note on A4: Sally Blair: Need to update URL when available
Note on A7: Sally Blair: this defaults to "Yes" and if the user moves it, the note in Table D row 11 shows up.

## S. LMCI
| User input |  |  | auto calculated |  | From another Table | From look up table
P S. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ |  |  |  |  | fds
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | LMCI-PRC-01-E Covered Process | o | o
Note on A4: Sally Blair: Need to update URL when available
Note on A7: Sally Blair: this defaults to "Yes" and if the user moves it, the note in Table D row 11 shows up.

## T. NRCA
| User input |  |  | auto calculated |  | From another Table | From look up table
Q T. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html.
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
m | m | NRCA-PRC-01-F Compressed Air Systems | o | o | << moves to "Yes" if Table J is triggered
m | m | NRCA-PRC-02-F Kitchen Exhaust | o | o | << moves to "Yes" if Table N is triggered, unless N01 is checked
m | m | NRCA-PRC-03-F Garage Exhaust | o | o | << moves to "Yes" if Table H is triggered
m | m | NRCA-PRC-04-F Refrigerated Warehouses - Evaporator Fan Motor Controls | o | o | << moves to "Yes" if Table F is triggered & Fan Power Evaporators subtable column 06 is not greyed out
m | m | NRCA-PRC-05-F Refrigerated Warehouses - Evaporative Condenser Controls | o | o | << moves to "Yes" if Table F is triggered & "Evaporative-cooled" is clicked in Condensers subtable column 01
m | m | NRCA-PRC-06-F-Refrigerated Warehouses - Air Cooled Condenser Controls | o | o | << moves to "Yes" if Table F is triggered & "Air-cooled" is clicked in Condensers subtable column 01
m | m | NRCA-PRC-16-F-Refrigerated Warehouses - Adiabatic Condenser Controls | o | o | << moves to "Yes" if Table F is triggered & "Adiabatic" is clicked in Condensers subtable column 01
m | m | NRCA-PRC-07-F-Refrigerated Warehouses - Variable Speed Compressor | o | o | << moves to "Yes" if Table F is triggered & Compressors subtable column 04 selection of "Controls compressor speed…" is selected
m | m | NRCA-PRC-08-F Refrigerated Warehouses - Electric Resistance Underslab Heating System | o | o | << moves to "Yes" if Table F is triggered & Underslab Heating subtable column 02 selection of "Using electric resistance with…" is selected
m | m | NRCA-PRC-?-F Transcritical CO2 Refrigeration Systems | o | o | << move to "Yes" if any selections for the following = "NA: Transcritical CO2" - Table F Air-Cooled Condenser col04-07 - Table F Water/Evap-Cooled Condenser col04-07 - Table F Adiabatic Condenser col03-06 - Table G Condensers col06-07 - Table G Compressors col04 OR Table F Compressor col03 = "Transcritical CO2 w SST..."
m | m | NRCA-PRC-12-F Elevator Lighting & Ventilation Controls | o | o | << moves to "Yes" if Table K is triggered
m | m | NRCA-PRC-13-F Escalators & Moving Walkways Speed Controls | o | o | << moves to "Yes" if Table L is triggered
m | m | NRCA-PRC-14-F Lab Exhaust Ventilation Systems | o | o | << Moves to "Yes" if Table O & column 4 selection lower is either volume flowrate @ stack controlled by anemometer per 140.9(c)3C" OR Volume flowrate @ stack controlled by a contaminant sensor per 140.9(c)3D
m | m | NRCA-PRC-15-F Fume Hood Automatic Sash Closure Systems | o | o | << moves to "Yes" if Table O & column 05 selection is "Hood sash closure system design controlled per §140.9(c)4"
m | m | NRCA-PRC-?-F Steam Traps | o | o | << moves to "Yes" if Table R is triggered
Note on A8: Sally Blair: If user moves one of these from "Yes" to "No" trigger note in Table D Row 12.
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will leak testing be added to this form? Reply: It should be, we can ask SCO
Note on C17: 11.12.21 Need to add form # once determined.
Note on C22: Sally Blair: Update with form # once determined.

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/ HERS Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Designer Name: | Responsible Designer Signature:
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
[d:OnlyUI] The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-PRC form. [d:/OnlyUI]
Diane, in schema this needs to allow more than one responsible person.
?
Add Responsible Person
Remove Last
Note on F13: 2019 Update: This button should duplicate this table in the pdf, but the user input fields should be blank, but editable by the user.
Note on B15: UI Only: Table tip only applies to UI, does not apply to report generator.