| A. General Information Note: Submit one Installation Certificate for each duct system that is taking credit for duct location. |  |  |
| --- | --- | --- |
| 01 | SC System Identification or Name |  |
| 02 | SC System Location or Area Served |  |
| 03 | Indoor Unit Name or Description of Area Served |  |
| 04 | Status – Less than 12 ft Ducts in Conditioned Space Performance Credit |  |
| 05 | Status – Ducts Located In Conditioned Space Performance Credit |  |
| 06 | Status – All Ducts Entirely in Directly Conditioned Space Performance Credit |  |
| 07 | Status – Portions of Ducts Located in Conditioned Space, R-6 Exception |  |
| 08 | Status – Duct Systems Located Entirely in Conditioned Space, No Insulation Requirement |  |

| B. 12 Linear Feet or Less of Duct Located Outside of Conditioned Space - RA3.1.4.1.2 |  |
| --- | --- |
| 01 | A visual inspection shall confirm space conditioning systems with air handlers located outside the conditioned space have 12 linear feet or less of duct located outside the conditioned space including air handler and plenum. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| C. Ducts Located In Conditioned Space - RA3.1.4.1.3 |  |
| --- | --- |
| 01 | A visual inspection shall confirm the space conditioning system is located entirely in conditioned space. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| D. All Ducts Located Entirely in Directly Conditioned Space Performance Credit - RA3.1.4.3.8 |  |  |
| --- | --- | --- |
| 01 | A Visual Inspection Shall Confirm the Space Conditioning Distribution System Location |  |
| 02 | Actual System Duct Leakage Rate (cfm) Measured Using RA3.1.4.3.4 Duct Leakage to Outside from Fan Pressurization of Ducts |  |
| 03 | Compliance Statement: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |  |

| E. Portions of Ducts Located in Conditioned Space, R-6 Exception The following shall be confirmed by visual inspection when applicable. |  |
| --- | --- |
| 01 | Portions of the duct system with no insulation (or with insulation less than minimum R-6) are located in conditioned space below the ceiling separating the occupiable space from the attic. |
| 02 | Portions of the duct system with no insulation (or with insulation less than minimum R-6 ) are located entirely inside the building’s thermal envelope. |
| 03 | At all locations where portions of the duct system with no insulation (or with insulation less than minimum R-6) penetrates into unconditioned space, the penetrations are draft stopped compliant with CFC sections 703.1 and 704.1 and air-sealed to the construction materials that are penetrated, using materials compliant with CMC sections E502.4.2 to prevent air infiltration into the cavity. All connections in unconditioned space are insulated to a minimum of R-6. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| F. Duct Systems Located Entirely in Conditioned Space, No Insulation Requirement – RA3.1.4.3.8 |  |  |
| --- | --- | --- |
| 01 | A Visual Inspection Shall Confirm the Space Conditioning Distribution System Location |  |
| 02 | Actual System Duct Leakage Rate (cfm) Measured Using RA3.1.4.3.4 Duct Leakage to Outside from Fan Pressurization of Ducts |  |
| 03 | Compliance Statement: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Installation documentation is accurate and complete. |  |  |  |
| Documentation Author Name: |  | Documentation Author Signature: |  |
| Documentation Author Company Name: |  | Date Signed: |  |
| Address: |  | CEA/HERS Certification Identification (if applicable): |  |
| City/State/Zip: |  | Phone: |  |
| Responsible Person's Declaration statement |  |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: ### The information provided on this Certificate of Installation is true and correct. ### I am either: a) a responsible person eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction, or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Installation and attest to the declarations in this statement, or b) I am an authorized representative of the responsible person and attest to the declarations in this statement on the responsible person’s behalf. - The constructed or installed features, materials, components or manufactured devices (the installation) identified on this Certificate of Installation conforms to all applicable codes and regulations and the installation conforms to the requirements given on the Certificate of Compliance, plans, and specifications approved by the enforcement agency. - I understand that a HERS rater will check the installation to verify compliance and if such checking determines the installation fails to comply, I am required to offer any necessary corrective action at no charge to the building owner. - I will ensure that a registered copy of this Certificate of Installation shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Installation is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| Responsible Builder/Installer Name: | Responsible Builder/Installer Signature: |  |  |
| Company Name: (Installing Subcontractor or General Contractor or Builder/Owner) | Position With Company (Title): |  |  |
| Address: | CSLB License: |  |  |
| City/State/Zip: | Phone: |  | Date Signed: |
| Third Party Quality Control Program (TPQCP) Status: | Name of TPQCP (if applicable): |  |  |

LMCI-MCH-21-H User Instructions

Section A. General Information

- HVAC System Identification or Name: This field is filled out automatically. It is referenced from the LMCI-MCH-01, which must be completed prior to this document.

- HVAC System Location or Area Served: This field is filled out automatically. It is referenced from the LMCI-MCH-01, which must be completed prior to this document.

- Indoor Unit Name: This field is filled out automatically. It is referenced from the LMCI-MCH-01, which must be completed prior to this document.

- Status – Less than 12 ft Ducts in Conditioned Space Performance Credit: This field is automatically filled based on the information given on the LMCC. If “True” appears here, it means that this credit was taken in the performance calculations, is required for compliance and must be field verified.

- Status – Ducts Located in Conditioned Space Performance Credit: This field is automatically filled based on the information given on the LMCC. If “True” appears here, it means that this credit was taken in the performance calculations, is required for compliance and must be field verified.

- Status – All Ducts Located Entirely in Directly Conditioned Space Performance Credit: This field is automatically filled based on the information given on the LMCC. If “True” appears here, it means that this credit was taken in the performance calculations, is required for compliance and must be field verified.

- Status – Portions of Ducts Located in Conditioned Space, R-6 Exception – This field is automatically filled based on the information given on the LMCC. If “True” appears here, it means that portions of the duct system are located in conditioned space and are allowed to be installed with insulation less than the minimum R-Value or no insulation.

- Status – Duct Systems Located Entirely in Conditioned Space, No Insulation Requirement– This field is automatically filled based on the information given on the LMCC. If “True” appears here, it means that the duct system is located entirely in conditioned space and is allowed to be installed with insulation less than the minimum R-Value or no insulation.

Section B. 12 Linear Feet or Less of Duct Located Outside of Conditioned Space

- This field is automatically filled.

Section C. Ducts Located in Conditioned Space

- This field is automatically filled.

Section D. All Ducts Located Entirely in Directly Conditioned Space Performance Credit

- A Visual Inspection Shall Confirm the Distribution System is in Conditioned Space: If a visual inspection confirms that the ducts are entirely within directly conditioned space, then select “entirely in directly conditioned space”, otherwise select “not entirely in directly conditioned space”. The latter selection means that the system does not meet the requirements and the LMCC will have to be revised or the system will need to be modified such that the ducts are located entirely within directly conditioned space.

- Actual System Duct Leakage Rate (cfm) Measured using RA3.1.4.3.4 Duct Leakage to Outside from Fan Pressurization of Ducts: Enter the measured duct leakage rate (cfm) using the procedures found in RA3.1.4.3.4.

- Compliance Statement: This field is automatically filled.

Section E. Portions of Ducts Located in Conditioned Space, R-6 Exception

- This field must be a true statement (or not applicable) for the system to comply.

- This field must be a true statement (or not applicable) for the system to comply.

- This field must be a true statement (or not applicable) for the system to comply.

Section F. Duct Systems Located Entirely in Conditioned Space, No Insulation Requirement – RA3.1.4.3.8

1.	A Visual Inspection Shall Confirm the Distribution System is in Conditioned Space: If a visual inspection confirms that the ducts are entirely within conditioned space, then select “entirely in conditioned space”, otherwise select “not entirely in conditioned space”. The latter selection means that the system does not meet the requirements and the LMCC will have to be revised or the system will need to be modified such that the ducts are located entirely within conditioned space.

2.	Actual System Duct Leakage Rate (cfm) Measured using RA3.1.4.3.4 Duct Leakage to Outside from Fan Pressurization of Ducts: Enter the measured duct leakage rate (cfm) using the procedures found in RA3.1.4.3.4.

3.     Compliance Statement: This field is automatically filled.

| A. General Information Note: Submit one Installation Certificate for each duct system that is taking credit for duct location. |  |  |
| --- | --- | --- |
| 01 | SC System Identification or Name | <<Text referenced from MCH-01>> |
| 02 | SC System Location or Area Served | <<Text referenced from MCH-01>> |
| 03 | Indoor Unit Name or Description of Area Served | <<Text referenced from MCH-01>> |
| 04 | Status – Less than 12 ft Ducts in Conditioned Space Performance Credit | <<calculated field: if Less than 12ft Ducts Outside of Conditioned Space Flagged on LMCC = true , then display message “true” and display Table B below; else display message "not applicable” >> |
| 05 | Status – Ducts Located In Conditioned Space Performance Credit | <<calculated field: if Ducts Located In Conditioned Space Compliance Credit Claimed on LMCC = true , then display message “true” and display Table C below; else display message "not applicable” >> |
| 06 | Status – All Ducts Entirely in Directly Conditioned Space Performance Credit | <<calulated Field: if Exception from Minimum R-Value for Ducts In Conditioned Space reported on MCH-01 = yes, then display message “true” and display Table D below; else display message "not applicable”>> |
| 07 | Status – Portions of Ducts Located in Conditioned Space, R-6 Exception | <<calculated Field: if Exception from Minimum R-Value for Duct Portions Located in Conditioned Space reported on MCH-01 = yes, then display message “true” and display Table E below; else display message "not applicable”>> |
| 08 | Status – Duct Systems Located Entirely in Conditioned Space, No Insulation Requirement | <<calculated Field: if Exception from Minimum R-Value for Duct System Located Entirely in Conditioned Space reported on MCH-01 = yes, then display message “true” and display Table F below; else display message "not applicable” >> |

| B. 12 Linear Feet or Less of Duct Located Outside of Conditioned Space - RA3.1.4.1.2 <<This table only shown if A04 indicates the table is applicable, else display the "section does not apply" message >> |  |
| --- | --- |
| 01 | A visual inspection shall confirm space conditioning systems with air handlers located outside the conditioned space have 12 linear feet or less of duct located outside the conditioned space including air handler and plenum. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| C. Ducts Located In Conditioned Space - RA3.1.4.1.3 <<This table only shown if A05 indicates the table is applicable, else display the "section does not apply" message >> |  |
| --- | --- |
| 01 | A visual inspection shall confirm the space conditioning system is located entirely in conditioned space. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| D. All Ducts Located Entirely in Directly Conditioned Space Performance Credit - RA3.1.4.3.8 <<This table only shown if A06 indicates the table is applicable, else display the "section does not apply" message >> |  |  |
| --- | --- | --- |
| 01 | A Visual Inspection Shall Confirm the Space Conditioning Distribution System Location | <<user pick from list: ***Entirely in directly conditioned space; or ***Not entirely in directly conditioned space - does not comply>> |
| 02 | Actual System Duct Leakage Rate (cfm) Measured Using RA3.1.4.3.4 Duct Leakage to Outside from Fan Pressurization of Ducts | <<user input, numeric xxx.x>> |
| 03 | Compliance Statement: <<if measured duct leakage in D02 is less than or equal to 25 cfm, and visual inspection result in D01 = Entirely in directly conditioned space; then display text: "the duct system is considered to be entirely in directly conditioned space and performance credit is allowable", else the system does not meet the criteria for ducts entirely in directly conditioned space.>> |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |  |

| E. Portions of Ducts Located in Conditioned Space, R-6 Exception <<This table only shown if A07 or A08 indicates the table is applicable, else display the “section does not apply” message >> |  |
| --- | --- |
| 01 | Portions of the duct system with no insulation (or with insulation less than minimum R-6)are located in conditioned space below the ceiling separating the occupiable space from the attic. |
| 02 | Portions of the duct system with no insulation (or with insulation less than minimum R-6) are located entirely inside the building’s thermal envelope. |
| 03 | At all locations where portions of the duct system with no insulation (or with insulation less than minimum R-6) penetrates into unconditioned space, the penetrations are draft stopped compliant with CFC sections 703.1 and 704.1 and air-sealed to the construction materials that are penetrated, using materials compliant with CMC sections E502.4.2 to prevent air infiltration into the cavity. All connections in unconditioned space are insulated to a minimum of R-6. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| F. Duct Systems Located Entirely in Conditioned Space, No insulation Requirement - RA3.1.4.3.8 <<This table only shown if A08 indicates the table is applicable, else display the "section does not apply" message >> |  |  |
| --- | --- | --- |
| 01 | A Visual Inspection Shall Confirm the Space Conditioning Distribution System Location | <<user pick from list: ***Entirely in conditioned space; or ***Not entirely in conditioned space - does not comply>> |
| 02 | Actual System Duct Leakage Rate (cfm) Measured Using RA3.1.4.3.4 Duct Leakage to Outside from Fan Pressurization of Ducts | <<user input, numeric xxx.x>> |
| 03 | Compliance Statement: <<if measured duct leakage in F02 is less than or equal to 25 cfm, and visual inspection result in F01 = Entirely in conditioned space; then display text: "the duct system is considered to be entirely in conditioned space and duct insulation is not required", else the system does not meet the criteria for ducts entirely in conditioned space.>> |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |  |