| A. System Information |  |  |
| --- | --- | --- |
| 01 | Space Conditioning System Identification or Name |  |
| 02 | Space Conditioning System Location or Area Served |  |
| 03 | Building Type from CF1R |  |
| 04 | Verified Low Leakage Ducts in Conditioned Space (VLLDCS) Credit from CF1R? |  |
| 05 | Verified Low Leakage Air-handling Unit Credit from CF1R? |  |
| 06 | Duct System Compliance Category |  |

MCH-20c - Low Leakage Air-Handling Unit (LLAHU)

| B. Duct Leakage Diagnostic Test |  |  |  |
| --- | --- | --- | --- |
| 01 | Condenser Nominal Cooling Capacity (ton) |  |  |
| 02 | Heating Capacity (kBtu/h) |  |  |
| 03 | Conditioned Floor Area Served by this HVAC System (ft2) |  |  |
| 04 | Duct Leakage Test Conditions |  |  |
| 05 | Duct Leakage Test Method |  |  |
| 06 | Leakage Factor |  |  |
| 07 | Air-Handling Unit Airflow (AHU Airflow) Determination Method |  |  |
| 08 | Measured AHU Airflow (cfm) |  |  |
| 09 | Calculated Target Allowable Duct Leakage Rate (cfm) |  |  |
| 10 | Actual Duct Leakage Rate from Leakage Test Measurement (cfm) |  |  |
| 11 | Air-Handling Unit Manufacturer Name |  |  |
| 12 | Air-Handling Unit Model Number |  |  |
| 13 | Compliance Statement: |  |  |
| 14 | Notes: |  |  |

| ### C. Additional Requirements for Compliance |  |  |
| --- | --- | --- |
| 01 | The Low Leakage Air-handling Unit Model identified on this compliance document is included in the list of certified Low Leakage Air-Handling Units published on the Energy Commission Website at: http://www.energy.ca.gov/title24/equipment_cert/llahu/low_leakage_air_handling_units.pdf |  |
| 02 | System was tested in its normal operation condition. No temporary taping allowed. |  |
| 03 | Outside air (OA) duct connections to the central forced air duct system shall not be sealed/taped off during duct leakage testing. OA ducts used for Central Fan Integrated (CFI) Indoor Air Quality ventilation systems, or Central Fan Ventilation Cooling Systems, that utilize dampers that open only when OA is required and automatically close when OA is not required, may configure the OA damper to the closed position during duct leakage testing. |  |
| 04 | All supply and return register boots were sealed to the drywall. |  |
| 05 | Building cavities were not used as plenums or platform returns in lieu of ducts. |  |
| 06 | If cloth backed tape was used it was covered with Mastic and draw bands. |  |
| 07 | All connection points between the air handler and the supply and return plenums are completely sealed. |  |
| 08 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 09 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| D. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Verification documentation is accurate and complete. |  |  |  |
| Documentation Author Name: | Documentation Author Signature: |  |  |
| Company: | Date Signed: |  |  |
| Address: | CEA/HERS Certification Information (if applicable): |  |  |
| City/State/Zip: | Phone: |  |  |
| Responsible Person's Declaration statement |  |  |  |
| I certify the following under penalty of perjury, under the laws of the State of California: - The information provided on this Certificate of Verification is true and correct. - I am the certified HERS Rater who performed the verification identified and reported on this Certificate of Verification (responsible rater). - The installed features, materials, components, manufactured devices, or system performance diagnostic results that require HERS verification identified on this Certificate of Verification comply with the applicable requirements in Reference Appendices RA2, RA3, and the requirements specified on the Certificate of Compliance for the building approved by the enforcement agency. - The information reported on applicable sections of the Certificate(s) of Installation (CF2R) signed and submitted by the person(s) responsible for the construction or installation conforms to the requirements specified on the Certificate(s) of Compliance (CF1R) approved by the enforcement agency. - I will ensure that a registered copy of this Certificate of Verification shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Verification is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| BUILDER OR INSTALLER INFORMATION AS SHOWN ON THE CERTIFICATE OF INSTALLATION |  |  |  |
| Company Name (Installing Subcontractor, General Contractor, or Builder/Owner): |  |  |  |
| Responsible Builder or Installer Name: |  | CSLB License: |  |
| HERS PROVIDER DATA REGISTRY INFORMATION |  |  |  |
| Sample Group Number (if applicable): |  |  | Dwelling Test Status in Sample Group (if applicable): |
| HERS RATER INFORMATION |  |  |  |
| HERS Rater Company Name: |  |  |  |
| Responsible Rater Name: |  |  | Responsible Rater Signature: |
| Responsible Rater Certification Number w/ this HERS Provider: |  |  | Date Signed: |

CF3R-MCH-20c-H User Instructions

Section A. System Information

- HVAC System Identification or Name: This field is filled out automatically. It is referenced from the CF2R-MCH-20.

- HVAC System Location or Area Served: This field is filled out automatically. It is referenced from the CF2R-MCH-20.

- Building Type: This field is filled out automatically. It is referenced from the CF2R-MCH-20.

- Verified Low Leakage Ducts in Conditioned Space (VLLDCS): This field is filled out automatically. It is referenced from the CF2R-MCH-20.

- Verified Low Leakage Air-handling Unit (VLLAHU) Credit: This field is filled out automatically. It is referenced from the CF2R-MCH-20.

Duct System Compliance Category: This field is filled out automatically. It is referenced from the CF2R-MCH-20.

Section B. Duct Leakage Diagnostic Test - MCH-20c - Low Leakage Air-Handling Unit (LLAHU)

- Condenser Nominal Cooling Capacity (ton): Same data given on MCH-01.

- Heating Capacity (kBtu/h): Same data given on MCH-01;

- Conditioned Floor Area Served by this HVAC System (ft2): User will input CFA for zone which should be consistent with the value from the CF1R. User will have the option to leave this field blank because the zone CFA is only required for the default airflow calculation.

- Duct Leakage Test Conditions: User must select from the following options:

  - Test Final: Test conducted at final inspection (testing at rough is not an option with this test. See Section RA3.1.4.3.1 of the 2016 Reference Appendices).

- Duct Leakage Test Method?: User will select from the following options: Total Leakage.

- Leakage Factor: value will be automatically populated from in CF1R.

- Air-Handling Unit Airflow (AHU Airflow) Determination Method: User will select from the following options:

  - Cooling System Method: For systems with cooling, this selection must be made, and the nominal air handler airflow shall be 400 CFM per nominal ton of condensing unit cooling capacity as specified by the manufacturer or the heating only value, whichever is greater (See Section RA3.1.4.2.2 of the 2016 Reference Appendices).

  - Heating System Method: For heating only systems the nominal air handler airflow shall be 21.7 CFM per kBtu/hr of rated heating output capacity.

  - Measured Airflow Method: The system airflow can be used as the air handler airflow for the purpose of establishing duct leakage percentage (See Section RA3.1.4.2.3 of the 2016 Reference Appendices).

- Measured AHU Airflow (cfm): If “Measured Airflow Method” is selected in B07, user must input measured airflow.

- Calculated Target Allowable Duct Leakage Rate (cfm): This value will be automatically populated depending on values in B06, B07, and B08.

- Actual Duct Leakage Rate from Leakage Test Measurement (cfm): User will input this value from actual measurements from leakage test.

- Air-Handling Unit Manufacturer Name: This will be automatically populated from information entered in the MCH-01.

- Air-Handling Unit Model Number: This will be automatically populated from information entered in the MCH-01.

- Compliance Statement: If Actual Duct Leakage Rate from leakage test (B10) is less than or equal to Calculated Target Allowable Duct Leakage Rate (B09), “System passes leakage test” will automatically populate. If not, “System fails leakage test will automatically populate.

- Notes: This field is automatically filled out. The values in B01, B02, B03, B11 and B12 are checked against the values in the same rows of the CF2R-MCH-20 for this system. If they do not match an error message will appear here.

Section C Additional Requirements for Compliance

- This field must be a true statement (or not applicable) for the system to comply.

- This field must be a true statement (or not applicable) for the system to comply.

- This field must be a true statement (or not applicable) for the system to comply.

- This field must be a true statement (or not applicable) for the system to comply.

- This field must be a true statement (or not applicable) for the system to comply

- This field must be a true statement (or not applicable) for the system to comply

- This field must be a true statement (or not applicable) for the system to comply

- Verification Status: If this Section does not apply, then select “All N/A”. If the system meets all of the additional requirements for compliance then select “Pass”, otherwise select “Fail”. The latter selection means that the system does not meet the requirements and the system will need to be modified to meet the requirements or airflow and fan efficacy will have to be verified by diagnostic testing.

- Correction Notes: If one or more applicable requirements are not met “Fail” will appear in the row above. When this occurs the rater is required to enter detailed notes here that describes what failed and why.

Section D. Determination of HERS Verification Compliance

- This field is filled out automatically. Compliance requires that all individual criteria pass.

| A. System Information |  |  |  |
| --- | --- | --- | --- |
| 01 | Space Conditioning System Identification or Name | <<text (data from CF2R-MCH-20)>> |
| 02 | Space Conditioning System Location or Area Served | <<text (data from CF2R-MCH-20)>> |
| 03 | Building Type from CF1R | <<text (data from CF2R-MCH-20)>> |
| 04 | Verified Low Leakage Ducts in Conditioned Space (VLLDCS) Credit from CF1R? | <<text (data from CF2R-MCH-20)>> |
| 05 | Verified Low Leakage Air-handling Unit Credit from CF1R? | <<text (data from CF2R-MCH-20)>> |
| 06 | Duct System Compliance Category | <<text (data from CF2R-MCH-20)>> |
| 07. determine compliance method for this document; display applicable tables below; (this row not visible to user) |  | <<Calculated Result: if A6= Replacement using Smoke Test or Alteration using Smoke Test; then display method: 20e. Altered or Replacement Duct System using Smoke Test if 6= Replacement or Alteration; then display method: 20d. Altered or Replacement Duct System elseif 6=New and 4=VLLDCS (true); then display method: 20b. Low Leakage Ducts in Conditioned Space elseif 6=New and 5=VLLAHU (true); then display method: 20c. Low Leakage Air-Handling Unit elseif 6=New then display method: 20a. Completely New Duct System >> |

MCH-20c - Low Leakage Air-Handling Unit (LLAHU)

| B. Duct Leakage Diagnostic Test |  |  |
| --- | --- | --- |
| 01 | Condenser Nominal Cooling Capacity (ton) | <<user input is either numeric x.x; or select value =N/A>> |
| 02 | Heating Capacity (kBtu/h) | << user input is either numeric xxx.x; or select value =N/A >> |
| 03 | Conditioned Floor Area Served by this HVAC System (ft2) | <<user input, numeric, xxx,xxx>> |
| 04 | Duct Leakage Test Conditions | <<text (data from CF2R-MCH-20)>> |
| 05 | Duct Leakage Test Method | <<text (data from CF2R-MCH-20)>> |
| 06 | Leakage Factor | <<text (data from CF2R-MCH-20)>> |
| 07 | Air-Handling Unit Airflow (AHU Airflow) Determination Method | << pick one from list: CoolingSystemMethod; HeatingSystemMethod; MeasuredAirflowMethod |
| 08 | Measured AHU Airflow (cfm) | <<if B07 = MeasuredAirflowMethod, then user enter numeric x,xxx, else if Value in B07 ≠ MeasuredAirflowMethod, then value in B08=n/a>> |
| 09 | Calculated Target Allowable Duct Leakage Rate (cfm) | <<calculated field: numeric xxx: if AHUAirflowMethod= CoolingSystemMethod then AHUAirflow=CondenserNomCoolCapacityTon*400* LeakageFactor; elseif AHUAirflowMethod= HeatingSystemMethod then AHUAirflow=HeatingCapacityKbtuh*21.7* LeakageFactor; elseif AHUAirflowMethod= MeasuredAirflowMethod then AHUAirflow= Measured AHUAirflow * LeakageFactor>> |
| 10 | Actual Duct Leakage Rate from Leakage Test Measurement (cfm) | <<user input: numeric xxx.x>> |
| 11 | Air-Handling Unit Manufacturer Name | <<user input, text, maximum 200 characters>> |
| 12 | Air-Handling Unit Model Number | <<user input, text, maximum 200 characters>> |
| 13 | Compliance Statement: <<if measured leakage is < or = to target allowed: "system passes leakage test"; else if measured leakage is > target allowed: "system fails leakage test">> |  |
| 14 | Notes: <<if CF2R-MCH-20 row B01, B02 and B03 ≠ CF3R-MCH-20 row B01, B02 and B03, then display “The installed cooling capacity, heating capacity or CFA served does not match the Installation Certificate”, elseif CF2R-MCH-20 row B01, B02 and B03 = CF3R-MCH-20 row B01, B02 and B03, then display “ “; if CF2R-MCH-20 row B11 and B12 ≠ CF3R-MCH-20 row B11 and B12, then display “The Air-Handling Unit Manufacturer Name or Model Number does not match the Installation Certificate”, elseif CF2R-MCH-20 row B11 and B12 = CF3R-MCH-20 row B11 and B12, then display “ “>> |  |

| ### C. Additional Requirements for Compliance |  |  |
| --- | --- | --- |
| The responsible persons signature on this document indicates the installation complies with the following requirements: |  |  |
| 01 | The Low Leakage Air-handling Unit Model identified on this compliance document is included in the list of certified Low Leakage Air-Handling Units published on the Energy Commission Website at: http://www.energy.ca.gov/title24/equipment_cert/llahu/low_leakage_air_handling_units.pdf |  |
| 02 | System was tested in its normal operation condition. No temporary taping allowed. |  |
| 03 | Outside air (OA) duct connections to the central forced air duct system shall not be sealed/taped off during duct leakage testing. OA ducts used for Central Fan Integrated (CFI) Indoor Air Quality ventilation systems, or Central Fan Ventilation Cooling Systems, that utilize dampers that open only when OA is required and automatically close when OA is not required, may configure the OA damper to the closed position during duct leakage testing. |  |
| 04 | All supply and return register boots were sealed to the drywall. |  |
| 05 | Building cavities were not used as plenums or platform returns in lieu of ducts. |  |
| 06 | If cloth backed tape was used it was covered with Mastic and draw bands. |  |
| 07 | All connection points between the air handler and the supply and return plenums are completely sealed. |  |
| 08 | Verification Status: | <<user pick from list: *** Pass - all applicable requirements are met; or *** Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or *** All n/a - This entire table is not applicable |
| 09 | Correction Notes: | <<if Verification Status= Fail, then text entry in this Corrections Notes field is required; user input text>> |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| D. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 | <<if B13=system passes leakage test, and C08≠Fail, then display: Complies: All specified verification protocol requirements on this document are met; else display: Does not comply: One or more specified verification protocol requirements on this document are not met >> |