| A. General Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | Dwelling Unit Name |  | 02 | Climate Zone |  |
| 03 | Dwelling Unit Total Conditioned Floor Area (ft2) |  | 04 | Number of Space Conditioning Systems in this Dwelling Unit |  |
| 05 | Certificate of Compliance Type |  | 06 | Method Used to Calculate HVAC Loads |  |
| 07 | Calculated Dwelling Unit Sensible Cooling Load (Btu/h) |  | 08 | Calculated Dwelling Unit Heating Load (Btu/h) |  |
| 09 | Dwelling Unit Number of Bedrooms |  |  |  |  |

MCH-01b - Space Conditioning Systems Ducts and Fans - Prescriptive Alterations

| B. Space Conditioning (SC) System Information |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | SC System Location or Area Served | CFA served by this SC System (ft2) | Is the SC system a ducted system? | Installing a refrigerant containing component? | Installing new SC System components? | Installing more than 40 feet of ducts? | Installing entirely new duct system? | Installing entirely new SC system? | Alteration Type |

| C. Space Conditioning (SC) System Alterations Compliance Information |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
| SC Identification or Name | Heating System Type | Altered Heating Component | Heating Efficiency Type | Heating Minimum Efficiency Value | Cooling System Type | Altered Cooling Components | Cooling Efficiency Type | Cooling Minimum Efficiency Value | Required Thermostat Type | New or Replaced Duct Length | New Duct R-Value | Central Fan Integrated (CFI) Ventilation System Status |

| D. Installed Heating Equipment Information |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| SC Identification or Name | Heating Efficiency Type | Heating Efficiency Value | Heating Unit Manufacturer | Heating Unit Model Number | Heating Unit Serial Number | Rated Heating Capacity, Output (Btu/h) |
| Notes: |  |  |  |  |  |  |

| E. Installed Cooling Equipment Information |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 |
| SC Identification or Name | Cooling Efficiency Type | Cooling Efficiency Value | Condenser or Package Unit Manufacturer | Condenser or Package Unit Model Number | Condenser or Package Unit Serial Number | System Rated Cooling Capacity at Design Conditions (Btu/h) | Condenser Rated Nominal Capacity (ton) |
| Notes: |  |  |  |  |  |  |  |

| F. Extension of Existing Duct System, Greater Than 40 Feet |  |  |
| --- | --- | --- |
| 01 | 02 |  |
| SC Identification or Name | New Duct R-Value |  |

| G. Installed Duct System Information |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 |
| SC System Identification or Name | SC System Location or Area Served | Supply Duct Location | Supply Duct R-Value | Return Duct Location | Return Duct R-Value | Method of Compliance with Duct and Filter Grille Sizing Req's in 150.0(m)13 | Number of Air Filter Devices on System | Can RA3.3 Airflow Protocols be used to test this System? |
| Notes: |  |  |  |  |  |  |  |  |

| H. Installed Air Filter Device Information |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| SC System Identification or Name | SC System Location or Area Served | Air Filter Identification or Name | Air Filter Device Type | Air Filter Device Location | Determined Design Airflow Rate for Air Filter Device (cfm) | Determined Design Allowable Pressure Drop for Air Filter Device (inch W.C.) |
| Notes: |  |  |  |  |  |  |

| I. Air Filter Device Requirements |  |
| --- | --- |
| 01 | The system shall be designed to ensure that all recirculated air and all outdoor air supplied to the occupiable space is filtered before passing through the system's thermal conditioning components. |
| 02 | The system shall be designed to accommodate the clean-filter pressure drop imposed by the system air filter device(s). The design airflow rate and maximum allowable clean-filter pressure drop at the design airflow rate applicable to each air filter device shall be determined, and all system air filter device locations shall be labeled to disclose the applicable design airflow rate and the maximum allowable clean-filter pressure drop. The labels shall be permanently affixed to the air filter device, readily legible, and visible to a person replacing the air filter media, and the air filter devices shall be provided with air filter media that conforms to these determined/labeled maximum allowable clean-filter pressure drop values as rated using AHRI Standard 680. |
| 03 | All system air filter devices shall be located and installed in such a manner as to allow access and regular service by the system owner. |
| 04 | The system shall be provided with air filter media having a designated efficiency equal to or greater than MERV 6 when tested in accordance with ASHRAE Standard 52.2, or a particle size efficiency rating equal to or greater than 50% in the 3.0–10 micron range when tested in accordance with AHRI Standard 680. |
| 05 | The system shall be provided with air filter media that has been labeled by the manufacturer to disclose the efficiency and pressure drop ratings that conform to the required efficiency and pressure drop requirements for the air filter device. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| J. HERS Verification Requirements |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | SC System Location or Area Served | Exemption From Duct Leakage Requirements | MCH-20 Duct Leakage Test | Exemption from Minimum R-Value for Ducts In Conditioned Space | MCH-21 Duct Location Verification | MCH-22 AHU Fan Efficacy (W/cfm) | MCH-23 AHU Airflow Rate (cfm/ton) | MCH-25 Refrigerant Charge | MCH-28 Return Duct Design - Table 150.0-B or C |
| Notes: |  |  |  |  |  |  |  |  |  |

| K. Space Conditioning Systems, Ducts and Fans – Mandatory Requirements and Additional Measures Note: Additional mandatory requirements from Section 150.0 that are not listed here may be applicable to some systems. These requirements may be applicable to only newly installed equipment or portions of the system that are altered. Existing equipment may be exempt from these requirements. |  |
| --- | --- |
| Heating Equipment |  |
| 01 | Equipment Efficiency: All heating equipment must meet the minimum efficiency requirements of Section 110.1 and Section 110.2(a) and the Appliance Efficiency Regulations. |
| 02 | Controls: All unitary heating systems, including heat pumps, must be controlled by a setback thermostat. These thermostats must be capable of allowing the occupant to program the temperature set points for at least four different periods in 24 hours. See Sections 150.0(i), 110.2(b). |
| 03 | Sizing: Heating load calculations must be done on portions of the building served by new heating systems to prevent inadvertent undersizing or oversizing. See sections 150.0(h)1 and 2). |
| 04 | Furnace Temperature Rise: Central forced-air heating furnace installations must be configured to operate at or below the furnace manufacturer's maximum inlet-to-outlet temperature rise specification. See Section 150.0(h)4. |
| 05 | Standby Losses and Pilot Lights: Fan-type central furnaces may not have a continuously burning pilot light. Section 110.5 and Section 110.2(d). |
| Cooling Equipment |  |
| 06 | Equipment Efficiency: All cooling equipment must meet the minimum efficiency requirements of Section 110.1 and Section 110.2(a) and the Appliance Efficiency Regulations. |
| 07 | Refrigerant Line Insulation: All refrigerant line insulation in split system air conditioners and heat pumps must meet the R-value and protection requirements of Section 150.0(j)2 and 3, and Section 150.0(m)9. |
| 08 | Condensing Unit Location: Condensing units shall not be placed within 5 feet of a dryer vent outlet. See Section 150.0(h)3A. |
| 09 | Liquid Line Filter Drier: If applicable, a liquid line filter drier shall be installed according to the manufacturer’s specifications. Section 150.0(h)3B |
| 10 | Sizing: Cooling load calculations must be done on portions of the building served by new cooling systems to prevent inadvertent undersizing or oversizing. See Section 150.0(h)1 and 2. |
| Air Distribution System Ducts, Plenums and Fans |  |
| 11 | Insulation: In all cases, unless ducts are enclosed entirely in directly conditioned space, the minimum duct insulation value is R-6. Note that higher values may be required by the prescriptive or performance requirements. See Section 150.0(m)1. |
| 12 | Connections and Closures: All installed air-distribution system ducts and plenums must be, sealed and insulated to meet the requirements of CMC Sections 601.0, 602.0, 603.0, 604.0, 605.0 and ANSI/SMACNA-006-2006: Supply-air and return-air ducts and plenums must be insulated to a minimum installed level of R-6.0 or enclosed entirely in directly conditioned space as confirmed through field verification and diagnostic testing in accordance with the requirements of Reference Residential Appendix RA3.1.4.3.8. |
| Heat Pump Thermostat |  |
| 13 | A thermostat shall be installed that meets the requirements of Section 110.2(b) and Section 110.2(c). |
| 14 | The thermostat shall be installed in accordance with the manufacturers published installation specifications. |
| 15 | First stage of heating shall be assigned to heat pump heating. |
| 16 | Second stage back up heating shall be set to come on only when the indoor set temperature cannot be met. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| ### I certify that this Certificate of Installation documentation is accurate and complete. |  |  |  |
| Documentation Author Name: |  | Documentation Author Signature: |  |
| Documentation Author Company Name: |  | Date Signed: |  |
| Address: |  | CEA/HERS Certification Identification (If applicable): |  |
| City/State/Zip: |  | Phone: |  |
| Responsible Person's Declaration statement |  |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: ### The information provided on this Certificate of Installation is true and correct. - I am either: a) a responsible person eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction, or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Installation, and attest to the declarations in this statement, or b) I am an authorized representative of the responsible person and attest to the declarations in this statement on the responsible person’s behalf. - The constructed or installed features, materials, components or manufactured devices (the installation) identified on this Certificate of Installation conforms to all applicable codes and regulations and the installation conforms to the requirements given on the Certificate of Compliance, plans, and specifications approved by the enforcement agency. - I will ensure that a registered copy of this Certificate of Installation shall be posted or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Installation is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| Responsible Builder/Installer Name: | Responsible Builder/Installer Signature: |  |  |
| Company Name: (Installing Subcontractor or General Contractor or Builder/Owner) | Position With Company (Title): |  |  |
| Address: | CSLB License: |  |  |
| City/State/Zip: | Phone |  | Date Signed: |

CF2R-MCH-01b-E User Instructions

Minimum requirements for prescriptive HVAC installation compliance can be found in Building Energy Efficiency Standards Section 150.2(b)1C.

Completing these documents will require that you have the Reference Appendices for the 2016 Building Energy Efficiency Standards. This document contains the Joint Appendices which are used to determine climate zone and to complete the section for opaque surfaces.

When the term CF2R is used it means the CF2R-MCH-01-H.

Instructions for sections with column numbers and row numbers are given separately.

A. General Information

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. When the project scope includes an addition to an existing building, the value is equal to the sum of the existing conditioned floor area plus the conditioned floor area of the addition. The default value from the CF1R may be overwritten in this document. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.  This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- Oversized equipment can result in reduced efficiency and capacity. Entirely new systems (see definition in Section 9.6.9 of the RCM) must be properly sized to match the heating and cooling load of the space that it serves. To do this, heating and cooling load calculations must be performed using an approved calculation methodology. These are listed here. Select the load calculation methodology used for this dwelling unit. If the project consists of a partial replacement of equipment or ducts (change-out) then load calculations are not required. Select N/A. Load calculations are always recommended, especially if the loads of the house have been changed since the original equipment has been installed (reduced via weatherization, other improvements).

- Enter the total sensible cooling load for the dwelling unit described by this document. For projects involving dwelling units with more than one system, this will be a sum of the loads for the parts of the dwelling unit served by those systems. If the project consists of a partial replacement of equipment or ducts (change-out), then load calculations are not required. Select N/A.

- Enter the total heating load for the dwelling unit described by this document. For projects involving dwelling units with more than one system, this will be a sum of the loads for the parts of the dwelling unit served by those systems. If the project consists of a partial replacement of equipment or ducts (change-out), then load calculations are not required. Select N/A.

- Enter the number of bedrooms in the dwelling unit.

B. Space Conditioning (SC) System Information

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon.  Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically based on the entries in the previous columns.

C. Space Conditioning (SC) System Alterations Compliance Information

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is calculated based on entries in previous columns.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are uncommon. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel. Revising the CF1R to match is recommended and may be required.

- This field is filled out automatically. It is calculated based on entries in previous columns.

D. Installed Heating Equipment Information

- This field is filled out automatically. It is referenced from the same row and column in the previous section.

- This field is filled out automatically. It is referenced from the same row and column in Section C.

- Enter the certified heating efficiency of the installed equipment. This value is verified against the minimum value shown in Section C. The installed efficiency must be greater than or equal to the required minimum efficiency.

- Enter the name of the installed Heating Unit Manufacturer as shown on the equipment nameplate.

- Enter the name of the installed Heating Unit Model Number as shown on the equipment nameplate.

- Enter the name of the installed Heating Unit Serial number as shown on the equipment nameplate.

- Enter the rated heating capacity (output) of the installed Heating Unit in BTUs per hour.

E. Installed Cooling Equipment Information:

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from Section C.

- Enter the certified cooling efficiency of the installed equipment that corresponds to the type shown in the previous column. This value is verified against the minimum value shown in Section C. The installed efficiency must be greater than or equal to the required minimum efficiency.

- Enter the name of the installed Condenser or Package Unit Manufacturer as shown on the equipment nameplate.

- Enter the name of the installed Condenser or Package Unit Model Number as shown on the equipment nameplate.

- Enter the name of the installed Condenser or Package Unit Serial Number as shown on the equipment nameplate.

- Enter the rated sensible cooling capacity at design conditions of the installed cooling system in BTUs per hour.

- Enter the installed Condenser Rated Nominal Cooling Capacity in tons. Note that this is based on the condenser, not the coil or air handler. This can usually be determined by the condenser model number.

F. Extension of Existing Duct System, Greater Than 40 Feet

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- Enter the R-value of the installed supply ducts. This value is verified against the minimum value shown in Section C. The installed R-value must be greater than or equal to the required minimum R-value.

G. Installed Duct System information

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- Select the choice that best describes the predominant location of the supply ducts for this system.

- Enter the R-value of the installed supply ducts. This value is verified against the minimum value shown in Section C. The installed R-value must be greater than or equal to the required minimum R-value.

- Select the choice that best describes the predominant location of the return ducts for this system.

- Enter the R-value of the installed return ducts. This value is verified against the minimum value shown in Section C. The installed R-value must be greater than or equal to the required minimum R-value.

- Pick the appropriate choice. Refer to section 150.0(m)13 of the 2016 Building Energy Efficiency Standards, and Section 4.4 of Chapter 4 of the 2016 Residential Compliance Manual for more information.

- Specify the number of air filter devices installed in this space conditioning system. Air filter devices installed in completely new systems must be properly sized, as documented in the next section. The value entered here will determine the number of rows needed in the following section.

- If the system is of a type that can use one of the Reference Residential Appendix RA3.3 protocols for testing the airflow rate, then enter yes. Otherwise enter no.

H. Installed Air Filter Device Information

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- Enter a descriptive name of each air filter device so that it may be distinguished from others in the same system.  Examples: FG1, filter2, etc.

- Select the appropriate type of filter device from the list.

- Enter a descriptive name of each air filter device so that it may be identified in the home. Examples: master suite, main hallway, at furnace, entry wall, etc.

- Enter the design flow in CFM of the filter device. The total for all filter devices in a single system should be greater than or equal to the total system design CFM in cooling mode (or heating mode for heat-only systems).

- Enter the design static pressure drop provided by the filter device manufacturer. This should be consistent with the duct design calculations. Not accounting for higher filter pressure drops will result in poor system airflow characteristics, reduced capacity and reduced efficiency. This may result in not passing field verification.

I. Air Filter Device Requirements

This table is a list of requirements for air filter devices.

J. HERS Verification Requirements

- This field is filled out automatically. It references previous sections in this document.

- This field is filled out automatically. It references previous sections in this document.

- If applicable, select the any of the exemptions listed. Exemptions will be flagged and may subject the system to additional enforcement scrutiny.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- If applicable, select the any of the exemptions listed. Exemptions will be flagged and may subject the system to additional enforcement scrutiny.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

K. Space Conditioning Systems, Ducts and Fans – Mandatory Requirements and Additional Measures

This table is a list of mandatory measures and additional requirements for space conditioning systems, ducts and fans.

| A. General Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | Dwelling Unit Name | <<default reference text from CF1R; or allow user override input: text, 15? character maximum>> | 02 | Climate Zone | <<default reference text from CF1R >> |
| 03 | Dwelling Unit Total Conditioned Floor Area (ft2) | <<numeric: xxxxx; if1 parent is CF1R-PRF, then if2 project scope = Newly Constructed (Addition Alone) then prompt user to enter a value equal to dwelling unit existing CFA + addition CFA else reference the value from CF1R endif2 elseif parent is CF1R-NCB-01, then if3 project scope = New Addition greater than 1,000 ft2 then prompt user to enter a value equal to dwelling unit existing CFA + addition CFA elseif project scope = Newly Constructed Building, then if4 building type = Single Family, then reference value from CF1R-NCB field A10 elseif Building Type=Multifamily, then reference value from CF1R-NCB field M02 endif4 endif3 elseif parent is CF1R-ADD-01, then if5 building type= Single Family, then reference value from field A08 from the CF1R-ALT-02 that is required for the dwelling unit according to CF1R-ADD-01 Section J. elseif Building Type=Multifamily, then reference value from field A08 from the CF1R-ALT-02 that is required for the dwelling unit according to CF1R-ADD-01 Section L. endif5 elseif parent is CF1R-ALT-01, then if6 building type= Single Family, then reference value from field A08 from the CF1R-ALT-02 that is required for the dwelling unit according to CF1R-ALT-01 Section G. elseif Building Type=Multifamily, then reference value from field A08 from the CF1R-ALT-02 that is required for the dwelling unit according to CF1R-ALT-01 Section letter I. endif6 elseif parent is CF1R-ALT-02, then reference value from CF1R-ALT-02 field A08. endif1 allow user to override default and input a value; flag overridden values and report in project status notes field >> | 04 | Number of Space Conditioning Systems in this Dwelling Unit | <<integer: xx; If parent is CF1R-ALT-02 doc type, then use as default the value referenced from CF1R-ALT-02 Section A (field A10); or allow user to override the default and input a new value; flag non-default values and report in project status notes field; elseif parent is not CF1R-ALT-02 doc type, then user input the integer value>> |
| 05 | Certificate of Compliance Type | << reference document type property from CF1R: allowed values: performance (CF1R-PRF); or prescriptive additions/alterations (CF1R-ADD/CF1R-ALT); or prescriptive newly constructed (CF1R-NCB)>> | 06 | method Used to calculate HVAC loads | <<user select from list: *ASHRAE Handbook; *SMACNA Residential Comfort System Installation Standards Manual; *ACCA Manual J *n/a equipment changeout, like-for-like>> |
| 07 | Calculated dwelling unit Sensible Cooling Load (Btu/h) | <<user entry: integer: xxxxx; or allow selection of value=n/a if value in A06="n/a equipment changeout, like-for-like" >> | 08 | Calculated Dwelling Unit Heating Load (Btu/h) | <<user entry: integer: xxxxx; or allow selection of value=n/a if value in A06="n/a equipment changeout, like-for-like">> |
| 09 | Dwelling Unit Number of Bedrooms | <<<<calculated field: integer xx: if CertComplianceType=performance, then use as default the value referenced from CF1R-PRF or allow user to override the default and input a new value; flag non-default values and report in project status notes field; elseif parent is not CF1R-PRF doc type, then user input the integer value xx>> | 10 | Determination of Mech01 type (this field not visible to user) | <<calculated field: if1 CertComplianceType=performance, then if2 CF1R-PRF Project Scope=one of the following two types: **Addition and/or Alteration **Newly Constructed - Addition Alone then display doc variation MCH-01d; elseif CF1R-PRF Project Scope=Newly Constructed, then display doc variation MECH01a endif2 elseif CertComplianceType=prescriptive additions/alterations, then display doc variation MECH01b, elseif CertComplianceType=prescriptive newly constructed, then display doc variation MECH01c (this field not visible to user) endif1>> |

MCH-01b - Space Conditioning Systems Ducts and Fans - Prescriptive Alterations

| B. Space Conditioning (SC) System Information << require one row of data to be entered in this table for each of the quantity of space conditioning systems entered in A04>> |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | SC System Location or Area Served | CFA served by this SC System (ft2): | Is the SC system a ducted system? | Installing a refrigerant containing component? | Installing new SC System components? | Installing more than 40 feet of ducts? | Installing entirely new duct system? | Installing entirely new SC system? | Alteration Type |
| <<reference values from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required; do not allow duplicate system names to be used>> | <<reference values from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; allow user to override the default and input a new value; flag non-default values and report in project status notes field; a revised CF1R may be required >> | << Calculated field: determine the correct result for "alteration type" for entry in this field by the user responses in B04, B05, B06, B07, B08, B09 and use of Logic Table for Determining Alteration Type and HERS Verification Requirements (inserted below this section); constrain user input for fields B04-B09 to allow only the available combinations of responses given in the Logic Table in rows a through s; alteration types are: *Extension of Existing Duct System; *Altered Space Conditioning System; *Entirely New or Complete Replacement Duct System with or without Equipment Changeout; *Entirely New or Complete Replacement Space Conditioning System * No alteration Performed >> |

| Logic Table for Determining Alteration Type and HERS Verification Requirements (this table not shown on the completed document) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
|  | Is the altered or installed system a ducted system? | Altering or installing a refrigerant containing component? | Installing new components? (packaged unit, or condensing unit, or cooling/heating coil, or air-handling unit, etc) | Installing more than 40 linear feet of new or replacement ducts? | Is the entire duct system accessible for sealing, and is more than 75% of the duct system new or replaced? | Are all of the system's components and ducts new or replaced? (entirely new system) | alteration type | HERS | notes |
| a | no | yes | no | no | no | no | Altered space conditioning system | RC | e.g. alteration to refrigerant containing component - mini-split or packaged AC |
| b | no | yes | yes | no | no | no | Altered space conditioning system | RC | e.g. changeout mini-split system component |
| c | yes | no | yes | no | no | no | Altered space conditioning system | DctLk | e.g. new hydronic AHU or furnace |
| d | yes | no | yes | yes | no | no | Altered space conditioning system | DctLk | e.g. new furnace + duct alteration |
| e | yes | yes | no | no | no | no | Altered space conditioning system | RC | e.g. alteration to a refrigerant containing component - split system |
| f | yes | yes | yes | no | no | no | Altered space conditioning system | RC + DctLk | e.g. changeout refrigerant containing components |
| g | yes | yes | yes | yes | no | no | Altered space conditioning system | RC + DctLk | e.g. changeout refrigerant containing compinent + altered ducts |
| h | yes | yes | no | yes | no | no | Altered space conditioning system | RC + DctLk | e.g. alteration to refrigerant containing component + altered ducts |
| i | yes | no | no | yes | yes | no | Entirely new duct system with or without Equipment Changeout | DctLk + FE/AF or Tbl150.0-B,C | e.g. new duct system without equipment changeout |
| j | yes | no | yes | yes | yes | no | Entirely new duct system with or without Equipment Changeout | DctLk + FE/AF or Tbl150.0-B,C | e.g. new furnace + new duct system |
| k | yes | yes | no | yes | yes | no | Entirely new duct system with or without Equipment Changeout | RC + DctLk + FE/AF or Tbl150.0-B,C | e.g. alteration to a refrigerant containing component + new duct system |
| l | yes | yes | yes | yes | yes | no | Entirely new duct system with or without Equipment Changeout | RC + DctLk + FE/AF or Tbl150.0-B,C | e.g. changeout refrigerant containing component + new duct system |
| m | no | no | yes | no | no | yes | Entirely new space conditioning system | none | e.g. new ductless hydronic heating system |
| n | no | yes | yes | no | no | yes | Entirely new space conditioning system | RC | e.g. new mini-split (weigh-in); or new room packeged AC (factory charged) |
| o | yes | no | yes | yes | yes | yes | Entirely new space conditioning system | DctLk + FE/AF or Tbl150.0-B,C | e.g. new ducted hydronic heating system |
| p | yes | yes | yes | yes | yes | yes | Entirely new space conditioning system | RC + DctLk + FE/AF or Tbl150.0-B,C | e.g. new split system |
| q | yes | no | no | yes | no | no | Extension of an existing duct system | DctLk | e.g. altered ducts |
| r | no | no | no | no | no | no | System is exempt from the alteration requirements | none | no alteration performed |
| s | yes | no | no | no | no | no | System is exempt from the alteration requirements | none | no alteration performed |
| t | yes | yes | yes | no | yes | yes | Entirely new space conditioning system | RC + DctLk + FE/AF or Tbl150.0-C,D | e.g. new ducted system that has less than 40 ft of ducts |
| Nomenclature: RC = Refrigerant Charge Verification (MCH-25) DctLk = Duct Leakage Test (MCH-20) FE/AF or Tbl150.0-B,C - Fan Efficacy and Airflow Rate verification (MCH-22; MCH-23) or alternative compliance: (MCH-28) |  |  |  |  |  |  |  |  |  |

| C. Space Conditioning (SC) System Alterations Compliance Information << require one row of data in this table for each of the SC Systems listed in Section B for which Alteration Type in B10≠ no alteration performed >> |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
| SC Identification or Name | Heating System Type | Altered Heating Component | Heating Efficiency Type | Heating Minimum Efficiency Value | Cooling System Type | Altered Cooling Components | Cooling Efficiency Type | Cooling Minimum Efficiency Value | Required Thermostat Type | New or Replaced Duct Length | New Duct R-Value | Central Fan Integrated (CFI) Ventilation System Status |
| <<reference value from B01>> | << reference value from CF1R as default; allow user to override the default and pick one from list: *central gas furnace; *central split HP; *central packaged HP *central large packaged HP *ductless mini-split HP; *room HP; *boiler; *hydronic; *combined hydronic; *hydronic+forced air; *combined hydronic+forced air; *hydronic HP, *hydronic HP+forced air; *gas wall furnace; *gas space heater; *electric; *non-air-source heat pump; *Wood Heat; *N/A (no heating); *Small duct high velocity HP; *Ductless multi-split HP; *Ductless VRF HP; *Packaged gas furnace flag non-default values and report in project status notes field; a revised CF1R may be required >> | << reference value from CF1R as default; allow user to override the default and pick as many as are applicable from list: *gas furnace AHU; *fancoil AHU; *outdoor condensing unit; *indoor coil; *boiler; *TXV or EXV; *compressor; *refrigerant lineset; *no heating component altered; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<if C02 = hydronic, hydronic = forced air, combined hydronic, combined hydronic + forced air, hydronic HP or hydronic HP + forced air, then display NA; else reference value from CF1R as default; if C03 = no heating component altered, then value =n/a else allow user to override the default and pick one from list: *AFUE; *HSPF; *COP; flag non-default values and report in project status notes field; a revised CF1R may be required >> | << if C02 = hydronic, hydronic = forced air, combined hydronic, combined hydronic + forced air, hydronic HP or hydronic HP + forced air, then display NA; else reference value from CF1R as default; if C03 = no heating component altered, then value =n/a else allow user to override the default to enter value: user enter value: xx.x; default minimum value for AFUE= 80; or default minimum value for HSPF= 8.0; allow user to overwrite default value, but flag non-default values and report in project status notes field a revised CF1R may be required>> | <<reference value from CF1R as default; allow user to override the default and pick one from list: *central split AC; *central split HP *central packaged AC ; *central packaged HP *central large packaged AC ; * central large packaged HP *ductless mini-split AC; *ductless mini-split HP; *gas absorption AC *room AC; *room HP; *hydronic HP, *hydronic HP+forced air *evaporative - direct *evaporative - indirect *evaporative - indirectdirect *evaporatively cooled condenser *Ice Storage AC *non-air-source heat pump; *non-air-cooled air conditioner; *no cooling; *Small duct high velocity HP; *Small duct high velocity AC; *Ductless multi-split HP; *Ductless multi-split AC; *Ductless VRF HP; *Ductless VRF AC; flag non-default values and report in project status notes field; a revised CF1R may be required >> | << reference value from CF1R as default; allow user to override the default and pick as many as are applicable from list: *outdoor condensing unit, *indoor fancoil AHU, *indoor coil, *TXV or EXV, *Compressor, *refrigerant lineset, *no cooling component altered; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; if C07= no cooling component altered, then value =n/a else allow user to override the default;to enter value: user pick from list: *SEER; *EER; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<reference value from CF1R as default; if C07= no cooling component altered, then value =n/a else allow user to override the default to enter value: xx.x; default minimum value for SEER=13; allow user to overwrite default value, but flag non-default values and report in project status notes field a revised CF1R may be required >> | <<If alteration type in B10=Extension of Existing Duct System; then display result: "N/A"; else display result: "setback">> | <<calculated field: if B04=no, then display N/A; else reference value from CF1R as default; allow user to override the default and pick one from list: *≤40ft; *>40ft; *N/A - no ducts replaced; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<calculated field: if B04=no, then display N/A; elseif C11=N/A, then display N/A; elsif C11≠N/A, then, if A02= CZ 1-10, 12, 13, then R-6.; elseif A02=CZ 11, 14-16 then R-8; end>> | <<user pick one from list: *CFI System *Not CFI>> |

| D. Installed Heating Equipment Information << If all systems listed in Section C have a value in C03= no heating component altered, then display the section does not apply message; else require one row of data in this table for each of the SC Systems listed in Section C that do not have a value in C03= no heating component altered>> |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| SC Identification or Name | Heating Efficiency Type | Heating Efficiency Value | Heating Unit Manufacturer | Heating Unit Model Number | Heating Unit Serial Number | Rated Heating Capacity, Output (Btu/h) |
| <<reference value from B01>> | <<reference value from C04>> | <<if C05 = NA, then report NA; Else user input, numeric, xx.x; check value must be ≥ value in C05, to comply; else flag non-compliant value and do not allow this document to be registered >> | <<user input alphanumeric text string max 50? characters>> | <<user input alphanumeric text string max 50? characters>> | <<user input alphanumeric text string max 50? characters>> | <<user input, numeric, xxxx>> |
| Notes: |  |  |  |  |  |  |  |

| E. Installed Cooling Equipment Information: <<if all of the SC Systems listed in Section C have a value in C06=no cooling, then display the section does not apply message; else require one row of data in this table for each of the SC Systems listed in Section C that do not have: a value in C06=no cooling or a value in C07 = no cooling component altered >> |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 |
| SC Identification or Name | Cooling Efficiency Type | Cooling Efficiency Value | Condenser or Package Unit Manufacturer | Condenser or Package Unit Model Number | Condenser or Package Unit Serial Number | System Rated Cooling Capacity at Design Conditions (Btu/h) | Condenser Rated Nominal Capacity (ton) |
| <<reference value from C01>> | <<reference value from C08>> | <<user input, numeric, xx.x; check value must be ≥ value in C09 to comply; else flag non-compliant value and do not allow this document to be registered >> | <<user input alphanumeric text string max 50? characters>> | <<user input alphanumeric text string max 50? characters>> | <<user input alphanumeric text string max 50 characters>> | <<user input, numeric, xxxxxx>> | <<user input, numeric, x.x>> |
| Notes: |  |  |  |  |  |  |  |

| F. Extension of Existing Duct System, Greater Than 40 Feet <<Require one row of data to be entered in this table for each SC System for which B07 = Yes AND B08 = No; else display section header and the standard “This section does not apply” message>> |  |  |
| --- | --- | --- |
| 01 | 02 |  |
| SC Identification or Name | New Duct R-Value |  |
| <<reference value from B01>> | <<user pick from list: R-6, R-8, R-10, R-12; check value: must be ≥ value in C12 to comply >> |  |

| G. Installed Duct System information <<if all SC systems in section B have a value in B04=no, then display the section does not apply message; elsif there are no SC Systems listed in Section B for which a yes response was given in B08, or B09, then display the section does not apply message; elseif a space conditioning system in Section B has a value in B04=yes, then if B08=yes, then require one row of data in this table elsif B09=yes, then require one row of data in this table end end>> |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 |
| SC System Identification or Name | SC System Location or Area Served | Supply Duct Location | Supply Duct R-Value | Return Duct Location | Return Duct R-Value | Method of Compliance with Duct and Filter Grille Sizing Req's in 150.0(m)13 | Number of Air Filter Devices on System | Can RA3.3 Airflow Protocols be used to test this System? |
| <<reference value from B01>> | <<auto filled from B02>> | <<User pick one from list: * conditioned space-entirely, *conditioned space -except 12ft, *unconditioned attic, *unconditioned crawl space, *controlled ventilation crawl space *unconditioned garage, *unconditioned basement, *outdoors>> | <<user pick from list: R-6, R-8, R-10, R-12; check value: must be ≥ value in C12 to comply >> | <<User pick one from list: * conditioned space-entirely, *conditioned space-except 12ft, *unconditioned attic, *unconditioned crawl space, *controlled ventilation crawl space *unconditioned garage, *unconditioned basement, *outdoors>> | <<user pick from list: R-6, R-8, R-10, R-12; check value: must be ≥ value in C12 to comply >> | <<if C06=no cooling, then result = Exempt - No Cooling; elseif C06= one of the following three system types: **evaporative - direct, or **evaporative - indirect, or **evaporative - indirectdirect, then result = Exempt - Evaporative System; elseif G09=no, then result = Exempt - RA3.3 Protocols are N/A; elseif B09=yes, AND C13=CFI System, then result = HERS Verified Fan Efficacy (W/cfm) and Airflow Rate(cfm/ton); else, user select one from the following two values: **HERS Verified Fan Efficacy (W/cfm) and Airflow Rate (cfm/ton); **HERS verified Return Duct Design per Table 150.0-B, C; >> | <<user enter integer value which will determine number or rows per system in next section>> | <<user pick one from list: **yes **no>> |
|  | Notes: |  |  |  |  |  |  |  |  |

| H. Installed Air Filter Device Information <<if all SC systems in section B have a value in B04=no, then display the section does not apply message; elsif there are no SC Systems listed in Section B for which a yes response was given in B08, or B09, then display the section does not apply message; elseif a space conditioning system in Section B has a value in B04=yes, then if B08=yes, then require one row of data (each) for the quantity of Air filter devices tagged in G08 for all of the System Names in G01 elsif B09=yes, then require one row of data (each) for the quantity of Air filter devices tagged in G08 for all of the System Names in G01 end end>> |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| SC System Identification or Name | SC System Location or Area Served | Air Filter Identification or Name | Air Filter Device Type | Air Filter Device Location | Determined Design Airflow Rate for Air Filter Device (cfm) | Determined Design Allowable Pressure Drop for Air Filter Device (inch W.C.) |
| <<reference value from B01>> | <<auto filled from B02>> | <<user input text, maximum 20? characters>> | <<user select fom list: *Filter Grille *Furnace Mounted *Duct Mounted >> | <<user input text, maximum 30 characters>> | <<user enter value numeric; xxx>> | <<user enter value, numeric, x.xx>> |
| Notes: |  |  |  |  |  |  |

| I. Air Filter Device Requirements <<if all SC systems in section B have a value in B04=no, then display the section does not apply message; elsif there are no SC Systems listed in Section B for which a yes response was given in B08, or B09, then display the section does not apply message, else display this section>> |  |
| --- | --- |
| 01 | The system shall be designed to ensure that all recirculated air and all outdoor air supplied to the occupiable space is filtered before passing through the system's thermal conditioning components. |
| 02 | The system shall be designed to accommodate the clean-filter pressure drop imposed by the system air filter device(s). The design airflow rate and maximum allowable clean-filter pressure drop at the design airflow rate applicable to each air filter device shall be determined, and all system air filter device locations shall be labeled to disclose the applicable design airflow rate and the maximum allowable clean-filter pressure drop. The labels shall be permanently affixed to the air filter device, readily legible, and visible to a person replacing the air filter media, and the air filter devices shall be provided with air filter media that conforms to these determined/labeled maximum allowable clean-filter pressure drop values as rated using AHRI Standard 680. |
| 03 | All system air filter devices shall be located and installed in such a manner as to allow access and regular service by the system owner. |
| 04 | The system shall be provided with air filter media having a designated efficiency equal to or greater than MERV 6 when tested in accordance with ASHRAE Standard 52.2, or a particle size efficiency rating equal to or greater than 50% in the 3.0–10 micron range when tested in accordance with AHRI Standard 680. |
| 05 | The system shall be provided with air filter media that has been labeled by the manufacturer to disclose the efficiency and pressure drop ratings that conform to the required efficiency and pressure drop requirements for the air filter device. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| J. HERS Verification Requirements << require one row of data in this table for each of the SC Systems listed in Section C >> |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
|  |  |  | MCH-20 |  | MCH-21 | MCH-22 | MCH-23 | MCH-25 | MCH-28 |
| SC System Identification or Name | SC System Location or Area Served | Exemption From Duct Leakage Requirements | Duct Leakage Test | Exemption from Minimum R-Value for Ducts In Conditioned Space | Duct Location Verification | AHU Fan Efficacy (W/cfm) | AHU Airflow Rate (cfm/ton) | Refrigerant Charge | Return Duct Design - Table 150.0-B or C |
| <<reference value from B01>> | <<auto filled from B02>> | << calculated field: If B04=no, then value=N/A; else Default Value=No Exemptions; allow user to override the default and pick one from list: * Ducts have previously been sealed, tested, and certified by a HERS rater; * Duct system has less than 40 ft of duct; * Duct system is insulated or sealed with asbestos; flag non-default values and report in project status notes field; The enforcement agency may require additional documentation as validation>> | <<Calculated field: if value in B04=no (system with no ducts), then display result in this field=no elseif J03=N/A, then display result in this field=no, elseif J03 ≠ No Exemptions, then display result = no; elseif J03= No Exemptions, then determine the result for this field by the user responses in B04, B05 , B06, B07, B08, B09 and use of Logic Table for Determining Alteration Type and HERS Verification Requirements (inserted below section B); constrain user input for fields B04-B09 to allow only the available combinations of responses given in the Logic Table in rows a through q; If the term "DctLk" appears in the HERS column, then display result=yes in this field (duct leakage test required); elsif the term "DctLk" does not appear in the HERS column, then display result=no in this field >> | << Default Value=No Exemption >> | << display result=no>> | << Calculated field: if value in B04=no (system with no ducts), then display result in this field=no elseif the value in G07= HERS Verified Fan Efficacy (W/cfm) and Airflow Rate (cfm/ton), then display result in this field=yes; elseif all of the following three conditions are true: **B09=yes **C06=no cooling **C13=CFI System, then result= yes; else display result=no>> | << Calculated field: if value in B04=no (system with no ducts), then display result in this field=no elseif the value in G07= HERS Verified Fan Efficacy (W/cfm) and Airflow Rate (cfm/ton), then display result in this field="yes"; elseif the value in J09=yes, AND the value in J10=no, then result in this field=yes elseif all of the following three conditions are true: **B09=yes **C06=no cooling **C13=CFI System, then result= yes; else display result="no">> | << Calculated field: If [C06 or C02] = one of the following 2 values: *non-airsource heat pump *non-air-cooled air conditioner Then result = no; Else determine value by the user responses in B04, B05 , B06, B07, B08, B09 and use of "Logic Table for Determining Alteration Type and HERS Verification Requirements" (inserted below section B); constrain user input for fields B04-B09 to allow only the available combinations of responses given in the Logic Table in rows a through t; If the term "RC" appears in the HERS column, and A02 =one of the CZ values in the following list: 2,8,9,10,11,12,13,14,or15, then display result = yes in this field; else display result = no>> | << Calculated field: if value in B04=no (system with no ducts), then display result in this field=no elseif the value in G07= HERS verified Return Duct Design per Table 150.0-B, C; then display result in this field="yes"; else display result="no">> |
| Notes: |  |  |  |  |  |  |  |  |  |

| K. Space Conditioning Systems, Ducts and Fans – Mandatory Requirements and Additional Measures Note: Additional mandatory requirements from Section 150.0 that are not listed here may be applicable to some systems. These requirements may be applicable to only newly installed equipment or portions of the system that are altered. Existing equipment may be exempt from these requirements. |  |
| --- | --- |
| Heating Equipment |  |  |
| 01 |  | Equipment Efficiency: All heating equipment must meet the minimum efficiency requirements of Section 110.1 and Section 110.2(a) and the Appliance Efficiency Regulations. |
| 02 |  | Controls: All unitary heating systems, including heat pumps, must be controlled by a setback thermostat. These thermostats must be capable of allowing the occupant to program the temperature set points for at least four different periods in 24 hours. See Sections 150.0(i), 110.2(b). |
| 03 |  | Sizing: Heating load calculations must be done on portions of the building served by new heating systems to prevent inadvertent undersizing or oversizing. See sections 150.0(h)1 and 2). |
| 04 |  | Furnace Temperature Rise: Central forced-air heating furnace installations must be configured to operate at or below the furnace manufacturer's maximum inlet-to-outlet temperature rise specification. See Section 150.0(h)4. |
| 05 |  | Standby Losses and Pilot Lights: Fan-type central furnaces may not have a continuously burning pilot light. Section 110.5 and Section 110.2(d). |
| Cooling Equipment |  |  |
| 06 |  | Equipment Efficiency: All cooling equipment must meet the minimum efficiency requirements of Section 110.1 and Section 110.2(a) and the Appliance Efficiency Regulations. |
| 07 |  | Refrigerant Line Insulation: All refrigerant line insulation in split system air conditioners and heat pumps must meet the R-value and protection requirements of Section 150.0(j)2 and 3, and Section 150.0(m)9. |
| 08 |  | Condensing Unit Location: Condensing units shall not be placed within 5 feet of a dryer vent outlet. See Section 150.0(h)3A. |
| 09 |  | Liquid Line Filter Drier: If applicable, a liquid line filter drier shall be installed according to the manufacturer’s specifications. |
| 10 |  | Sizing: Cooling load calculations must be done on portions of the building served by new cooling systems to prevent inadvertent undersizing or oversizing. See Section 150.0(h)1 and 2. |
| Air Distribution System Ducts, Plenums and Fans |  |  |
| 11 |  | Insulation: In all cases, unless ducts are enclosed entirely in directly conditioned space, the minimum duct insulation value is R-6. Note that higher values may be required by the prescriptive or performance requirements. See Section 150.0(m)1. |
| 12 |  | Connections and Closures: All installed air-distribution system ducts and plenums must be, sealed and insulated to meet the requirements of CMC Sections 601.0, 602.0, 603.0, 604.0, 605.0 and ANSI/SMACNA-006-2006: Supply-air and return-air ducts and plenums must be insulated to a minimum installed level of R-6.0 or enclosed entirely in directly conditioned space as confirmed through field verification and diagnostic testing in accordance with the requirements of Reference Residential Appendix RA3.1.4.3.8. |
| Heat Pump Thermostat |  |  |
| 13 |  | A thermostat shall be installed that meets the requirements of Section 110.2(b) and Section 110.2(c). |
| 14 |  | The thermostat shall be installed in accordance with the manufacturers published installation specifications. |
| 15 |  | First stage of heating shall be assigned to heat pump heating. |
| 16 |  | Second stage back up heating shall be set to come on only when the indoor set temperature cannot be met. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| ### I certify that this Certificate of Installation documentation is accurate and complete. |  |  |  |
| Documentation Author Name: |  | Documentation Author Signature: |  |
| Documentation Author Company Name: |  | Date Signed: |  |
| Address: |  | CEA/HERS Certification Identification (If applicable): |  |
| City/State/Zip: |  | Phone: |  |
| Responsible Person's Declaration statement |  |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: ### The information provided on this Certificate of Installation is true and correct. - I am either: a) a responsible person eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction, or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Installation, and attest to the declarations in this statement, or b) I am an authorized representative of the responsible person and attest to the declarations in this statement on the responsible person’s behalf. - The constructed or installed features, materials, components or manufactured devices (the installation) identified on this Certificate of Installation conforms to all applicable codes and regulations and the installation conforms to the requirements given on the Certificate of Compliance, plans, and specifications approved by the enforcement agency. - I will ensure that a registered copy of this Certificate of Installation shall be posted or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Installation is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| Responsible Builder/Installer Name: | Responsible Builder/Installer Signature: |  |  |
| Company Name: (Installing Subcontractor or General Contractor or Builder/Owner) | Position With Company (Title): |  |  |
| Address: | CSLB License: |  |  |
| City/State/Zip: | Phone: |  | Date Signed: |