| A. General Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | Dwelling Unit Name |  | 02 | Climate Zone |  |
| 03 | Dwelling Unit Total Conditioned Floor Area (ft2) |  | 04 | Number of Space Conditioning Systems in this dwelling unit |  |
| 05 | Certificate of Compliance Type |  | 06 | Method used to calculate HVAC loads |  |
| 07 | Calculated Dwelling Unit Sensible Cooling Load (Btu/h) |  | 08 | Calculated Dwelling Unit Heating Load (Btu/h) |  |
| 09 | Dwelling Unit Number of Bedrooms |  |  |  |  |

MCH-01d - Space Conditioning Systems Ducts and Fans - For use with Performance E+A+A Certificate of Compliance

| B. Design Space Conditioning (SC) System Component Specifications from CF1R This table reports the space conditioning system features that were specified on the registered CF1R-PRF compliance document for this project. |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | SC System Type | Heating System Type | Cooling System Type | SC System Fan Type | Distribution System Type | Required Thermostat Type | Low Leakage Air-Handling Unit (LLAHU) Status | SC System Status | Duct System Status |
| Notes: |  |  |  |  |  |  |  |  |  |

| C. Design Space Conditioning (SC) System Compliance Requirements from CF1R This table reports the space conditioning system features that were specified on the registered CF1R-PRF compliance document for this project. |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | Heating Efficiency Type | Minimum Heating Efficiency Value | Heat Pump Heating Capacity @ 47°F | Heat Pump Heating Capacity @ 17°F | Minimum Cooling Efficiency SEER | Minimum Cooling Efficiency EER | Minimum Cooling System Airflow Rate (CFM/ton) | Maximum Fan Efficacy (W/CFM ) | Modeled R-Value for Ducts |
| Notes: |  |  |  |  |  |  |  |  |  |

| D. Installed New, Altered, and Existing Space Conditioning (SC) System Component Information |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
| SC System Identification or Name | SC System Location or Area Served | Conditioned Floor Area Served by the System (ft2) | Heating System Type | Cooling System Type | SC System Fan Type | Distribution System Type | SC System Thermostat Type | Central Fan Integrated (CFI) Vent System Status | New or Replaced Duct Length | New Duct R-Value | SC System Status | Duct System Status |
| Notes: |  |  |  |  |  |  |  |  |  |  |  |  |

| E. Space Conditioning (SC) System Alteration Type Determination |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 9 | 10 | 11 |
| SC System Identification or Name | SC System Location or Area Served | Is the SC system a ducted system? | Installing refrigerant containing component? | Installing new SC System component? | Installing more than 40 feet of ducts? | Installing entirely new duct system? | Installing entirely new SC system? | Alteration Type | Altered Heating Components | Altered Cooling Components |

| F. Installed Heating System Equipment Information (not heat pumps) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 |
| SC System Identification or Name | SC System Location or Area Served | Heating Efficiency Type | Heating Efficiency Value | Heating Unit Manufacturer | Heating Unit Model Number | Heating Unit serial number | Rated Heating Capacity, Output (Btu/h) |
| Notes: |  |  |  |  |  |  |  |

| G. Installed Cooling System Outdoor Condensing Unit or Package Unit Equipment Information (not heat pumps) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 |
| SC System Identification or Name | SC System Location or Area Served | Cooling Efficiency SEER | Cooling Efficiency EER | Condenser or Package Unit Manufacturer | Condenser or Package Unit Model Number | Condenser or Package Unit Serial Number | System Rated Cooling Capacity at Design Conditions (Btu/h) | Condenser Rated Nominal Cooling Capacity (ton) |
| Notes: |  |  |  |  |  |  |  |  |

| H. Installed Split System Indoor Coil or Fan Coil Unit Equipment Information (applicable to DX or hydronic heating/cooling coils or fan coil units) |  |  |  |  |
| --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 |
| SC System Identification or Name | SC System Location or Area Served | Indoor Coil or Fan Coil Unit Manufacturer | Indoor Coil or Fan Coil Unit Model Number | Indoor Coil or Fan Coil Unit Serial Number |
| Notes: |  |  |  |  |

| I. Installed Heat Pump System – Split System Condensing Unit or Package Unit Equipment Information |  |  |  |  |
| --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 |
| SC System Identification or Name | SC System Location or Area Served | Condenser or Package Unit Manufacturer | Condenser or Package Unit Model Number | Condenser or Package Unit Serial Number |
| Notes: |  |  |  |  |

| J. Installed Heat Pump System – Efficiency and Performance Compliance Information |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | SC System Location or Area Served | Heating Efficiency Type | Heating Efficiency Value | System Rated Heating Capacity at 47°F | System Rated Heating Capacity at 17°F | System Rated Cooling Efficiency SEER | System Rated Cooling Efficiency EER | System Rated Cooling Capacity at Design Conditions (Btu/h) | Condenser Rated Nominal Cooling Capacity (ton) |
| Notes: |  |  |  |  |  |  |  |  |  |

| K. Extension of Existing Duct System, Greater Than 40 Feet |  |  |  |
| --- | --- | --- | --- |
| 01 | 02 | 03 |  |
| SC System Identification or Name | SC System Location or Area Served | New Duct R-Value |  |

| L. Installed Duct System Information |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System ID or Name | SC System Location or Area Served | Supply Duct Location | Supply Duct R-Value | Return Duct Location | Return Duct R-Value | Exemption from Min R-Value for Ducts In Conditioned Space | Method of compliance with duct and filter grille sizing Req's in 150.0(m)13 | Number of Air Filter Devices on System | Can RA3.3 Airflow Protocols be used to test this System? |
| Notes: |  |  |  |  |  |  |  |  |  |

| M. Installed Air Filter Device Information Mandatory requirements for air filter devices are specified Section 150.0(m)12. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| SC System Identification or Name | SC System Location or Area Served | Air Filter Identification or Name | Air Filter Device Type | Air Filter Device Location | Determined Design Airflow Rate for Air Filter Device (cfm) | Determined Design Allowable Pressure Drop for Air Filter Device (inch W.C.) |
| Notes: |  |  |  |  |  |  |  |

| N. Air Filter Device Requirements |  |
| --- | --- |
| 01 | The system shall be designed to ensure that all recirculated air and all outdoor air supplied to the occupiable space is filtered before passing through the system's thermal conditioning components. |
| 02 | The system shall be designed to accommodate the clean-filter pressure drop imposed by the system air filter device(s). The design airflow rate and maximum allowable clean-filter pressure drop at the design airflow rate applicable to each air filter device shall be determined, and all system air filter device locations shall be labeled to disclose the applicable design airflow rate and the maximum allowable clean-filter pressure drop. The labels shall be permanently affixed to the air filter device, readily legible, and visible to a person replacing the air filter media, and the air filter devices shall be provided with air filter media that conforms to these determined/labeled maximum allowable clean-filter pressure drop values as tested using ASHRAE Standard 52.2 or rated using AHRI Standard 680 |
| 03 | All system air filter devices shall be located and installed in such a manner as to allow access and regular service by the system owner. |
| 04 | The system shall be provided with air filter media having a designated efficiency equal to or greater than MERV 6 when tested in accordance with ASHRAE Standard 52.2, or a particle size efficiency rating equal to or greater than 50 percent in the 3.0–10 μm range when tested in accordance with AHRI Standard 680. |
| 05 | The system shall be provided with air filter media that has been labeled by the manufacturer to disclose the efficiency and pressure drop ratings that conform to the required efficiency and pressure drop requirements for the air filter device. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| O. HERS Verification Requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
|  |  |  | MCH-20 | MCH-21 | MCH-22 | MCH-23 | MCH-25 | MCH-26 | MCH-27 | MCH-28 | MCH-29 | MCH30 |
| SC System Identification or Name | SC System Location or Area Served | Exemption from Duct Leakage Requirements | Duct Leakage Test | Duct Location Verification | AHU Fan Efficacy (W/cfm) | AHU Airflow Rate (cfm/ton) | Refrigerant Charge | Rated SC System Equipment Verification | IAQ Mechanical Ventilation | Return Duct Design - Table 150.0-B or C | Supply Duct Surface Area R-Value Buried Ducts | Ventilation Cooling Credit |
| Notes: |  |  |  |  |  |  |  |  |  |  |  |  |

| P. Space Conditioning Systems, Ducts and Fans – Mandatory Requirements and Additional Measures Note: Additional mandatory requirements from Section 150.0 that are not listed here may be applicable to some systems. These requirements may be applicable to only newly installed equipment or portions of the system that are altered. Existing equipment may be exempt from these requirements. |  |
| --- | --- |
| Heating Equipment |  |  |  |
| 01 |  | Equipment Efficiency: All heating equipment must meet the minimum efficiency requirements of Section 110.1 and Section 110.2(a) and the Appliance Efficiency Regulations. |  |
| 02 |  | Controls: All unitary heating systems, including heat pumps, must be controlled by a setback thermostat. These thermostats must be capable of allowing the occupant to program the temperature set points for at least four different periods in 24 hours. See Sections 150.0(i), 110.2(b). |  |
| 03 |  | Sizing: Heating load calculations must be done on portions of the building served by new heating systems to prevent inadvertent undersizing or oversizing. See sections 150.0(h)1 and 2). |  |
| 04 |  | Furnace Temperature Rise: Central forced-air heating furnace installations must be configured to operate at or below the furnace manufacturer's maximum inlet-to-outlet temperature rise specification. See Section 150.0(h)4. |  |
| 05 |  | Standby Losses and Pilot Lights: Fan-type central furnaces may not have a continuously burning pilot light. Section 110.5 and Section 110.2(d). |  |
| Cooling Equipment |  |  |  |
| 06 |  | Equipment Efficiency: All cooling equipment must meet the minimum efficiency requirements of Section 110.1 and Section 110.2(a) and the Appliance Efficiency Regulations. |  |
| 07 |  | Refrigerant Line Insulation: All refrigerant line insulation in split system air conditioners and heat pumps must meet the R-value and protection requirements of Section 150.0(j)2 and 3, and Section 150.0(m)9. |  |
| 08 |  | Condensing Unit Location: Condensing units shall not be placed within five (5) feet of a dryer vent outlet. See Section 150.0(h)3A. |  |
| 09 |  | Sizing: Cooling load calculations must be done on portions of the building served by new cooling systems to prevent inadvertent undersizing or oversizing. See Section 150.0(h)1 and 2. |  |
| Air Distribution System Ducts, Plenums and Fans |  |  |  |
| 10 |  | Insulation: In all cases, unless ducts are enclosed entirely in directly conditioned space, the minimum duct insulation value is R-6. Note that higher values may be required by the prescriptive or performance requirements. See Section 150.0(m)1. |  |
| 11 |  | Connections and Closures: All installed air-distribution system ducts and plenums must be, sealed and insulated to meet the requirements of CMC Sections 601.0, 602.0, 603.0, 604.0, 605.0 and ANSI/SMACNA-006-2006: Supply-air and return-air ducts and plenums must be insulated to a minimum installed level of R-6.0 or enclosed entirely in directly conditioned space as confirmed through field verification and diagnostic testing in accordance with the requirements of Reference Residential Appendix RA3.1.4.3.8. |  |
| Heat Pump Thermostat |  |  |  |
| 12 |  | A thermostat shall be installed that meets the requirements of Section 110.2(b) and Section 110.2(c). |  |
| 13 |  | The thermostat shall be installed in accordance with the manufacturers published installation specifications. |  |
| 14 |  | First stage of heating shall be assigned to heat pump heating. |  |
| 15 |  | Second stage back up heating shall be set to come on only when the indoor set temperature cannot be met. |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |  |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| ### I certify that this Certificate of Installation documentation is accurate and complete. |  |  |  |
| Documentation Author Name: |  | Documentation Author Signature: |  |
| Documentation Author Company Name: |  | Date Signed: |  |
| Address: |  | CEA/HERS Certification Identification (If applicable): |  |
| City/State/Zip: |  | Phone: |  |
| Responsible Person's Declaration statement |  |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: ### The information provided on this Certificate of Installation is true and correct. - I am either: a) a responsible person eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction, or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Installation, and attest to the declarations in this statement, or b) I am an authorized representative of the responsible person and attest to the declarations in this statement on the responsible person’s behalf. - The constructed or installed features, materials, components or manufactured devices (the installation) identified on this Certificate of Installation conforms to all applicable codes and regulations and the installation conforms to the requirements given on the Certificate of Compliance, plans, and specifications approved by the enforcement agency. - I will ensure that a registered copy of this Certificate of Installation shall be posted or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Installation is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| Responsible Builder/Installer Name: | Responsible Builder/Installer Signature: |  |  |
| Company Name: (Installing Subcontractor or General Contractor or Builder/Owner) | Position With Company (Title): |  |  |
| Address: | CSLB License: |  |  |
| City/State/Zip: | Phone: |  | Date Signed: |

CF2R-MCH-01d-E User Instructions

Section A. General Information

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. When the project scope includes an addition to an existing building, the value is equal to the sum of the existing conditioned floor area plus the conditioned floor area of the addition.  The default value from the CF1R-PRF may be overwritten in this document.  Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- Oversized equipment can result in reduced efficiency and capacity. Entirely new systems (see definition in Section 9.6.9 of the RCM) must be properly sized to match the heating and cooling load of the space that it serves. To do this, heating and cooling load calculations must be performed using an approved calculation methodology. These are listed here. Select the load calculation methodology used for this dwelling unit. If the project consists of a partial replacement of equipment or ducts (change-out) then load calculations are not required. Select N/A. Load calculations are always recommended, especially if the loads of the house have been changed since the original equipment has been installed (reduced via weatherization, other improvements).

- Enter the total sensible cooling load for the dwelling unit described by this document.  For projects involving dwelling units with more than one system, this will be a sum of the loads for the parts of the dwelling unit served by those systems. If the project consists of a partial replacement of equipment or ducts (change-out) then load calculations are not required. Select N/A.

- Enter the total heating load for the dwelling unit described by this document. For projects involving dwelling units with more than one system, this will be a sum of the loads for the parts of the dwelling unit served by those systems. If the project consists of a partial replacement of equipment or ducts (change-out) then load calculations are not required. Select N/A.

- Enter the number of bedrooms in the dwelling unit.  This field is filled out automatically using the default value from the CF1R-PRF for performance compliance, and is user entry for prescriptive compliance.  The default value from the CF1R-PRF may be overwritten in this document.  Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

Section B. Design Space Conditioning (SC) System Component Specifications from CF1R

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is determined based on entries on the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is determined based on entries on the Certificate of Compliance (CF1R), which must be completed prior to this document.

Section C. Design Space Conditioning (SC) System Compliance Requirements from CF1R

- This field is filled out automatically. It is referenced from the same row and column in the previous section.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

- This field is filled out automatically. It is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document.

Section D. Installed New, Altered, and Existing Space Conditioning (SC) System Component Information

- Select System name from the list of systems identified in previous sections and originally specified on the CF1R.

- Briefly describe the area served by this system. Examples: entire house, upstairs, downstairs, sleeping area, north wing, etc.

- Enter the conditioned floor area served by the system described in this row. The total value of this column for all rows must equal the total dwelling unit conditioned floor area as shown in Section A.

- This field is filled out automatically. It appears in Section B and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It appears in Section B and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It appears in Section B and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It appears in Section B and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It appears in Section B and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- Central fan integrated ventilation systems may be subject to additional field verification. See definition in Section 100.1 of the 2013 Building Energy Efficiency Standards. Select the correct description that applies to the system described in this row.

- This field is filled out automatically if it appears on the CF1R otherwise enter the duct length.

- This field is filled out automatically.

- This field is filled out automatically. It appears in Section B and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It appears in Section B and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

Section E. Space Conditioning (SC) System Alteration Type Determination

- SC System Identification or Name: Enter a unique identifier for this system that will readily distinguish it from other systems in the dwelling unit, such as “HVAC1,” “upstairs system,” etc. It is recommended to mark the system with this identifier using a permanent marker for ease of identification in the field. For single-system dwelling units, enter a simple name such as “HVAC.”

- SC System Location or Area Served: Enter a unique description of the portion of dwelling unit served by this system, such as “entire second floor,” “bedroom wing,” etc. For single-system dwelling units, enter a simple description such as “entire house.”

- Is the altered or installed system a ducted system? Select “YES” if the system has a central air handler (package or split) that is connected to one or more supply air outlets via ducting of any shape or material. Select “NO” for nonducted systems such as ductless mini-splits, through-the-wall systems, package terminal air conditioners, etc.

- Altering or installing a refrigerant containing component? Select “YES” if the project includes installing or replacing a component that contains refrigerant; otherwise select “NO.” Refrigerant containing components include compressors, condensing coils, evaporator coils, refrigerant metering devices or refrigerating lines.

- Installing new components? Select “YES” if new HVAC components such as a packaged unit, condensing unit, cooling/heating coil, or air-handling unit (e.g. furnace), etc. are being installed in the system; otherwise select “NO.”

- Installing more than 40 linear feet of new or replacement ducts? Select “YES” if the project involves installing more than 40 linear feet of new or replacement ducts; otherwise select “NO.”

- Is the entire duct system accessible for sealing and is more than 75% of the duct system new or replaced? Select “YES” when, upon completion of the project, more that 75% of the ducts will be new ducts and/or replaced ducts, AND if at any time during the project all of the ducts are accessible for duct sealing; otherwise select “NO.” “Accessible” is defined in Joint Appendix JA1 of the 2013 Reference Appendices (glossary).

- Are all of the system's components and ducts new (entirely new system) or replaced? Select “YES” if the duct system meets the definition of an “Entirely New or Replacement Duct System” and all of the heating and cooling components (furnace, condenser, coil, etc.) are all new or replaced; otherwise select “NO.”

- Alteration Type: This field is calculated automatically based on the information entered in previous fields. Alteration types are defined in Joint Appendix JA1 of the 2013 Reference Appendices. The alteration type will determine which of the following sections are required by this document.

- Altered Heating Components.  select all that are applicable

- Altered Cooling Components.  select all that are applicable

Section F. Installed Heating System Information (not heat pumps)

- This field is filled out automatically. It is referenced from the same row and column in the previous section.

- This field is filled out automatically. It is referenced from the same row and column in the previous section.

- This field is filled out automatically. It is referenced from the same row and column in Section C.

- Enter the certified heating efficiency of the installed equipment. This value is verified against the minimum value shown in Section C. The installed efficiency must be greater than or equal to the required minimum efficiency.

- Enter the name of the installed Heating Unit Manufacturer as shown on the equipment nameplate.

- Enter the name of the installed Heating Unit Model Number as shown on the equipment nameplate.

- Enter the name of the installed Heating Unit Serial number as shown on the equipment nameplate.

- Enter the rated heating capacity (output) of the installed Heating Unit in BTUs per hour.

Section G. Installed Cooling System Outdoor Unit or Package Unit Equipment Information (not heat pump)

- This field is filled out automatically. It is referenced from the same row and column in the previous section.

- This field is filled out automatically. It is referenced from the same row and column in the previous section.

- Enter the certified cooling efficiency (SEER) of the installed equipment. This value is verified against the minimum value shown in Section C.  The installed efficiency must be greater than or equal to the required minimum efficiency.

- Enter the certified cooling efficiency (EER) of the installed equipment. This value is verified against the minimum value shown in Section C.  The installed efficiency must be greater than or equal to the required minimum efficiency.

- Enter the name of the installed Condenser or Package Unit Manufacturer as shown on the equipment nameplate.

- Enter the name of the installed Condenser or Package Unit Model Number as shown on the equipment nameplate.

- Enter the name of the installed Condenser or Package Unit Serial Number as shown on the equipment nameplate.

- Enter the rated sensible cooling capacity at design conditions of the installed cooling system in BTUs per hour.

- Enter the installed Condenser Rated Nominal Cooling Capacity in tons. Note that this is based on the condenser, not the coil or air handler. This can usually be determined by the condenser model number.

Section H. Installed Split System Indoor Coil or Fan Coil Unit Equipment information (applicable to DX or hydronic heating/cooling coils or fan coil units)

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- Enter the name of the installed Indoor Coil or Fan Coil Unit Manufacturer as shown on the equipment nameplate.

- Enter the name of the installed Indoor Coil or Fan Coil Unit Model Number as shown on the equipment nameplate.

- Enter the name of the installed Indoor Coil or Fan Coil Unit Serial Number as shown on the equipment nameplate.

Section I. Installed Heat Pump System – Split System Condensing Unit or Package Unit Equipment Information

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- Enter the name of the installed Heat Pump Condenser or Package Unit Manufacturer as shown on the equipment nameplate.

- Enter the name of the installed Heat Pump Condenser or Package Unit Model Number as shown on the equipment nameplate.

- Enter the name of the installed Heat Pump Condenser or Package Unit Serial Number as shown on the equipment nameplate.

Section J. Installed Heat Pump System – Efficiency and Performance Compliance Information

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row in Section C.

- Enter the certified heating efficiency of the installed equipment. This value is verified against the minimum value shown in Section C. The installed efficiency must be greater than or equal to the required minimum efficiency.

- Enter the certified heating capacity at 47F of the installed equipment. This value is verified against the minimum value shown in Section C. The installed capacity must be greater than or equal to the required minimum capacity.

- Enter the certified heating capacity at 17F of the installed equipment. This value is verified against the minimum value shown in Section C. The installed capacity must be greater than or equal to the required minimum capacity.

- Enter the certified cooling efficiency (SEER) of the installed equipment. This value is verified against the minimum value shown in Section C. The installed efficiency must be greater than or equal to the required minimum efficiency.

- Enter the certified cooling efficiency (EER) of the installed equipment. This value is verified against the minimum value shown in Section C. The installed efficiency must be greater than or equal to the required minimum efficiency.

- Enter the rated sensible cooling capacity at design conditions of the installed cooling system in BTUs per hour.

- Enter the installed Condenser Rated Nominal Cooling Capacity in tons. Note that this is based on the condenser, not the coil or air handler. Can usually be determined by the condenser model number.

Section K. Extension of Existing Duct System, Greater Than 40 Feet

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- Enter the R-value of the installed supply ducts. This value is verified against the minimum value shown in Section C. The installed R-value must be greater than or equal to the required minimum R-value.

Section L. Installed Duct System Information

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It appears in Section B and D, and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- Enter the R-value of the installed supply ducts. This value is verified against the minimum value shown in Section C. The installed R-value must be greater than or equal to the required minimum R-value.

- This field is filled out automatically. It appears in Section B and D, and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- Enter the R-value of the installed return ducts. This value is verified against the minimum value shown in Section C. The installed R-value must be greater than or equal to the required minimum R-value.

- The duct system is exempt from the minimum R-value requirement if all of the ducts are located entirely within conditioned space. If indicated as such in the previous columns, the user may select “yes” to indicate the exemption. Note: Selecting “yes” may subject the duct system to additional HERS verification.

- For entirely new duct systems taking the performance credit for better than default air flow or fan efficacy, field verification of these criteria is required and this field is filled out automatically. Otherwise, the user may pick the appropriate choice. Refer to section 150.0(m)13 and Residential Compliance Manual Chapter 4.4 for more information.

- Altered existing duct systems may be exempt from duct sealing and testing requirements. If so, the exemption may be indicated here. The default value here is “No Exemptions”. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- This field is filled out automatically. It appears in Section B, and is referenced from the Certificate of Compliance (CF1R), which must be completed prior to this document. This value may be overwritten in this document but valid discrepancies with the CF1R are atypical. Overwriting the default value will automatically flag this entry and subject it to additional scrutiny by QA and enforcement personnel.

- Specify the number of air filter devices installed in this space conditioning system. Air filter devices installed in completely new systems must be properly sized, as documented in the next section. The value entered here will determine the number of rows needed in the following section.

- If the system is of a type that can use one of the Reference Residential Appendix RA3.3 protocols for testing the airflow rate, then enter yes.  Otherwise enter no. Most ducted split systems and package systems are of the type that minimum airflow can be verified using an approved measurement procedure.  Examples of systems that do not meet this description are ductless systems.  A “No” response here may subject the project to additional scrutiny by enforcement personnel.

Section M. Installed Air Filter Device Information

- This field is filled out automatically. It is referenced from the same row and column in the previous sections.

- This field is filled out automatically. It is referenced from the same row and column in the previous sections

- Enter a descriptive name of each air filter device so that it may be distinguished from others in the same system. Examples: FG1, filter2, etc.

- Select the appropriate type of filter device from the list.

- Enter a descriptive name of each air filter device so that it may be identified in the home. Examples: master suite, main hallway, at furnace, entry wall, etc.

- Enter the design flow in CFM of the filter device. The total for all filter devices in a single system should be greater than or equal to the total system design CFM in cooling mode (or heating mode for heat-only systems).

- Enter the design static pressure drop provided by the filter device manufacturer. This should be consistent with the duct design calculations. Not accounting for higher filter pressure drops will result in poor system airflow characteristics, reduced capacity and reduced efficiency. This may result in not passing field verification.

Section N. Air Filter Device Requirements

<no input fields>

Section O. HERS Verification Requirements

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

- This field is filled out automatically. It is calculated based on data from the CF1R and from previous sections in this document.

Section P. Space Conditioning Systems, Ducts and Fans – Mandatory Requirements and Additional Measures

<no input fields>

| A. General Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 01 | Dwelling Unit Name | <<reference text from CF1R >> | 02 | Climate Zone | << reference text from CF1R>> |
| 03 | Dwelling Unit Total Conditioned Floor Area (ft2) | <<numeric: xxxxx; if1 parent is CF1R-PRF, then if2 project scope = Newly Constructed (Addition Alone) then prompt user to enter a value equal to dwelling unit existing CFA + addition CFA else reference the value from CF1R endif2 elseif parent is CF1R-NCB-01, then if3 project scope = New Addition greater than 1,000 ft2 then prompt user to enter a value equal to dwelling unit existing CFA + addition CFA elseif project scope = Newly Constructed Building, then if4 building type = Single Family, then reference value from CF1R-NCB field A10 elseif Building Type=Multifamily, then reference value from CF1R-NCB field M02 endif4 endif3 elseif parent is CF1R-ADD-01, then if5 building type= Single Family, then reference value from field A08 from the CF1R-ALT-02 that is required for the dwelling unit according to CF1R-ADD-01 Section J. elseif Building Type=Multifamily, then reference value from field A08 from the CF1R-ALT-02 that is required for the dwelling unit according to CF1R-ADD-01 Section L. endif5 elseif parent is CF1R-ALT-01, then if6 building type= Single Family, then reference value from field A08 from the CF1R-ALT-02 that is required for the dwelling unit according to CF1R-ALT-01 Section G. elseif Building Type=Multifamily, then reference value from field A08 from the CF1R-ALT-02 that is required for the dwelling unit according to CF1R-ALT-01 Section letter I. endif6 elseif parent is CF1R-ALT-02, then reference value from CF1R-ALT-02 field A08. endif1 allow user to override default and input a value; flag overridden values and report in project status notes field >> | 04 | Number of Space Conditioning Systems in this dwelling unit | <<integer: xx; If parent is CF1R-ALT-02 doc type, then use as default the value referenced from CF1R ALT-02 Section A (field A10); or allow user to override the default and input a new value; flag non-default values and report in project status notes field; elseif parent is not CF1R-ALT-02 doc type, then user input the integer value>> |
| 05 | Certificate of Compliance Type | << reference document type property from CF1R: allowed values: performance (CF1R-PRF); or prescriptive additions/alterations (CF1R-ADD/CF1R-ALT); or prescriptive newly constructed (CF1R-NCB)>> | 06 | method used to calculate HVAC loads | <<user select from list: *ASHRAE Handbook; *SMACNA Residential Comfort System Installation Standards Manual; *ACCA Manual J *n/a equipment changeout, like-for-like>> |
| 07 | Calculated Dwelling Unit Sensible Cooling Load (Btu/h) | <<user entry: numeric: xxxxx (allow n/a entry if "n/a equipment changeout, like-for-like" is selected in A06) >> | 08 | Calculated Dwelling Unit Heating Load (Btu/h) | <<user entry: numeric: xxxxx (allow n/a entry if "n/a equipment changeout, like-for-like" is selected in A06) >> |
| 09 | Dwelling Unit Number of Bedrooms | <<<<calculated field: integer xx: if CertComplianceType=performance, then use as default the value referenced from CF1R-PRF or allow user to override the default and input a new value; flag non-default values and report in project status notes field; elseif parent is not CF1R-PRF doc type, then user input the integer value xx>> | 10 | Determination of Mech01 type (this field not visible to user) | <<calculated field: if1 CertComplianceType=performance, then if2 CF1R-PRF Project Scope=one of the following two types: **Addition and/or Alteration **Newly Constructed - Addition Alone then display doc variation MCH-01d; elseif CF1R-PRF Project Scope=Newly Constructed, then display doc variation MECH01a endif2 elseif CertComplianceType=prescriptive additions/alterations, then display doc variation MECH01b, elseif CertComplianceType=prescriptive newly constructed, then display doc variation MECH01c (this field not visible to user) endif1>> |

MCH-01d - Space Conditioning Systems Ducts and Fans - For use with Performance E+A+A Certificate of Compliance

| B. Design Space Conditioning (SC) System Component Specifications from CF1R This table reports the space conditioning system features that were specified on the registered CF1R-PRF compliance document for this project. <<require one row of data for each SC System identified on the CF1R report that is applicable to this dwelling unit; do not allow user to overwrite these referenced data >> |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | SC System Type | Heating System Type | Cooling System Type | SC System Fan Type | Distrribution System Type | Required Thermostat Type | Low Leakage Air-Handling Unit (LLAHU) Status | SC System Status | Duct System Status |
| <auto filled text: referenced from CF1R>> | << auto filled text: Reference from CF1R>> | <<auto filled text: referenced from CF1R>> | <<auto filled text: referenced from CF1R>> | <<auto filled text: referenced from CF1R>> | <<auto filled text: referenced from CF1R>> | <<auto filled text referenced from CF1R>> | <<if on CF1R LowLkgAH= true, then value= *Has Low Leakage Air Handler, elsif LowLkgAH= false, then value= *None | <<calculated field: reference value from CF1R for this system name. values are: **new **altered **existing>> | <<calculated field: if B06= DuctsNone, then value=N/A, else reference value from CF1R for this system name. values are: **new **altered **existing **existing +new>> |
| Notes: |  |  |  |  |  |  |  |  |  |

| C. Design Space Conditioning (SC) System Compliance Requirements from CF1R This table reports the space conditioning system features that were specified on the registered CF1R-PRF compliance document for this project. <<require one row of data for each SC System in Section B; do not allow user to overwrite these referenced data>> |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | Heating Efficiency Type | Minimum Heating Efficiency Value | Heat Pump Heating Capacity @ 47°F | Heat Pump Heating Capacity @ 17°F | Minimum Cooling Efficiency SEER | Minimum Cooling Efficiency EER | Minimum Cooling System Airflow Rate (CFM/ton) | Maximum Fan Efficacy (W/CFM ) | Modeled R-Value for Ducts |
| <<auto filled text: referenced from B01>> | <<If B03 = ‘Combined Hydronic’ then report NA; else auto filled text: referenced from CF1R for this system name>> | <<If B03 = ‘Combined Hydronic’ then report NA; else auto filled text: referenced from CF1R for this system name>> | << auto filled text: referenced from CF1R for this system name if the data is available; else if the system type on the CF1R does not provide this data, then result=N/A >> | <<auto filled text: referenced from CF1R for this system name if the data is available; else if the system type on the CF1R does not provide this data, then result=N/A>> | <<auto filled text: referenced from CF1R for this system name if the data is available; else if the system type on the CF1R does not provide this data, then result=N/A >> | <<auto filled text: referenced from CF1R for this system name if the data is available; else if the system type on the CF1R does not provide this data, then result=N/A>> | <<auto filled text: referenced from CF1R for this system name if the data is available; else if the system type on the CF1R does not provide this data, then result=N/A>> | <<auto filled text: referenced from CF1R for this system name if the data is available; else if the system type on the CF1R does not provide this data, then result=N/A>> | << calculated field: if CF1R flags requirement for a Verified Duct System Design, then display text: Verified Duct System Design else reference the R-value from the CF1R for this system name if the data is available (acceptable values: R-0, R-21, R-4.2, R-6, R-8, R-10, R-12); else if CF1R does not provide R-value data for this system, then result=N/A>> |
| Notes: |  |  |  |  |  |  |  |  |  |

| D. Installed New, Altered, and Existing Space Conditioning (SC) System Component Information << require one row of data to be entered in this table for each of the quantity of space conditioning systems entered in A04.>> |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
| SC System Identification or Name | SC System Location or Area Served | Conditioned Floor Area Served by the System (ft2) | Heating System Type | Cooling System Type | SC System Fan Type | Distribution System Type | SC System Thermostat Type | Central Fan Integrated (CFI) Vent System Status | New or Replaced Duct Length | New Duct R-Value | SC System Status | Duct System Status |
| << as default, require user to select applicable system name from a list comprised of the systems identified in column B01; else allow user to override the default and enter text 15 characters maximum; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<user input, text, 15 characters maximum>> | << user input, numeric, xxxx; *Require the sum of the values in this column to be equal to the value in A03 as condition of completion of this doc>> | <<if SC system is not shown in section B, then user pick one from list below, else, reference value from B03 as default; allow user to override the default and pick one from list below: *central gas furnace; *central split HP; *central packaged HP *central large packaged HP *ductless mini-split HP; *room HP; *boiler; *hydronic; *combined hydronic; *hydronic+forced air; *combined hydronic+forced air; *hydronic HP, *hydronic HP+forced air; *gas wall furnace; *gas space heater; *electric ; *Wood Heat; *small duct high velocity HP; *ductless multi-split HP; *ductless VRF HP; *Packaged gas furnace *flag non-default values and report in project status notes field; a revised CF1R may be required >> | << if SC system is not shown in section B, then user pick one from list below, else reference value from B04 as default; allow user to override the default and pick one from list below: *central split AC; *central split HP *central packaged AC ; *central packaged HP *central large packaged AC ; *central large packaged HP *ductless mini-split AC; *ductless mini-split HP; *gas absorption AC *room AC; *room HP; *hydronic HP, *hydronic HP+forced air; *evaporative - direct *evaporative - indirect *evaporative - indirectdirect *evaporatively cooled condenser *Ice Storage AC *no cooling; *small duct high velocity HP; *small duct high velocity AC; *ductless multi-split HP; *ductless multi-split AC; *ductless VRF HP; *ductless VRF AC; *flag non-default values and report in project status notes field; a revised CF1R may be required >>>> | << if SC system is not shown in section B, then user pick one from list below, else reference value from B05 as default; allow user to override the default and pick one from list below: * PSC – Permanent Split Capacitor *BPM – Brushless Permanent Magnet *flag non-default values and report in project status notes field; a revised CF1R may be required >> | << if SC system is not shown in section B, then user pick one from list below, else:reference value from B06 as default. Allow user to overwrite only the following default values from B06: *DuctsAttic *DuctsGarage *DuctsOutdoor; If overriding pick one from list: *DuctsAttic - Ducts located overhead in unconditioned attic *DuctsCrawl - Ducts located underfloor in unconditioned crawl space *DuctsGarage - Ducts located in an unconditioned garage *DuctsInEx12 - Ducts located within the conditioned space (except < 12 lineal ft) *DuctsInAll - HVAC system(s) with all HVAC ducts located in conditioned space *DuctsNone - Air distribution systems without ducts *DuctsOutdoor - Ducts located in exposed outdoor locations *LowLlCod - Verified low-leakage ducts in conditioned space *Ducts located in multiple places *flag non-default values and report in project status notes field; a revised CF1R may be required >> | << if SC system is not shown in section B, then user pick one from list below, else:reference value from B07 as default; allow user to override the default and pick one from list: *setback *OCST per JA5 >> | <<user pick one from list: *CFI System *Not CFI>> | <<calculated field: if D07=DuctsNone, then display N/A; else reference value from CF1R as default; (values are: **≤40ft; **>40ft; **N/A - no ducts); allow user to override the default and pick one from list: **≤40ft; **>40ft; **N/A - no ducts replaced; flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<calculated field: if D07=DuctsNone, then display N/A; if D10=N/A - no ducts replaced, then display N/A; if D10 ≠ NA and value in C10 is > R-6 for CZs: 1-10, 12, 13 or > R-8 for CZs: 11, 14-16, then display value from C10; elseif D10≠N/A, then, if A02= CZ 1-10, 12, 13, then R-6.; elseif A02=CZ 11, 14-16 then R-8; end>> | <<calculated field: if SC system is not shown in section B, then user pick one from list: **new **altered **existing else reference value from B09 as default; allow user to override the default and pick one from list: **new **altered **existing flag non-default values and report in project status notes field; a revised CF1R may be required >> | <<calculated field:if SC system is not shown in section B, then user pick one from list: **new **altered **existing **existing+new elseif D07= DuctsNone, then value=N/A, else reference value from B10 as default; allow user to override the default and pick one from list **new **altered **existing **existing+new flag non-default values and report in project status notes field; a revised CF1R may be required >> |
| Notes: |  |  |  |  |  |  |  |  |  |  |  |  |

| E. Space Conditioning (SC) System Alteration Type Determination << if there are no SC systems listed in Section D for which D12 = one of the following two values: [altered]; [existing], or D13= one of the following three values: [altered]; [existing], [existing+new], then display the section does not apply message, else require one row of data to be entered in this table for each SC system listed in Section D for which D12 = one of the following two values: [altered]; [existing], or D13= one of the following three values: [altered]; [existing], [existing+new]>> |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 9 | 10 | 11 |
| SC System Identification or Name | SC System Location or Area Served | Is the SC system a ducted system? | Installing refrigerant containing component? | Installing new SC System component? | Installing more than 40 feet of ducts? | Installing entirely new duct system? | Installing entirely new SC system? | Alteration Type | Altered Heating Components | Altered Cooling Components |
| <<auto filled text: referenced from D01>> | <<auto filled text: referenced from D02>> | <<calculated field: if D07= DuctsNone, then value=no, else value=yes>> | <<user pick from list: "yes"; or "no">> | <<user pick from list: "yes"; or "no">> | <<calculated field: if D10=≥40ft, then value=yes, else value = no>> | <<user pick from list: "yes"; or "no">> | <<user pick from list: "yes"; or "no">> | << Calculated field: determine the correct result for "alteration type" for entry in this field by the user responses in E03, E04, E05, E06, E07, E08 and use of "Logic Table for Determining Alteration Type and HERS Verification Requirements" (logic table is inserted below this section); constrain user input for fields E03, E04, E05, E06, E07, E08 to allow only the available combinations of responses given in the Logic Table in rows a through t; alteration types are: *Extension of Existing Duct System; *Altered Space Conditioning System; *Entirely New or Complete Replacement Duct System with or without Equipment Changeout; *Entirely New or Complete Replacement Space Conditioning System * No alteration Performed >> | <<Calculated field: if E09= No alteration Performed, then value in this field= no heating component altered, else prompt user to pick as many as are applicable from list: *gas furnace AHU; *wall furnace *indoor fancoil AHU; *outdoor condensing unit; *indoor coil; *boiler; *TXV or EXV; *compressor; *refrigerant lineset; *no heating component altered>> | << Calculated field: if E09= No alteration Performed, then value in this field= no cooling component altered, else prompt user to pick as many as are applicable from list: *outdoor condensing unit, *outdoor package unit *indoor fancoil AHU, *indoor coil, *TXV or EXV, *Compressor, *refrigerant lineset, *no cooling component altered>> |

| Logic Table for Determining Alteration Type and HERS Verification Requirements (this table not shown on the completed document) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
|  | Is the altered or installed system a ducted system? | Altering or installing a refrigerant containing component? | Installing new components? (packaged unit, or condensing unit, or cooling/heating coil, or air-handling unit, etc) | Installing more than 40 linear feet of new or replacement ducts? | Is the entire duct system accessible for sealing, and is more than 75% of the duct system new or replaced? | Are all of the system's components and ducts new or replaced? (entirely new system) | alteration type | HERS | notes |
| a | no | yes | no | no | no | no | Altered space conditioning system | RC | e.g. alteration to refrigerant containing component - mini-split or packaged AC |
| b | no | yes | yes | no | no | no | Altered space conditioning system | RC | e.g. changeout mini-split system component |
| c | yes | no | yes | no | no | no | Altered space conditioning system | DctLk | e.g. new hydronic AHU or furnace |
| d | yes | no | yes | yes | no | no | Altered space conditioning system | DctLk | e.g. new furnace + duct alteration |
| e | yes | yes | no | no | no | no | Altered space conditioning system | RC | e.g. alteration to a refrigerant containing component - split system |
| f | yes | yes | yes | no | no | no | Altered space conditioning system | RC | e.g. changeout refrigerant containing components |
| g | yes | yes | yes | yes | no | no | Altered space conditioning system | RC + DctLk | e.g. changeout refrigerant containing compinent + altered ducts |
| h | yes | yes | no | yes | no | no | Altered space conditioning system | RC + DctLk | e.g. alteration to refrigerant containing component + altered ducts |
| i | yes | no | no | yes | yes | no | Entirely new duct system with or without Equipment Changeout | DctLk + FE/AF or Tbl150.0-C,D | e.g. new duct system without equipment changeout |
| j | yes | no | yes | yes | yes | no | Entirely new duct system with or without Equipment Changeout | DctLk + FE/AF or Tbl150.0-C,D | e.g. new furnace + new duct system |
| k | yes | yes | no | yes | yes | no | Entirely new duct system with or without Equipment Changeout | RC + DctLk + FE/AF or Tbl150.0-C,D | e.g. alteration to a refrigerant containing component + new duct system |
| l | yes | yes | yes | yes | yes | no | Entirely new duct system with or without Equipment Changeout | RC + DctLk + FE/AF or Tbl150.0-C,D | e.g. changeout refrigerant containing component + new duct system |
| m | no | no | yes | no | no | yes | Entirely new space conditioning system | none | e.g. new ductless hydronic heating system |
| n | no | yes | yes | no | no | yes | Entirely new space conditioning system | RC | e.g. new mini-split (weigh-in); or new room packaged AC (factory charged) |
| o | yes | no | yes | yes | yes | yes | Entirely new space conditioning system | DctLk + FE/AF or Tbl150.0-C,D | e.g. new ducted hydronic heating system |
| p | yes | yes | yes | yes | yes | yes | Entirely new space conditioning system | RC + DctLk + FE/AF or Tbl150.0-C,D | e.g. new split system |
| q | yes | no | no | yes | no | no | Extension of an existing duct system | DctLk | e.g. altered ducts |
| r | no | no | no | no | no | no | System is exempt from the alteration requirements | none | no alteration performed |
| s | yes | no | no | no | no | no | System is exempt from the alteration requirements | none | no alteration performed |
| t | yes | yes | yes | no | yes | yes | Entirely new space conditioning system | RC + DctLk + FE/AF or Tbl150.0-C,D | e.g. new ducted system that has less than 40 ft of ducts |
| Nomenclature: RC = Refrigerant Charge Verification (MCH-25) DctLk = Duct Leakage Test (MCH-20) FE/AF or Tbl150.0-C,D - Fan Efficacy and Airflow Rate verification (MCH-22; MCH-23) or alternative compliance: (MCH-28) |  |  |  |  |  |  |  |  |  |

| F. Installed Heating System Equipment Information (not heat pumps) <<<if all of the SC Systems listed in Section D have a value in D04 = one of the heat pump types (see list that follows below), AND if Section E applies but all of the SC Systems listed in Section E have a value in E10=no heating component altered, then display the section does not apply message; else require one row of data to be entered in this table for each of the SC Systems in Section D that meet BOTH of the following 2 criteria: [D12=new], [D04 ≠ one of the heat pump types in the list that follows below]; ALSO if Section E applies require one row of data to be entered in this table for each of the SC Systems in Section E that meet both of the following 2 criteria: [E05=yes], [E10=one of the following 3 heating component types: {gas furnace AHU}; {wall furnace}; {boiler}]: *central split HP; *central packaged HP *central large packaged HP *ductless mini-split HP; *hydronic HP, *hydronic HP+forced air; *room HP; *small duct high velocity HP; *ductless multi-split HP; *ductless VRF HP >> |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 |
| SC System Identification or Name | SC System Location or Area Served | Heating Efficiency Type | Heating Efficiency Value | Heating Unit Manufacturer | Heating Unit Model Number | Heating Unit Serial Number | Rated Heating Capacity, Output (Btu/h) |
| <<auto filled from D01>> | <<auto filled from D02>> | <<if SC system is not shown in section C, then user pick one from list: *AFUE; *COP; *HSPF, or *NA else as default reference the value from C02; allow user to override default and pick from list *AFUE; *COP; *HSPF; or *NA flag non-default values and report in project status notes field; a revised CF1R may be required > > | <<If C03 = NA, then report NA; else user input, numeric, 100.0≥xx.x≥0.0; if the SC System is shown in Section C, then, check value entered by user in this field (F04) must be ≥ value shown in C03, and if not ≥ value shown in C03, flag as non-compliant value and do not allow registration to proceed elseif the SC System isNOT shown in Section C, end>> | <<user input alphanumeric text string max 50 characters>> | <<user input alphanumeric text string max 50 characters>> | <<user input alphanumeric text string max 50 characters>> | <<user input, numeric, xxxx>> |
| Notes: |  |  |  |  |  |  |  |

| G. Installed Cooling System Outdoor Condensing Unit or Package Unit Equipment Information (not heat pumps) << if all of the SC Systems listed in Section D have a value in D05= No Cooling, AND if Section E applies but all of the SC Systems listed in Section E have a value in E11=no cooling component altered, then display the section does not apply message; else require one row of data to be entered in this table for each of the SC Systems in Section D that meet ALL of the following 3 criteria: [D12=new], [D05≠no cooling], [D05 ≠ one of the heat pump types in the list that follows below]; ALSO if Section E applies require one row of data to be entered in this table for each of the SC Systems in Section E that meet ALL of the following 3 criteria: [E05=yes], [D05 ≠ one of the heat pump types in the list that follows below] [E11=one of the following 2 cooling component types: {outdoor condensing unit}; {outdoor package unit}] *central split HP; *central packaged HP *central large packaged HP *ductless mini-split HP; *hydronic HP, *hydronic HP+forced air; *room HP; *small duct high velocity HP; *ductless multi-split HP; *ductless VRF HP >> |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 |
| SC System Identification or Name | SC System Location or Area Served | Cooling Efficiency SEER | Cooling Efficiency EER | Condenser or Package Unit Manufacturer | Condenser or Package Unit Model Number | Condenser or Package Unit Serial Number | System Rated Cooling Capacity at Design Conditions (Btu/h) | Condenser Rated Nominal Cooling Capacity (ton) |
| <<auto filled from D01>> | <<auto filled from D02>> | <<if SC system is NOT shown in section C, then prompt user to input, numeric, xx.x; end if SC system IS shown in section C, and value in C06=N/A, then result=NA; else require user to input, numeric, xx.x; and check value entered by user in this field (G03) must be ≥ value in C06, to comply; else flag non-compliant value and do not allow registration to proceed>> | <<if SC system is NOT shown in section C, then prompt user to input, numeric, xx.x; end if SC system IS shown in section C, and value in C07=N/A, then result=NA; else require user to input, numeric, xx.x; and check value entered by user in this field (G04) must be ≥ value in C07, to comply; else flag non-compliant value and do not allow registration to proceed>> | <<user input alphanumeric text string max 50 characters>> | <<user input alphanumeric text string max 50 characters>> | <<user input alphanumeric text string max 50 characters>> | <<user input, numeric, xxxxxx>> | <<user input, numeric, x.x>> |
| Notes: |  |  |  |  |  |  |  |  |

| H. Installed Split System Indoor Coil or Fan Coil Unit Equipment Information (applicable to DX or hydronic heating/cooling coils or fan coil units) Systems with more than one indoor coil or fan coil unit (e.g. multi-split systems) shall provide information for each of the system indoor coils or fan coil units. <<<if none of the SC Systems listed in Section D have a value in either D04 or D05 = one of the system types in the list that follows below, then display the section does not apply message; else require a minimum of one row of data to be entered in this table for each of the SC Systems listed in Section D that meets both of the following 2 criteria: [D12=new]; [{D04 or D05}=one of the system types in the list that follows below]; ALSO if Section E applies require a minimum of one row of data to be entered in this table for each of the SC Systems in Section E that meet the following 2 criteria: [E05=yes]; [{E10 or E11}=one of the following two component types {indoor fancoil AHU}; { indoor coil}]. *central split AC; *central split HP *ductless mini-split AC; *ductless mini-split HP; *hydronic + forced air; *combined hydronic + forced air; *hydronic HP+forced air; *gas absorption AC; *evaporatively cooled condenser; *Ice Storage AC; *small duct high velocity AC; *small duct high velocity HP; *ductless multi-split AC; *ductless multi-split HP; *ductless VRF AC; *ductless VRF HPAllow user to enter additional rows of data for systems that have more than one indoor coil or fan coil unit (e.g. multi-split HP).>> |  |  |  |  |
| --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 |
| SC System Identification or Name | SC System Location or Area Served | Indoor Coil or Fan Coil Unit Manufacturer | Indoor Coil or Fan Coil Unit Model Number | Indoor Coil or Fan Coil Unit Serial Number |
| <<auto filled from D01>> | <<auto filled from D02>> | <<user input alphanumeric text string max 50 characters>> | <<user input alphanumeric text string max 50 characters>> | <<user input alphanumeric text string max 50 characters>> |
| Notes: |  |  |  |  |

| I. Installed Heat Pump System – Split System Condensing Unit or Package Unit Equipment Information <<<if none of the SC Systems listed in Section D have a value in D05 = one of the heat pump types in the list that follows below, then display the section does not apply message; else require one row of data to be entered in this table for each of the SC Systems listed in Section D that meets BOTH of the following 2 criteria: [D12=new] [D05 = one of the heat pump types in the list that follows below]; ALSO if Section E applies, require one row of data to be entered in this table for each of the SC Systems in Section E that meet the following 3 criteria: [E05=yes] [D05 = one of the heat pump types in the list that follows below]; [E11=one of the following 2 cooling component types: {outdoor condensing unit}; {outdoor package unit}] *central split HP; *central packaged HP *central large packaged HP *ductless mini-split HP; *room HP *hydronic HP, *hydronic HP+forced air; *small duct high velocity HP; *ductless multi-split HP; *ductless VRF HP >> |  |  |  |  |
| --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 |
| SC System Identification or Name | SC System Location or Area Served | Condenser or Package Unit Manufacturer | Condenser or Package Unit Model Number | Condenser or Package Unit Serial Number |
| <<auto filled from D01>> | <<auto filled from D02>> | <<user input alphanumeric text string max 50 characters>> | <<user input alphanumeric text string max 50 characters>> | <<user input alphanumeric text string max 50 characters>> |
| Notes: |  |  |  |  |

| J. Installed Heat Pump System – Efficiency and Performance Compliance Information <<<if none of the SC Systems listed in Section D have a value in D05 = one of the heat pump types in the list that follows below, then display the section does not apply message; else require one row of data to be entered in this table for each of the SC Systems listed in Section D that meets BOTH of the following 2 criteria: [D12=new] [D05 = one of the heat pump types in the list that follows below]; ALSO if Section E applies, require one row of data to be entered in this table for each of the SC Systems in Section E that meet the following 3 criteria: [E05=yes] [D05 = one of the heat pump types in the list that follows below]; [E11=one of the following 2 cooling component types: {outdoor condensing unit}; {outdoor package unit}] *central split HP; *central packaged HP *central large packaged HP *ductless mini-split HP; *hydronic HP, *hydronic HP+forced air; *room HP; *small duct high velocity HP; *ductless multi-split HP; *ductless VRF HP >> |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System Identification or Name | SC System Location or Area Served | Heating Efficiency Type | Heating Efficiency Value | System Rated Heating Capacity at 47°F | System Rated Heating Capacity at 17°F | System Rated Cooling Efficiency SEER | System Rated Cooling Efficiency EER | System Rated Cooling Capacity at Design Conditions (Btu/h) | Condenser Rated Nominal Cooling Capacity (ton) |
| <<auto filled from D01>> | <<auto filled from D02>> | <<reference value from C02; note: values may be *AFUE; *COP; *HSPF; or *NA>> | <<If C03 = NA, then report NA; else user input, numeric, 100.0≥xx.x≥0.0; check value must be ≥ value in C03, to comply; else flag non-compliant value and do not allow registration to proceed>> | << if value in C04=N/A, then result=NA; else user input, numeric, xx.x; check value must be ≥ value in C04, to comply; else flag non-compliant value and do not allow registration to proceed>> | << if value in C05=N/A, then result=NA; else user input, numeric, xx.x; check value must be ≥ value in C05, to comply; else flag non-compliant value and do not allow registration to proceed>> | << if value in C06=N/A, then result=NA; else user input, numeric, xx.x; check value must be ≥ value in C06, to comply; else flag non-compliant value and do not allow registration to proceed>> | << if value in C07=N/A, then result=NA; else user input, numeric, xx.x; check value must be ≥ value in C07, to comply; else flag non-compliant value and do not allow registration to proceed>> | <<user input, numeric, xxxxxx>> | <<user input, numeric, x.x>> |
| Notes: |  |  |  |  |  |  |  |  |  |

| K. Extension of Existing Duct System, Greater Than 40 Feet <<if there are no Alteration Types in column E09 equal to "Extension of Existing Duct System" then display the "section does not apply" message; else require one row of data to be entered in this table for each SC System that has an alteration type value in column E09 equal to: "Extension of Existing Duct System">> |  |  |  |
| --- | --- | --- | --- |
| 01 | 02 | 03 |  |
| SC System Identification or Name | SC System Location or Area Served | New Duct R-Value |  |
| <<reference value from D01>> | <<reference value from D02>> | <<user pick from list: R-6, R-8, R-10, R-12; check value: must be ≥ value in D11 to comply; flag non-compliant value and report in project status notes field; a revised CF1R or revised installation may be required >> |  |

| L. Installed Duct System Information <<if all of the SC Systems listed in Section D have a Distribution System Type value in D07 =DuctsNone (Air distribution systems without ducts), then display the section does not apply message; else require one row of data in this table for each SC System listed in Section D that meets BOTH of the following 2 criteria: [D13=new], [D07 = one of the Ducted Distribution types: DuctsAttic; DuctsCrawl; DuctsGarage; DuctsInEx12; DuctsInAll; DuctsOutdoor; LowLlCod; Ducts located in multiple places]. ALSO, if Section E applies, require one row of data in this table for each SC system listed in Section E that meets BOTH of the following 2 criteria: [E03=yes], [E07=yes]>> |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |
| SC System ID or Name | SC System Location or Area Served | Supply Duct Location | Supply Duct R-Value | Return Duct Location | Return Duct R-Value | Exemption from Min R-Value for Ducts In Conditioned Space | Method of compliance with duct and filter grille sizing Req's in 150.0(m)13 | Number of Air Filter Devices on System | Can RA3.3 Airflow Protocols be used to test this System? |
| <<auto filled D01>> | <<auto filled from D02>> | <<reference value from D07 as default. Allow user to overwrite only the following default values from D07: *DuctsAttic *DuctsGarage *DuctsOutdoor; If overriding pick one from list: *conditioned space-entirely, *conditioned space -except 12ft, *unconditioned attic, *unconditioned crawl space, *controlled ventilation crawl space *unconditioned garage, *unconditioned basement, *outdoors *Ducts located in multiple places *Verified low-leakage ducts entirely in conditioned space flag non-default values and report in project status notes field; a revised CF1R may be required >> | << calculted field: if C10 =Verified Duct System Design, then display text: Verified Duct System Design; else user pick from list: R-4.2, R-6, R-8, R-10, R-12; and check value: must be ≥ value in D11, or L07 must= yes to comply; else flag non-compliant value and do not allow registration to proceed >> | <<reference value from D07 as default. Allow user to overwrite only the following default values from D07: *DuctsAttic *DuctsGarage *DuctsOutdoor; If overriding pick one from list: *conditioned space-entirely, *conditioned space -except 12ft, *unconditioned attic, *unconditioned crawl space, *controlled ventilation crawl space *unconditioned garage, *unconditioned basement, *outdoors *Ducts located in multiple places Verified low-leakage ducts entirely in conditioned space flag non-default values and report in project status notes field; a revised CF1R may be required >> | << calculted field: if C10 =Verified Duct System Design, then display text: Verified Duct System Design; else user pick from list: R-4.2, R-6, R-8, R-10, R-12; and check value: must be ≥ value in D11, or L07 must= yes to comply; else flag non-compliant value and do not allow registration to proceed >> | << Default Value=No Exemption, if values in both L03 and L05= conditioned space-entirely allow user to override the default and pick from list: result=yes>> | << if System Type in D05=no cooling, then result = Exempt - No Cooling elseif D05=one of the following three system types:: **evaporative - direct, or **evaporative - indirect, or **evaporative - indirectdirect, then result = Exempt - Evaporative System; elseif L12=no, then result = Exempt - RA3.3 Protocols are N/A; elseif B10={new or altered}, AND one or more of the following three conditions is true: **value in C09 is less than 0.58 **value in C08 greater than 350 **D09=CFI System then result=HERS Verified Fan Efficacy and Airflow Rate; elseif [{D13=new} or {E07=yes}] then user select one from list: **HERS Verified Fan Efficacy and Airflow Rate; **HERS verified Return Duct Design per Table 150.0-C, D; else result = Exempt - Duct system not entirely new; end>> | <<user enter integer value will determine number or rows per system in next section>> | <<user pick one value from list: **yes **no>> |
| Notes: |  |  |  |  |  |  |  |  |  |

| M. Installed Air Filter Device Information Mandatory requirements for air filter devices are specified Section 150.0(m)12. <<If Section L. applies, then display Section M.; else display section header and the standard “This section does not apply” message>> |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 |
| SC System Identification or Name | SC System Location or Area Served | Air Filter Identification or Name | Air Filter Device Type | Air Filter Device Location | Determined Design Airflow Rate for Air Filter Device (cfm) | Determined Design Allowable Pressure Drop for Air Filter Device (inch W.C.) |
| <<auto filled from D01>> | <<auto filled from D02>> | <<user input text, maximum 20? characters>> | <<user select from list: *Filter Grille *Furnace Mounted *Duct Mounted >> | <<user input text, maximum 30 characters>> | <<user enter numeric, xxx>> | <<user enter value, numeric, x.xx>> |
| Notes: |  |  |  |  |  |  |  |

| N. Air Filter Device Requirements <<if Section M. applies, then display Section N.; else display section header and the standard “This section does not apply” message>> |  |
| --- | --- |
| 01 | The system shall be designed to ensure that all recirculated air and all outdoor air supplied to the occupiable space is filtered before passing through the system's thermal conditioning components. |
| 02 | The system shall be designed to accommodate the clean-filter pressure drop imposed by the system air filter device(s). The design airflow rate and maximum allowable clean-filter pressure drop at the design airflow rate applicable to each air filter device shall be determined, and all system air filter device locations shall be labeled to disclose the applicable design airflow rate and the maximum allowable clean-filter pressure drop. The labels shall be permanently affixed to the air filter device, readily legible, and visible to a person replacing the air filter media, and the air filter devices shall be provided with air filter media that conforms to these determined/labeled maximum allowable clean-filter pressure drop values as tested using ASHRAE Standard 52.2 or rated using AHRI Standard 680 |
| 03 | All system air filter devices shall be located and installed in such a manner as to allow access and regular service by the system owner. |
| 04 | The system shall be provided with air filter media having a designated efficiency equal to or greater than MERV 6 when tested in accordance with ASHRAE Standard 52.2, or a particle size efficiency rating equal to or greater than 50 percent in the 3.0–10 μm range when tested in accordance with AHRI Standard 680. |
| 05 | The system shall be provided with air filter media that has been labeled by the manufacturer to disclose the efficiency and pressure drop ratings that conform to the required efficiency and pressure drop requirements for the air filter device. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| O. HERS Verification Requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
|  |  |  | MCH-20 | MCH-21 | MCH-22 | MCH-23 | MCH-25 | MCH-26 | MCH-27 | MCH-28 | MCH-29 | MCH30 |
| SC System Identification or Name | SC System Location or Area Served | Exemption from Duct Leakage Requirements | Duct Leakage Test | Duct Location Verification | AHU Fan Efficacy (W/cfm) | AHU Airflow Rate (cfm/ton) | Refrigerant Charge | Rated SC System Equipment Verification | IAQ Mechanical Ventilation | Return Duct Design - Table 150.0-B or C | Supply Duct Surface Area R-Value Buried Ducts | Ventilation Cooling Credit |
| <<auto filled from D01>> | <<auto filled from D02>> | <<calculated value: If D07 = DuctsNone, then value = NA; Else default value = No Exemptions; Allow user to override the default and pick one from list: * Ducts have previously been sealed, tested, and certified by a HERS Rater; * Duct system has less than 40 ft of duct; * Duct system is insulated or sealed with asbestos; Flag non-default values and report in project status notes field; The enforcement agency may require additional documentation as validation>> | <<Calculated field: if value in D07=DuctsNone (Air distribution systems without ducts), then display result =no elseif O03 ≠ default value (No Exemptions), then display result = no; elseif the CF1R flags the requirement for HERS verification of duct leakage; then display result=yes elseif Section E applies, then determine the result for this field by the user responses in E03, E04, E05 , E06, E07, E08, and use of Logic Table (inserted below section E); constrain user input for fields E03-E08 to allow only the available combinations of responses given in the Logic Table in rows a through t, and determine result for this field as follows: If the term "DctLk" appears in the HERS column, then display result=yes elseif logic result is consistent with row f, and the value in E11= oneof the following 3 criteria: **indoor fancoil AHU; **indoor coil; **outdoor package unit, then result=yes, elseif logic result is consistent with row f, and the value in E10=[gas furnace] then result=yes else result=no else result=no>> | << Calculated field: if value in D07=DuctsNone (Air distribution systems without ducts), then display result =no elseif the value in L07= yes, and the values in either L04 or L06 are <D11 then display result in this field=yes; Elseif value in D07= one of the following: *DuctsInEx12; *DuctsInAll; then display result in this field=yes; else display result=no>> | <<calculated field: if value in D07=DuctsNone (Air distribution systems without ducts), then result =no elseif L08 result is Fan Efficacy and Airflow Rate, then result is yes, else result=no>> | <<calculated field:if value in D07=DuctsNone (Air distribution systems without ducts), then result =no elseif if L08 result is Fan Efficacy, and Airflow Rate then result = yes, elseif section O field 07=yes, and value in Section O field 10=no, then value in this field=yes else result=no>> | <<Calculated field: if B09 = one of the following two values: *New or *Altered, then if CF1R reports verification of RC = Required, then result = Yes; Elseif the CF1R reports verification of RC = Not Required, then result = Np; Else if D12 = Existing AND E04 = Yes, then result = Yes; Else result = No>> | <<if G03 > 14, then result=yes; if G08 < 45000 and G04 > 12.2, then result=yes; elseif G08 >= 45000 and G04 > 11.7, then result = yes; else result=no>> | <<calculated field: If CF1R-PRF project scope = Newly Constructed (Addition Alone) and the Addition Conditioned Floor Area > 1,000 ft2, then result = yes; elseif CF1R-PRF flags the requirement for HERS verification of IAQ ventilation, then result=yes; else result = no | <<calculated field: if value in D07=DuctsNone (Air distribution systems without ducts), then display result =no elseif L08 result is Return Duct Design per Table 150.0-C, D; then result=yes else result=no>> | <<calculated field: if value in D07=DuctsNone (Air distribution systems without ducts), then display result =no; elseif the CF1R flags the requirement for HERS verified duct design (Supply Duct Surface Area R-Value or Buried Ducts or Deeply Buried Ducts), then result=yes, else result=no>> | << calculated field: if the CF1R flags the requirement for HERS verification of Ventilation Cooling credit; then result=yes, else result=no>> |
| Notes: |  |  |  |  |  |  |  |  |  |  |  |  |

| P. Space Conditioning Systems, Ducts and Fans – Mandatory Requirements and Additional Measures Note: Additional mandatory requirements from Section 150.0 that are not listed here may be applicable to some systems. These requirements may be applicable to only newly installed equipment or portions of the system that are altered. Existing equipment may be exempt from these requirements. |  |
| --- | --- |
| Heating Equipment |  |  |  |
| 01 |  | Equipment Efficiency: All heating equipment must meet the minimum efficiency requirements of Section 110.1 and Section 110.2(a) and the Appliance Efficiency Regulations. |  |
| 02 |  | Controls: All unitary heating systems, including heat pumps, must be controlled by a setback thermostat. These thermostats must be capable of allowing the occupant to program the temperature set points for at least four different periods in 24 hours. See Sections 150.0(i), 110.2(b). |  |
| 03 |  | Sizing: Heating load calculations must be done on portions of the building served by new heating systems to prevent inadvertent undersizing or oversizing. See sections 150.0(h)1 and 2). |  |
| 04 |  | Furnace Temperature Rise: Central forced-air heating furnace installations must be configured to operate at or below the furnace manufacturer's maximum inlet-to-outlet temperature rise specification. See Section 150.0(h)4. |  |
| 05 |  | Standby Losses and Pilot Lights: Fan-type central furnaces may not have a continuously burning pilot light. Section 110.5 and Section 110.2(d). |  |
| Cooling Equipment |  |  |  |
| 06 |  | Equipment Efficiency: All cooling equipment must meet the minimum efficiency requirements of Section 110.1 and Section 110.2(a) and the Appliance Efficiency Regulations. |  |
| 07 |  | Refrigerant Line Insulation: All refrigerant line insulation in split system air conditioners and heat pumps must meet the R-value and protection requirements of Section 150.0(j)2 and 3, and Section 150.0(m)9. |  |
| 08 |  | Condensing Unit Location: Condensing units shall not be placed within five (5) feet of a dryer vent outlet. See Section 150.0(h)3A. |  |
| 09 |  | Sizing: Cooling load calculations must be done on portions of the building served by new cooling systems to prevent inadvertent undersizing or oversizing. See Section 150.0(h)1 and 2. |  |
| Air Distribution System Ducts, Plenums and Fans |  |  |  |
| 10 |  | Insulation: In all cases, unless ducts are enclosed entirely in directly conditioned space, the minimum duct insulation value is R-6. Note that higher values may be required by the prescriptive or performance requirements. See Section 150.0(m)1. |  |
| 11 |  | Connections and Closures: All installed air-distribution system ducts and plenums must be, sealed and insulated to meet the requirements of CMC Sections 601.0, 602.0, 603.0, 604.0, 605.0 and ANSI/SMACNA-006-2006: Supply-air and return-air ducts and plenums must be insulated to a minimum installed level of R-6.0 or enclosed entirely in directly conditioned space as confirmed through field verification and diagnostic testing in accordance with the requirements of Reference Residential Appendix RA3.1.4.3.8. |  |
| Heat Pump Thermostat |  |  |  |
| 12 |  | A thermostat shall be installed that meets the requirements of Section 110.2(b) and Section 110.2(c). |  |
| 13 |  | The thermostat shall be installed in accordance with the manufacturers published installation specifications. |  |
| 14 |  | First stage of heating shall be assigned to heat pump heating. |  |
| 15 |  | Second stage back up heating shall be set to come on only when the indoor set temperature cannot be met. |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |  |  |