Title 24, Part 6, Section 150.0(o) Ventilation for Indoor Air Quality. All dwelling units shall meet the requirements of ANSI/ASHRAE Standard62.2. Ventilation and Acceptable Indoor Air Quality in Low-Rise Residential Buildings. Equation and table numbering on this form corresponds to the numbering for that information in the published ANSI/ASHRAE Standard 62.2-2010.

| A. Dwelling Mechanical Ventilation - General Information |  |  |
| --- | --- | --- |
| 01 | Dwelling Unit Name |  |
| 02 | Building Type |  |
| 03 | Project Scope |  |
| 04 | Total Conditioned Floor Area of Dwelling Unit (For addition projects the conditioned floor area equals existing area plus addition area) |  |
| 05 | Number of Bedrooms in Dwelling Unit (For addition projects the number of bedrooms equals the existing bedrooms plus addition bedrooms) |  |
| 06 | Ventilation Operation Schedule |  |
| 07 | Whole-Building Ventilation Rate Calculation Method |  |
| 08 | Whole Building Ventilation System Type |  |
| 09 | IAQ Fan Location |  |
| Note: Non-dwelling units do not meet the definition for a dwelling unit as defined in Section 100.1(b). Non-dwelling units are not designed to provide independent living facilities and do not provide permanent provisions for living, sleeping, eating, cooking and sanitation. |  |  |

MCH-27b - Continuous Ventilation Airflow - Total Ventilation Rate Method

| B. Whole-Building Continuous Ventilation - Total Ventilation Rate Method A mechanical supply system, exhaust system, or combination thereof shall provide whole-building ventilation with outdoor air each hour at no less than the rate in 62.2 equation 4.7. |  |  |
| --- | --- | --- |
| 01 | Total Required Ventilation Rate ( fan + infiltration), (Qtot) |  |
| 02 | CFM50 – Depressurization |  |
| 03 | Equivalent Leakage Area Depressurization |  |
| 04 | CFM50 – Pressurization |  |
| 05 | Equivalent Leakage Area Pressurization |  |
| 06 | Equivalent Leakage Area used for Ventilation |  |
| 07 | What is the vertical distance from the lowest above-grade floor to the highest ceiling in feet? |  |
| 08 | What is the weather and shielding factor (wsf) for the city listed in 62.2 Appendix X Table X1 ? |  |
| 09 | Normalized Leakage (NL) |  |
| 10 | Ventilation Provided by Infiltration (Qinf) |  |
| 11 | Required Continuous Whole-Building Ventilation Rate (Qfan) |  |
| 12 | Installed Continuous Whole-Building Ventilation Rate |  |

| C. Compliance Statement |  |
| --- | --- |
| 01 |  |

| D. Local Mechanical Exhaust System – Fan Selection and Duct Design Criteria for Compliance |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Local mechanical exhaust fans shall be installed in each kitchen and bathroom. Delivered local ventilation rates: - All local ventilation rates have been measured using a flow hood, flow grid, or other airflow measuring device and meet the requirements of 62.2 Tables 5.1 or 5.2; OR - The airflow rating at a pressure of 0.25 in. w.c. of a certified fan is assumed because the local ventilation system duct sizing meets the prescriptive requirements of 62.2 Table 5.3, or manufacturer's design criteria. |  |  |  |  |  |  |  |  |  |  |
| Table 5.1 Intermittent Local Ventilation Exhaust Airflow Rates |  |  |  |  |  |  |  |  |  |  |
| Application |  | Airflow |  | Notes |  |  |  |  |  |  |
| Kitchen |  | 100 cfm |  | Vented range hood (including appliance-range hood combinations) required if exhaust fan flow is less than 5 ACH. |  |  |  |  |  |  |
| Bathroom |  | 50 cfm |  |  |  |  |  |  |  |  |
| Table 5.2 Continuous Local Ventilation Exhaust Airflow Rates |  |  |  |  |  |  |  |  |  |  |
| Application |  | Airflow |  | Notes |  |  |  |  |  |  |
| Kitchen |  | 5 ACH |  | Based on kitchen volume. |  |  |  |  |  |  |
| Bathroom |  | 20 cfm |  |  |  |  |  |  |  |  |
| Table 5.3 Prescriptive Duct Sizing Requirements |  |  |  |  |  |  |  |  |  |  |
| Duct Type | Flex Duct |  |  |  |  |  | Smooth Duct |  |  |  |
| Fan Rating cfm @ 0.25 in. w.g. | 50 |  | 80 |  | 100 | 125 | 50 | 80 | 100 | 125 |
|  | Maximum Allowable Duct Length (ft) |  |  |  |  |  |  |  |  |  |
| Diameter, (in) | Flex Duct |  |  |  |  |  | Smooth Duct |  |  |  |
| 3 | X |  | X |  | X | X | 5 | X | X | X |
| 4 | 70 |  | 3 |  | X | X | 105 | 35 | 5 | X |
| 5 | NL |  | 70 |  | 35 | 20 | NL | 135 | 85 | 55 |
| 6 | NL |  | NL |  | 125 | 95 | NL | NL | NL | 145 |
| 7 and above | NL |  | NL |  | NL | NL | NL | NL | NL | NL |
| This table assumes no elbows. Deduct 15 ft of allowable duct length for each turn, elbow, or fitting. Interpolation and extrapolation in 62.2 Table 5.3 is not allowed. For airflow values not listed, use the next higher value. This table is not applicable for airflow > 125 cfm. NL = no limit on duct length of this size. X = not allowed, any length of duct of this size with assumed turns, elbows, fittings will exceed the rated pressure drop. |  |  |  |  |  |  |  |  |  |  |

| E. Other Requirements |  |
| --- | --- |
| The items listed below (6.1 through 6.8) correspond to the information given in ASHRAE 62.2 Section 6 "Other Requirements". Refer also to Chapter 4.6 of the Residential Compliance Manual (Section 4.6.5) for information describing these "Other Requirements". The signature of the Responsible Person in the declaration statement below certifies that the building complies with these requirements specified in ASHRAE 62.2 Section 6.1 through 6.9 if applicable. |  |
| 01 | 6.1 Transfer Air. Measures shall be taken to minimize air movement across envelope components to occupiable spaces from garages, unconditioned crawl spaces, and unconditioned attics. Supply and balanced ventilation systems shall be designed and constructed to provide ventilation air directly from the outdoors. |
| 02 | 6.2 Instructions and Labeling. Information on the ventilation design and/or ventilation systems installed, instructions on their proper operation to meet the requirements of this standard, and instructions detailing any required maintenance (similar to that provided for HVAC systems) shall be provided to the owner and the occupant of the dwelling unit. Controls shall be labeled as to their function (unless that function is obvious, such as toilet exhaust fan switches). See Chapter 13 of Guideline 242 for information on instructions and labeling. |
| 03 | 6.3 Clothes Dryers. Clothes dryers shall be exhausted directly to the outdoors. |
| 04 | 6.4 Combustion and Solid-Fuel Burning Appliances. Combustion and solid-fuel burning appliances must be provided with adequate combustion and ventilation air and vented in accordance with manufacturer’s installation instructions, NFPA 54/ANSI Z223.1, National Fuel Gas Code, NFPA 31, Standard for the Installation of Oil-Burning Equipment, or NFPA 211, Standard for Chimneys, Fireplaces, Vents, and Solid-Fuel Burning Appliances, or other equivalent code acceptable to the building official. Where atmospherically vented combustion appliances or solid-fuel burning appliances are located inside the pressure boundary, the total net exhaust flow of the two largest exhaust fans (not including a summer cooling fan intended to be operated only when windows or other air inlets are open) shall not exceed 15 cfm/100 ft² (75 Lps/100 m2) of occupiable space when in operation at full capacity. If the designed total net flow exceeds this limit, the net exhaust flow must be reduced by reducing the exhaust flow or providing compensating outdoor airflow. Atmospherically vented combustion appliances do not include direct-vent appliances. |
| 05 | 6.5 Garages. When an occupiable space adjoins a garage, the design must prevent migration of contaminants to the adjoining occupiable space. Air seal the walls, ceilings, and floors that separate garages from occupiable space. To be considered air sealed, all joints, seams, penetrations, openings between door assemblies and their respective jambs and framing, and other sources of air leakage through wall and ceiling assemblies separating the garage from the residence and its attic area shall be caulked, gasketed, weather stripped, wrapped, or otherwise sealed to limit air movement. Doors between garages and occupiable spaces shall be gasketed or made substantially airtight with weather stripping. |
| 06 | 6.6 Ventilation Opening Area. Spaces shall have ventilation openings as listed below. Such openings shall meet the requirements of Section 6.8. |
| 07 | 6.7 Minimum Filtration. Mechanical systems that supply air to an occupiable space through ductwork exceeding 10 ft (3 m) in length and through a thermal conditioning component, except evaporative coolers, shall be provided with a filter having a designated minimum efficiency of MERV 6, or better, when tested in accordance with ANSI/ASHRAE Standard 52.2, Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size, or a minimum Particle Size Efficiency of 50% in the 3.0-10 µm range in accordance with AHRI Standard 680, Performance Rating of Residential Air Filter Equipment. The system shall be designed such that all recirculated and mechanically supplied outdoor air is filtered before passing through the thermal conditioning components. The filter shall be located and installed in such a manner as to facilitate access and regular service by the owner. |
| 08 | 6.8 Air Inlets. Air inlets that are part of the ventilation design shall be located a minimum of 10 ft (3 m) from known sources of contamination such as a stack, vent, exhaust hood, or vehicle exhaust. The intake shall be placed so that entering air is not obstructed by snow, plantings, or other material. Forced air inlets shall be provided with rodent/insect screens (mesh not larger than 1/2 inch). |
| 09 | 6.9 Carbon Monoxide Detectors. A carbon monoxide alarm shall be installed in each dwelling unit in accordance with NFPA 720, Standard for the Installation of Carbon Monoxide (CO) Detection and Warning Equipment14, and shall be consistent with requirements of applicable laws, codes, and standards. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| F. Air Moving Equipment |  |
| --- | --- |
| The items listed below (7.1 through 7.3) correspond to the information given in ASHRAE 62.2 Section 7 "Air-Moving Equipment". Refer also to Chapter 4.6 of the Residential Compliance Manual (Section 4.6.6) for information describing these requirements in more detail. The signature of the Responsible Person in the declaration statement below certifies that the building complies with these requirements specified in ASHRAE 62.2 Section 7.1 through 7.3 if applicable. |  |
| 01 | 7.1 Selection and Installation. Ventilation devices and equipment shall be tested and listed in accordance with specific standards. Installations of systems or equipment shall be carried out in accordance with manufacturers’ design requirements and installation instructions. |
| 02 | 7.2 Sound Ratings for Fans. Ventilation fans shall be rated for sound at no less than the minimum airflow rate required by this standard, as noted below. These sound ratings shall be at a minimum of 0.1 in. w.c. (25 Pa) static pressure. 7.2.1 Whole-Building or Continuous Ventilation Fans. These fans shall be rated for sound at a maximum of 1.0 sone. 7.2.2 Intermittent Local Exhaust Fans. Fans used to comply with Section 5.2 shall be rated for sound at a maximum of 3 sone, unless their maximum rated airflow exceeds 400 cfm (200 L/s). (Some exceptions may apply.) |
| 03 | 7.3 Multibranch Exhaust Ducting. If more than one of the exhaust fans in a dwelling unit shares a common exhaust duct, each fan shall be equipped with a back-draft damper to prevent the recirculation of exhaust air from one room to another through the exhaust ducting system. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| G. Multifamily Buildings - Other Requirements |  |
| --- | --- |
| The items listed below correspond to the information given in ASHRAE 62.2 Section 8 "Multifamily Buildings". Refer also to Chapter 4.6 of the Residential Compliance Manual (Section 4.6.5) for information describing these requirements in more detail. The signature of the Responsible Person in the declaration statement below certifies that the building complies with these requirements specified in ASHRAE 62.2 Section 8, if applicable. |  |
| 01 | 8.2 Whole-Building Mechanical Ventilation. For multifamily buildings, the term “building” in Section 4 refers to a single dwelling unit. 8.4.1 Transfer Air. Measures shall be taken to minimize air movement across envelope components separating dwelling units, including sealing penetrations in the common walls, ceilings, and floors of each unit and by sealing vertical chases adjacent to the units. All doors between dwelling units and common hallways shall be gasketed or made substantially airtight. 8.4.1.1 Compliance. One method of demonstrating compliance with Section 8.4.1 shall be to verify a leakage rate below a maximum of 0.2 cfm/ft2 (100 L/s per 100 m2) of the dwelling unit envelope area (i.e., the sum of the area of the walls between dwelling units, exterior walls, ceiling and floor) at a test pressure of 50 Pa by a blower door test. The test shall be conducted with the dwelling unit as if it were exposed to outdoor air on all sides, top, and bottom by opening doors and windows of adjacent dwelling units. 8.5.1 Exhaust Ducts. Exhaust fans in separate dwelling units shall not share a common exhaust duct. Exhaust inlets from more than one dwelling unit may be served by a single exhaust fan downstream of all the exhaust inlets if the fan is designated and intended to run continuously or if each inlet is equipped with a back-draft damper to prevent cross-contamination when the fan is not running. 8.5.2 Supply Ducts. Supply outlets to more than one dwelling unit may be served by a single fan upstream of all the supply outlets if the fan is designed and intended to run continuously or if each supply outlet is equipped with a back-draft damper to prevent cross-contamination when the fan is not running. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Installation documentation is accurate and complete. |  |  |  |
| Documentation Author Name: |  | Documentation Author Signature: |  |
| Documentation Author Company Name: |  | Date Signed: |  |
| Address: |  | CEA/HERS Certification Identification (if applicable): |  |
| City/State/Zip: |  | Phone: |  |
| Responsible Person's Declaration statement |  |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: ### The information provided on this Certificate of Installation is true and correct. ### I am either: a) a responsible person eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction, or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Installation and attest to the declarations in this statement, or b) I am an authorized representative of the responsible person and attest to the declarations in this statement on the responsible person’s behalf. - The constructed or installed features, materials, components or manufactured devices (the installation) identified on this Certificate of Installation conforms to all applicable codes and regulations and the installation conforms to the requirements given on the Certificate of Compliance, plans, and specifications approved by the enforcement agency. - I understand that a HERS rater will check the installation to verify compliance and if such checking determines the installation fails to comply, I am required to offer any necessary corrective action at no charge to the building owner. - I will ensure that a registered copy of this Certificate of Installation shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Installation is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| Responsible Builder/Installer Name: | Responsible Builder/Installer Signature: |  |  |
| Company Name: (Installing Subcontractor or General Contractor or Builder/Owner) | Position With Company (Title): |  |  |
| Address: | CSLB License: |  |  |
| City/State/Zip: | Phone: |  | Date Signed: |
| Third Party Quality Control Program (TPQCP) Status: | Name of TPQCP (if applicable): |  |  |

CF2R-MCH-27b-H User Instructions

Section A. General Information

- This information is automatically pulled from the CF1R. This is the unique identifier for this dwelling unit. Needed mostly for multifamily dwelling units. Ventilation is calculated and provided for each dwelling unit individually.

- This information is automatically pulled from the CF1R. Choices are “single family” and “low-rise multifamily”.

- This information is automatically pulled from the CF1R. Choices are “New Construction” and “Addition greater than 1,000 ft2”.

- Value to be entered in the field equals the conditioned floor area of the space for which the ventilation is being calculated, in ft2. For additions over 1,000 ft2, this will be the floor area of the existing home plus the addition.

- Value to be entered in the field equals the number of bedrooms in the home. For additions over 1,000 ft2, this will be the number of bedrooms in the existing home plus the number of bedrooms in the addition.

- Select the Ventilation Operation Schedule method used from the choices provided:

- Continuous (the fan that provides ventilation will run 24/7)

- Intermittent (the fan that provides ventilation will be on some of the time and off some of the time)

- Select the Whole Building Ventilation Rate Calculation Method from the choices provided:

- Fan Ventilation Rate Method (only assumes ventilation from the ventilation fan)

- Total Ventilation Rate Method (assumes that some ventilation is provided by infiltration)

- Select the Whole Building Ventilation System Type from the choices provided:

- Standalone – Exhaust (ventilation fan[s] push air out of the house)

- Standalone – Supply (ventilation fan[s] push air into house)

- Standalone - Balanced (ventilation fan[s] push air into AND out of the house in equal amounts)

- Central Fan Integrated – CFI (central space condition system fan is used to pull air into the house) Note: these may not run continuously. If “Continuous” is chosen in A06 an error message will be shown. These types of ventilation systems will trigger extra field verification and scrutiny by inspection personnel.

- Enter the location in the residence where the IAQ fan is located.

Section B. Whole Building Continuous Ventilation – Total Ventilation Rate Method

- This value is automatically calculated using 62.2 equation 4.2a. The equation used to calculate this value in the field equals:

- If A02= Single Family then [(0.03 x conditioned floor area A04) + 7.5(Number of bedrooms A05 + 1)] = Required Continuous Whole-Building Ventilation Rate

- If A02= Multifamily then [(0.05 x conditioned floor area A04) + 7.5(Number of bedrooms A05 + 1)] = Required Continuous Whole-Building Ventilation Rate

- This information is automatically pulled from the registered MCH-24 for this dwelling unit. Note: The Total Ventilation Rate Method requires specific infiltration measurements that must be documented on a MCH-24.

- This value is automatically calculated. The equation used to calculate this value in the field equals: (CFM50 B02 x 0.055)/144 = Equivalent Leakage Area (ELA)

- This information is automatically pulled from the registered MCH-24 for this dwelling unit. Note: The Total Ventilation Rate Method requires specific infiltration measurements that must be documented on a MCH-24.

- This value is automatically calculated. The equation used to calculate this value in the field equals: (CFM50 B04 x 0.055)/144 = Equivalent Leakage Area (ELA)

- Calculated value. This is the average of the pressurization and depressurization Equivalent Leakage Areas.

- User entered value. Enter the vertical distance from the lowest above-grade floor to the highest ceiling, in feet.

- User entered value. Enter the Weather Shielding Factor (wsf) from 62.2 Appendix X Table X1.

| NORMATIVE APPENDIX X: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| INFILTRATION EFFECTIVENESS WEATHER AND SHIELDING FACTORS (WSF) |  |  |  |  |  |
| TABLE X1 U.S. Climates |  |  |  |  |  |
| TMY3 | wsf | Weather Station | Latitude | Longitude | State |
| 690150 | 0.5 | Twentynine Palms | 34.3 | –116.17 | California |
| 722860 | 0.43 | March AFB | 33.9 | –117.25 | California |
| 722868 | 0.45 | Palm Springs Intl | 33.83 | –116.50 | California |
| 722869 | 0.42 | Riverside Muni | 33.95 | –117.45 | California |
| 722880 | 0.39 | Burbank–Glendale–Pasadena AP | 34.2 | –118.35 | California |
| 722885 | 0.39 | Santa Monica Muni | 34.02 | –118.45 | California |
| 722886 | 0.39 | Van Nuys Airport | 34.22 | –118.48 | California |
| 722895 | 0.55 | Lompoc (AWOS) | 34.67 | –120.47 | California |
| 722897 | 0.51 | San Luis Co Rgnl | 35.23 | –120.63 | California |
| 722899 | 0.45 | Chino Airport | 33.97 | –117.63 | California |
| 722900 | 0.38 | San Diego Lindbergh Field | 32.73 | –117.17 | California |

| NORMATIVE APPENDIX X: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| INFILTRATION EFFECTIVENESS WEATHER AND SHIELDING FACTORS (WSF) |  |  |  |  |  |  |  |  |  |
| TABLE X1 U.S. Climates |  |  |  |  |  |  |  |  |  |
| TMY3 |  | wsf |  | Weather Station | Latitude |  | Longitude |  | State |
| 722903 |  | 0.39 |  | San Diego/Montgomery | 32.82 |  | –117.13 |  | California |
| 722904 |  | 0.4 |  | Chula Vista Brown Field NAAS | 32.58 |  | –116.98 |  | California |
| 722906 |  | 0.39 |  | San Diego North Island NAS | 32.7 |  | –117.20 |  | California |
| 722926 |  | 0.4 |  | Camp Pendleton MCAS | 33.3 |  | –117.35 |  | California |
| 722927 |  | 0.38 |  | Carlsbad/Palomar | 33.13 |  | –117.28 |  | California |
| 722930 |  | 0.39 |  | San Diego Miramar NAS | 32.87 |  | –117.13 |  | California |
| 722950 |  | 0.42 |  | Los Angeles Intl Arpt | 33.93 |  | –118.40 |  | California |
| 722956 |  | 0.38 |  | Jack Northrop Fld H | 33.92 |  | –118.33 |  | California |
| 722970 |  | 0.38 |  | Long Beach Daugherty Fld | 33.83 |  | –118.17 |  | California |
| 722976 |  | 0.34 |  | Fullerton Municipal | 33.87 |  | –117.98 |  | California |
| 722977 |  | 0.36 |  | Santa Ana John Wayne AP | 33.68 |  | –117.87 |  | California |
| 723805 |  | 0.51 |  | Needles Airport | 34.77 |  | –114.62 |  | California |
| 723810 |  | 0.59 |  | Edwards AFB | 34.9 |  | –117.87 |  | California |
| 723815 |  | 0.58 |  | Daggett Barstow–Daggett AP | 34.85 |  | –116.80 |  | California |
| 723816 |  | 0.62 |  | Lancaster Gen Wm Fox Field | 34.73 |  | –118.22 |  | California |
| 723820 |  | 0.57 |  | Palmdale Airport | 34.63 |  | –118.08 |  | California |
| 723830 |  | 0.68 |  | Sandberg | 34.75 |  | –118.72 |  | California |
| 723840 |  | 0.43 |  | Bakersfield Meadows Field | 35.43 |  | –119.05 |  | California |
| 723890 |  | 0.45 |  | Fresno Yosemite Intl AP | 36.78 |  | –119.72 |  | California |
| 723895 |  | 0.42 |  | Porterville (AWOS) | 36.03 |  | –119.07 |  | California |
| 723896 |  | 0.43 |  | Visalia Muni (AWOS) | 36.32 |  | –119.40 |  | California |
| 723910 |  | 0.45 |  | Point Mugu Nf | 34.12 |  | –119.12 |  | California |
| 723925 |  | 0.44 |  | Santa Barbara Municipal AP | 34.43 |  | –119.85 |  | California |
| 723926 |  | 0.43 |  | Camarillo (AWOS) | 34.22 |  | –119.08 |  | California |
| 723927 |  | 0.45 |  | Oxnard Airport | 34.2 |  | –119.20 |  | California |
| 723940 |  | 0.52 |  | Santa Maria Public Arpt | 34.92 |  | –120.47 |  | California |
| 723965 |  | 0.53 |  | Paso Robles Municipal Arpt | 35.67 |  | –120.63 |  | California |
| 724800 |  | 0.55 |  | Bishop Airport | 37.37 |  | –118.35 |  | California |
| 724815 |  | 0.46 |  | Merced/Macready Fld | 37.28 |  | –120.52 |  | California |
| 724830 |  | 0.51 |  | Sacramento Executive Arpt | 38.5 |  | –121.50 |  | California |
| 724837 |  | 0.45 |  | Beale AFB | 39.13 |  | –121.43 |  | California |
| 724838 |  | 0.5 |  | Yuba Co | 39.1 |  | –121.57 |  | California |
| 724839 |  | 0.51 |  | Sacramento Metropolitan AP | 38.7 |  | –121.58 |  | California |
| 724915 |  | 0.49 |  | Monterey Naf | 36.6 |  | –121.87 |  | California |
| 724917 |  | 0.54 |  | Salinas Municipal AP | 36.67 |  | –121.60 |  | California |
| 724920 |  | 0.5 |  | Stockton Metropolitan Arpt | 37.9 |  | –121.23 |  | California |
| 724926 |  | 0.47 |  | Modesto City–County AP | 37.63 |  | –120.95 |  | California |
| 724927 |  | 0.53 |  | Livermore Municipal | 37.7 |  | –121.82 |  | California |
| 724930 |  | 0.54 |  | Oakland Metropolitan Arpt | 37.72 |  | –122.22 |  | California |
| 724935 |  | 0.47 |  | Hayward Air Term | 37.67 |  | –122.12 |  | California |
| 724936 |  | 0.53 |  | Concord–Buchanan Field | 38 |  | –122.05 |  | California |
| 724940 |  | 0.6 |  | San Francisco Intl AP | 37.62 |  | –122.40 |  | California |
| 724945 |  | 0.48 |  | San Jose Intl AP | 37.37 |  | –121.93 |  | California |
| 724955 |  | 0.55 |  | Napa Co. Airport | 38.22 |  | –122.28 |  | California |
| 724957 |  | 0.49 |  | Santa Rosa (AWOS) | 38.52 |  | –122.82 |  | California |
| 725845 |  | 0.44 |  | Blue Canyon AP | 39.3 |  | –120.72 |  | California |
| 725846 |  | 0.66 |  | Truckee–Tahoe | 39.32 |  | –120.13 |  | California |
| 725847 |  | 0.64 |  | South Lake Tahoe | 38.9 |  | –120.00 |  | California |
| 725905 |  | 0.47 |  | Ukiah Municipal AP | 39.13 |  | –123.20 |  | California |
| 725910 |  | 0.5 |  | Red Bluff Municipal Arpt 40.15 –122.25 California | 40.15 |  | –122.25 |  | California |
| 725920 |  | 0.47 |  | Redding Municipal Arpt 40.52 –122. | 40.52 |  | –122.32 |  | California |
| NORMATIVE APPENDIX X Cont: |  |  |  |  |  |  |  |  |  |
| INFILTRATION EFFECTIVENESS WEATHER AND SHIELDING FACTORS (WSF) |  |  |  |  |  |  |  |  |  |
| TABLE X1 U.S. Climates |  |  |  |  |  |  |  |  |  |
| TMY3 | wsf |  | Weather Station |  | Latitude | Longitude |  | State |  |
| 725945 | 0.56 |  | Arcata Airport 40.98 –124.10 California |  | 40.98 | –124.10 |  | California |  |
| 725946 | 0.6 |  | Crescent City Faa Ai 41.78 –124.2 |  | 41.78 | –124.23 |  | California |  |
| 725955 | 0.55 |  | Montague Siskiyou County AP 41.78 –122.47 California |  | 41.78 | –122.47 |  | California |  |
| 725958 | 0.59 |  | Alturas 41.50 –120.5 |  | 41.5 | –120.53 |  | California |  |
| 745090 | 0.45 |  | Mountain View Moffett Fld NAS |  | 37.4 | –122.05 |  | California |  |
| 745160 | 0.67 |  | Travis Field AFB |  | 38.27 | –121.93 |  | California |  |
| 746120 | 0.52 |  | China Lake Naf |  | 35.68 | –117.68 |  | California |  |
| 747020 | 0.5 |  | Lemoore Reeves NAS |  | 36.33 | –119.95 |  | California |  |
| 747185 | 0.46 |  | Imperial |  | 32.83 | –115.58 |  | California |  |
| 747187 | 0.46 |  | Palm Springs Thermal AP |  | 33.63 | –116.17 |  | California |  |
| 747188 | 0.48 |  | Blythe Riverside Co Arpt |  | 33.62 | –114.72 |  | California |  |

- This value is automatically calculated using 62.2 equation 4.5. The equation used to calculate this value in the field equals: [1,000 x (Equivalent Leakage Area (ELA) B06/ conditioned floor area A04) x (Vertical Distance B07/8.2)^0.4]= Normalized Leakage (NL)

- This value is automatically calculated using 62.2 equation 4.6a. The equation used to calculate this value in the field equals: (Normalized Leakage (NL) B09 x conditioned floor area A04)/7.3= Ventilation Provided by Infiltration in CFM

- This value is automatically calculated using 62.2 equation 4.7. It is the difference between the total required ventilation and the ventilation provided by infiltration. The equation used to calculate this value in the field equals: (Required Continuous Whole-Building Ventilation Rate B01 - Ventilation Provided by Infiltration B10 = Required Continuous Whole-Building Ventilation Rate of the fan in CFM

- User entered value equals the installed ventilation rate of the fan in CFM. This value will be field verified by enforcement personnel.

Title 24, Part 6, Section 150.0(o) Ventilation for Indoor Air Quality. All dwelling units shall meet the requirements of ANSI/ASHRAE Standard62.2. Ventilation and Acceptable Indoor Air Quality in Low-Rise Residential Buildings. Equation and table numbering on this form corresponds to the numbering for that information in the published ANSI/ASHRAE Standard 62.2-2010.

| A. Dwelling Mechanical Ventilation - General Information |  |  |
| --- | --- | --- |
| 01 | Dwelling Unit Name | <<calculated field, referenced data from CF1R.>> |
| 02 | Building Type | <<reference value from CF1R, but allow user to override and select one from list: Single Family, Multifamily, Non-dwelling Unit>> |
| 03 | Project Scope | << calculated field, referenced data from CF1R>> |
| 04 | Total Conditioned Floor Area of Dwelling Unit (For addition projects the conditioned floor area equals existing area plus addition area) | <<calculated field: default value reference from MCH-01; or allow user to override default and input value xxxxx; flag overridden values and report in project status notes field >> |
| 05 | Number of Bedrooms in Dwelling Unit (For addition projects the number of bedrooms equals the existing bedrooms plus addition bedrooms) | <<calculated field: default value reference from MCH-01>> |
| 06 | Ventilation Operation Schedule | << user pick one from list: **Continuous; **Intermittent; or **N/A>> |
| 07 | Whole-Building Ventilation Rate Calculation Method | << user pick one from list: **Fan Ventilation Rate Method (4.1.1), **Total Ventilation Rate Method (4.1.2); or **N/A.>> |
| 08 | Whole Building Ventilation System Type | << calculated value if registered CF1R form equals CF1R-PRF-01, reference data from CF1R (note default report from CF1R equivalent to exhaust) and allow user to override and select *N/A; else if registered CF1R form equals CF1R-NCB-01, user pick one from list: **Standalone - Exhaust; or **Standalone - Supply; or **Standalone – Balanced; or **Central Fan Integrated (CFI); or **N/A>> if A06= Continuous and A08= Central Fan Integrated; then display: “Central Fan Integrated Ventilation System Not Allowed to Operate Continuously - Do Not Proceed”>> |
| 09 | IAQ Fan Location | <<user input, text>> |
| 10 | determine compliance method for this document; display applicable tables below; (this row not visible to user) | <<calculated field: if A06= Continuous and A07= Fan Ventilation Rate Method; then display method: **27a - Continuous Ventilation Airflow - Fan Vent Rate Method; elsif A06= Continuous and A07= Total Ventilation Rate Method; then display method: **27b - Continuous Ventilation Airflow - Total Vent Rate Method; elsif A06= Intermittent and A07= Fan Ventilation Rate Method; **27c - Intermittent Ventilation Airflow - Fan Vent Rate Method; elsif A06= Intermittent and A07= Total Ventilation Rate Method; then display method: **27d - Intermittent Ventilation Airflow - Total Vent Rate Method; Elseif A06 = N/A and A07 = N/A, then display method: **27e – Mechanical Ventilation – Non-dwelling Unit>> |
| Note: Non-dwelling units do not meet the definition for a dwelling unit as defined in Section 100.1(b). Non-dwelling units are not designed to provide independent living facilities and do not provide permanent provisions for living, sleeping, eating, cooking and sanitation. |  |  |

MCH-27b - Continuous Ventilation Airflow – Total Ventilation Rate Method

| B. Whole-Building Continuous Ventilation - Total Ventilation Rate Method A mechanical supply system, exhaust system, or combination thereof shall provide whole-building ventilation with outdoor air each hour at no less than the rate in 62.2 equation 4.7. |  |  |
| --- | --- | --- |
| 01 | Total Required Ventilation rate ( fan + infiltration), (Qtot) | <<calculated field, numeric: (use equation 4.1a): [(Z x row A04) + 7.5(row A05 + 1)], (cfm). For single family Z = 0.03, for multifamily Z = 0.05>> |
| 02 | CFM50 – Depressurization | << calculated field, if a registered MCH-24a-e form is found, then display: CFM50 depressurization value elseif no registered no MCH-24a-e is found, then display text: “Registered MCH-24a-e required – Do Not Proceed”>> |
| 03 | Equivalent Leakage Area Depressurization | <<calculated field, equals (row B02 x 0.055)/144>> |
| 04 | CFM50 – Pressurization | << calculated field, referenced data fromMCH-24a-e, display: CFM50 pressurization value >> |
| 05 | Equivalent Leakage Area Pressurization | <<calculated field, equals (row B04 x 0.055)/144>> |
| 06 | Equivalent Leakage Area used for ventilation | <<calculated field, equals row (B03 + B05)/2>> |
| 07 | What is the vertical distance from the lowest above-grade floor to the highest ceiling in feet? | << user input, (ft)>> |
| 08 | What is the weather and shielding factor (wsf) for the city listed in 62.2 Appendix X Table X1 ? | <<user input, drop down selection from California Energy Commission Adaptation of ANSI/ASHRAE Standard 62.2-2010>> Note: See reprint at end of document |
| 09 | Normalized Leakage (NL) | << calculated using 62.2 equation 4.5: 1000 x (row B06/row A04) x (row B07 / 8.2)^0.4>> |
| 10 | Ventilation Provided by Infiltration In (Qinf) | << calculated using 62.2 equation 4.6a: (row B09 x row B08 x A04)/7.3, (CFM)>> |
| 11 | Required Continuous Whole-Building Ventilation Rate (Qfan) | <<calculated using equation 4.7: row B01 – row B10, (CFM)>> |
| 12 | Installed Continuous Whole-Building Ventilation Rate | <<user entry, (CFM)>> |

| C. Compliance Statement |  |
| --- | --- |
| 01 | <<If the Installed Continuous Whole-Building Ventilation Rate B12 is equal to or greater than the required Continuous Whole-Building Ventilation rate B11 then display text: "Building Passes Continuous Whole-Building Ventilation Rate Test"; If the Installed Continuous Whole-Building Ventilation Rate B12 is less than the required Continuous Whole-Building Ventilation Rate B11 then display text: "Building Fails Continuous Whole-Building Ventilation Rate Test">> |

| D. Local Mechanical Exhaust System – Fan Selection and Duct Design Criteria for Compliance |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Local mechanical exhaust fans shall be installed in each kitchen and bathroom. Delivered local ventilation rates: - All local ventilation rates have been measured using a flow hood, flow grid, or other airflow measuring device and meet the requirements of 62.2 Tables 5.1 or 5.2; OR - The airflow rating at a pressure of 0.25 in. w.c. of a certified fan is assumed because the local ventilation system duct sizing meets the prescriptive requirements of 62.2 Table 5.3, or manufacturer's design criteria. |  |  |  |  |  |  |  |  |  |  |
| Table 5.1 Intermittent Local Ventilation Exhaust Airflow Rates |  |  |  |  |  |  |  |  |  |  |
| Application |  | Airflow |  | Notes |  |  |  |  |  |  |
| Kitchen |  | 100 cfm |  | Vented range hood (including appliance-range hood combinations) required if exhaust fan flow is less than 5 ACH. |  |  |  |  |  |  |
| Bathroom |  | 50 cfm |  |  |  |  |  |  |  |  |
| Table 5.2 Continuous Local Ventilation Exhaust Airflow Rates |  |  |  |  |  |  |  |  |  |  |
| Application |  | Airflow |  | Notes |  |  |  |  |  |  |
| Kitchen |  | 5 ACH |  | Based on kitchen volume. |  |  |  |  |  |  |
| Bathroom |  | 20 cfm |  |  |  |  |  |  |  |  |
| Table 5.3 Prescriptive Duct Sizing Requirements |  |  |  |  |  |  |  |  |  |  |
| Duct Type | Flex Duct |  |  |  |  |  | Smooth Duct |  |  |  |
| Fan Rating cfm @ 0.25 in. w.g. | 50 |  | 80 |  | 100 | 125 | 50 | 80 | 100 | 125 |
|  | Maximum Allowable Duct Length (ft) |  |  |  |  |  |  |  |  |  |
| Diameter, (in) | Flex Duct |  |  |  |  |  | Smooth Duct |  |  |  |
| 3 | X |  | X |  | X | X | 5 | X | X | X |
| 4 | 70 |  | 3 |  | X | X | 105 | 35 | 5 | X |
| 5 | NL |  | 70 |  | 35 | 20 | NL | 135 | 85 | 55 |
| 6 | NL |  | NL |  | 125 | 95 | NL | NL | NL | 145 |
| 7 and above | NL |  | NL |  | NL | NL | NL | NL | NL | NL |
| This table assumes no elbows. Deduct 15 ft of allowable duct length for each turn, elbow, or fitting. Interpolation and extrapolation in 62.2 Table 5.3 is not allowed. For airflow values not listed, use the next higher value. This table is not applicable for airflow > 125 cfm. NL = no limit on duct length of this size. X = not allowed, any length of duct of this size with assumed turns, elbows, fittings will exceed the rated pressure drop. |  |  |  |  |  |  |  |  |  |  |

| E. Other Requirements |  |
| --- | --- |
| The items listed below (6.1 through 6.8) correspond to the information given in ASHRAE 62.2 Section 6 "Other Requirements". Refer also to Chapter 4.6 of the Residential Compliance Manual (Section 4.6.5) for information describing these "Other Requirements". The signature of the Responsible Person in the declaration statement below certifies that the building complies with these requirements specified in ASHRAE 62.2 Section 6.1 through 6.9 if applicable. |  |
| 01 | 6.1 Transfer Air. Measures shall be taken to minimize air movement across envelope components to occupiable spaces from garages, unconditioned crawl spaces, and unconditioned attics. Supply and balanced ventilation systems shall be designed and constructed to provide ventilation air directly from the outdoors. |
| 02 | 6.2 Instructions and Labeling. Information on the ventilation design and/or ventilation systems installed, instructions on their proper operation to meet the requirements of this standard, and instructions detailing any required maintenance (similar to that provided for HVAC systems) shall be provided to the owner and the occupant of the dwelling unit. Controls shall be labeled as to their function (unless that function is obvious, such as toilet exhaust fan switches). See Chapter 13 of Guideline 242 for information on instructions and labeling. |
| 03 | 6.3 Clothes Dryers. Clothes dryers shall be exhausted directly to the outdoors |
| 04 | 6.4 Combustion and Solid-Fuel Burning Appliances. Combustion and solid-fuel burning appliances must be provided with adequate combustion and ventilation air and vented in accordance with manufacturer’s installation instructions, NFPA 54/ANSI Z223.1, National Fuel Gas Code, NFPA 31, Standard for the Installation of Oil-Burning Equipment, or NFPA 211, Standard for Chimneys, Fireplaces, Vents, and Solid-Fuel Burning Appliances, or other equivalent code acceptable to the building official. Where atmospherically vented combustion appliances or solid-fuel burning appliances are located inside the pressure boundary, the total net exhaust flow of the two largest exhaust fans (not including a summer cooling fan intended to be operated only when windows or other air inlets are open) shall not exceed 15 cfm/100 ft² (75 Lps/100 m2) of occupiable space when in operation at full capacity. If the designed total net flow exceeds this limit, the net exhaust flow must be reduced by reducing the exhaust flow or providing compensating outdoor airflow. Atmospherically vented combustion appliances do not include direct-vent appliances. |
| 05 | 6.5 Garages. When an occupiable space adjoins a garage, the design must prevent migration of contaminants to the adjoining occupiable space. Air seal the walls, ceilings, and floors that separate garages from occupiable space. To be considered air sealed, all joints, seams, penetrations, openings between door assemblies and their respective jambs and framing, and other sources of air leakage through wall and ceiling assemblies separating the garage from the residence and its attic area shall be caulked, gasketed, weather stripped, wrapped, or otherwise sealed to limit air movement. Doors between garages and occupiable spaces shall be gasketed or made substantially airtight with weather stripping. |
| 06 | 6.6 Ventilation Opening Area. Spaces shall have ventilation openings as listed below. Such openings shall meet the requirements of Section 6.8. |
| 07 | 6.7 Minimum filtration. Mechanical systems that supply air to an occupiable space through ductwork exceeding 10 ft (3 m) in length and through a thermal conditioning component, except evaporative coolers, shall be provided with a filter having a designated minimum efficiency of MERV 6, or better, when tested in accordance with ANSI/ASHRAE Standard 52.2, Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size, or a minimum Particle Size Efficiency of 50% in the 3.0-10 µm range in accordance with AHRI Standard 680, Performance Rating of Residential Air Filter Equipment. The system shall be designed such that all recirculated and mechanically supplied outdoor air is filtered before passing through the thermal conditioning components. The filter shall be located and installed in such a manner as to facilitate access and regular service by the owner. |
| 08 | 6.8 Air Inlets. Air inlets that are part of the ventilation design shall be located a minimum of 10 ft (3 m) from known sources of contamination such as a stack, vent, exhaust hood, or vehicle exhaust. The intake shall be placed so that entering air is not obstructed by snow, plantings, or other material. Forced air inlets shall be provided with rodent/insect screens (mesh not larger than 1/2 inch). |
| 09 | 6.9 Carbon Monoxide Detectors. A carbon monoxide alarm shall be installed in each dwelling unit in accordance with NFPA 720, Standard for the Installation of Carbon Monoxide (CO) Detection and Warning Equipment14, and shall be consistent with requirements of applicable laws, codes, and standards. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| F. Air Moving Equipment |  |
| --- | --- |
| The items listed below (7.1 through 7.3) correspond to the information given in ASHRAE 62.2 Section 7 "Air-Moving Equipment". Refer also to Chapter 4.6 of the Residential Compliance Manual (Section 4.6.6) for information describing these requirements in more detail. The signature of the Responsible Person in the declaration statement below certifies that the building complies with these requirements specified in ASHRAE 62.2 Section 7.1 through 7.3 if applicable. |  |
| 01 | 7.1 Selection and Installation. Ventilation devices and equipment shall be tested and listed in accordance with specific standards. Installations of systems or equipment shall be carried out in accordance with manufacturers’ design requirements and installation instructions. |
| 02 | 7.2 Sound Ratings for Fans. Ventilation fans shall be rated for sound at no less than the minimum airflow rate required by this standard, as noted below. These sound ratings shall be at a minimum of 0.1 in. w.c. (25 Pa) static pressure. 7.2.1 Whole-Building or Continuous Ventilation Fans. These fans shall be rated for sound at a maximum of 1.0 sone. 7.2.2 Intermittent Local Exhaust Fans. Fans used to comply with Section 5.2 shall be rated for sound at a maximum of 3 sone, unless their maximum rated airflow exceeds 400 cfm (200 L/s). (Some exceptions may apply.) |
| 03 | 7.3 Multibranch Exhaust Ducting. If more than one of the exhaust fans in a dwelling unit shares a common exhaust duct, each fan shall be equipped with a back-draft damper to prevent the recirculation of exhaust air from one room to another through the exhaust ducting system. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| G. Multifamily Buildings - Other Requirements <<only print this section if multi-family is selected in row A.1>> |  |
| --- | --- |
| The items listed below correspond to the information given in ASHRAE 62.2 Section 8 "Multifamily Buildings". Refer also to Chapter 4.6 of the Residential Compliance Manual (Section 4.6.5) for information describing these requirements in more detail. The signature of the Responsible Person in the declaration statement below certifies that the building complies with these requirements specified in ASHRAE 62.2 Section 8, if applicable. |  |
| 01 | 8.2 Whole-Building Mechanical Ventilation. For multifamily buildings, the term “building” in Section 4 refers to a single dwelling unit. 8.4.1 Transfer Air. Measures shall be taken to minimize air movement across envelope components separating dwelling units, including sealing penetrations in the common walls, ceilings, and floors of each unit and by sealing vertical chases adjacent to the units. All doors between dwelling units and common hallways shall be gasketed or made substantially airtight. 8.4.1.1 Compliance. One method of demonstrating compliance with Section 8.4.1 shall be to verify a leakage rate below a maximum of 0.2 cfm/ft2 (100 L/s per 100 m2) of the dwelling unit envelope area (i.e., the sum of the area of the walls between dwelling units, exterior walls, ceiling and floor) at a test pressure of 50 Pa by a blower door test. The test shall be conducted with the dwelling unit as if it were exposed to outdoor air on all sides, top, and bottom by opening doors and windows of adjacent dwelling units. 8.5.1 Exhaust Ducts. Exhaust fans in separate dwelling units shall not share a common exhaust duct. Exhaust inlets from more than one dwelling unit may be served by a single exhaust fan downstream of all the exhaust inlets if the fan is designated and intended to run continuously or if each inlet is equipped with a back-draft damper to prevent cross-contamination when the fan is not running. 8.5.2 Supply Ducts. Supply outlets to more than one dwelling unit may be served by a single fan upstream of all the supply outlets if the fan is designed and intended to run continuously or if each supply outlet is equipped with a back-draft damper to prevent cross-contamination when the fan is not running. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Installation documentation is accurate and complete. |  |  |  |
| Documentation Author Name: |  | Documentation Author Signature: |  |
| Documentation Author Company Name: |  | Date Signed: |  |
| Address: |  | CEA/CEPE/HERS certification identification (if applicable): |  |
| City/State/Zip: |  | Phone: |  |
| Responsible Person's Declaration statement |  |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: ### The information provided on this Certificate of Installation is true and correct. ### I am either: a) a responsible person eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction, or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Installation and attest to the declarations in this statement, or b) I am an authorized representative of the responsible person and attest to the declarations in this statement on the responsible person’s behalf. - The constructed or installed features, materials, components or manufactured devices (the installation) identified on this Certificate of Installation conforms to all applicable codes and regulations and the installation conforms to the requirements given on the Certificate of Compliance, plans, and specifications approved by the enforcement agency. - I understand that a HERS rater will check the installation to verify compliance and if such checking determines the installation fails to comply, I am required to offer any necessary corrective action at no charge to the building owner. - I will ensure that a registered copy of this Certificate of Installation shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Installation is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| Responsible Builder/Installer Name: | Responsible Builder/Installer Signature: |  |  |
| Company Name: (Installing Subcontractor or General Contractor or Builder/Owner) | Position With Company (Title): |  |  |
| Address: | CSLB License: |  |  |
| City/State/Zip: | Phone: |  | Date Signed: |
| Third Party Quality Control Program (TPQCP) Status: | Name of TPQCP (if applicable): |  |  |