Title 24, Part 6, Section 150.0(o) Ventilation for Indoor Air Quality. All dwelling units shall meet the requirements of ANSI/ASHRAE Standard62.2. Ventilation and Acceptable Indoor Air Quality in Low-Rise Residential Buildings. Equation and table numbering on this form corresponds to the numbering for that information in the published ANSI/ASHRAE Standard 62.2-2010.

| A. Dwelling Mechanical Ventilation - General Information |  |  |
| --- | --- | --- |
| 01 | Dwelling Unit Name |  |
| 02 | Building Type |  |
| 03 | Project Scope |  |
| 04 | Total Conditioned Floor Area of Dwelling Unit (For addition projects the conditioned floor area equals existing area plus addition area) |  |
| 05 | Number of Bedrooms in Dwelling Unit (For addition projects the number of bedrooms equals the existing bedrooms plus addition bedrooms) |  |
| 06 | Ventilation Operation Schedule |  |
| 07 | Whole-Building Ventilation Rate Calculation Method |  |
| 08 | Whole Building Ventilation System Type |  |
| 09 | IAQ Fan Location |  |

### MCH-27d - Intermittent Ventilation Airflow - Total Ventilation Rate Method

| B. Continuous Ventilation Airflow – Total Vent Rate Method A mechanical supply system, exhaust system, or combination thereof shall provide whole-building ventilation with outdoor air each hour at no less than the rate in 62.2 equation 4.7. |  |  |
| --- | --- | --- |
| 01 | Total Required Ventilation Rate ( fan + infiltration), (Qtot) |  |
| 02 | CFM50 – Depressurization |  |
| 03 | Equivalent Leakage Area Depressurization |  |
| 04 | CFM50 – Pressurization |  |
| 05 | Equivalent Leakage Area Pressurization |  |
| 06 | Equivalent Leakage Area Used for Ventilation |  |
| 07 | What is the vertical distance from the lowest above-grade floor to the highest ceiling in feet? |  |
| 08 | What is the weather and shielding factor (wsf) for the city listed in 62.2 Appendix X Table X1 ? |  |
| 09 | Normalized Leakage (NL) |  |
| 10 | Ventilation Provided by Infiltration In (Qinf) |  |
| 11 | Required Continuous Whole-Building Ventilation Rate (Qfan) |  |

| C. Intermittent Ventilation The effective ventilation rate of an intermittent system is the combination of its delivered capacity, its fractional on-time, cycle time, and the ventilation effectiveness from Table 4.2. |  |  |
| --- | --- | --- |
| 01 | In a single on off cycle, what is the ON time in hours? |  |
| 02 | In a single on off cycle, what is the OFF time in hours? |  |
| 03 | Fan Cycle Time Check |  |
| 04 | Daily Fractional On Time (f used in Table 4.2) |  |
| 05 | Daily Fractional On Time Check |  |
| 06 | Turnover (N used in Table 4.2) |  |
| 07 | Ventilation Effectiveness (e, from Table 4.2) |  |
| 08 | Intermittent Ventilation Rate |  |
| 09 | Installed Intermittent Ventilation Rate |  |
| 10 | System Fan Efficacy Compliance Status |  |
| 11 | System Fan Efficacy Compliance |  |

| D. Compliance Statement |  |
| --- | --- |
| 01 |  |

| E. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Verification documentation is accurate and complete. |  |  |  |
| Documentation Author Name: | Documentation Author Signature: |  |  |
| Company: | Date Signed: |  |  |
| Address: | CEA/HERS Certification Information (if applicable): |  |  |
| City/State/Zip: | Phone: |  |  |
| Responsible Person's Declaration statement |  |  |  |
| I certify the following under penalty of perjury, under the laws of the State of California: - The information provided on this Certificate of Verification is true and correct. - I am the certified HERS Rater who performed the verification identified and reported on this Certificate of Verification (responsible rater). - The installed features, materials, components, manufactured devices, or system performance diagnostic results that require HERS verification identified on this Certificate of Verification comply with the applicable requirements in Reference Appendices RA2, RA3, and the requirements specified on the Certificate of Compliance for the building approved by the enforcement agency. - The information reported on applicable sections of the Certificate(s) of Installation (CF2R) signed and submitted by the person(s) responsible for the construction or installation conforms to the requirements specified on the Certificate(s) of Compliance (CF1R) approved by the enforcement agency. - I will ensure that a registered copy of this Certificate of Verification shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Verification is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| BUILDER OR INSTALLER INFORMATION AS SHOWN ON THE CERTIFICATE OF INSTALLATION |  |  |  |
| Company Name (Installing Subcontractor, General Contractor, or Builder/Owner): |  |  |  |
| Responsible Builder or Installer Name: |  | CSLB License: |  |
| HERS PROVIDER DATA REGISTRY INFORMATION |  |  |  |
| Sample Group Number (if applicable): |  |  | Dwelling Test Status in Sample Group (if applicable): |
| HERS RATER INFORMATION |  |  |  |
| HERS Rater Company Name: |  |  |  |
| Responsible Rater Name: |  |  | Responsible Rater Signature: |
| Responsible Rater Certification Number w/ this HERS Provider: |  |  | Date Signed: |

CF3R-MCH-27d-H User Instruction

Section A. General Information

- This information is automatically pulled from the CF1R. This is the unique identifier for this dwelling unit. Needed mostly for multifamily dwelling units.  Ventilation is calculated and provided for each dwelling unit individually.

- This information is automatically pulled from the CF1R. Choices are “single family” and “low-rise multifamily”.

- This information is automatically pulled from the CF1R. Choices are “New Construction” and “Addition greater than 1,000 ft2”.

- Value to be entered in the field equals the conditioned floor area of the space for which the ventilation is being calculated, in ft2.  For additions over 1000 ft2, this will be the floor area of the existing home plus the addition.

- Value to be entered in the field equals the number of bedrooms in the home.  For additions over 1,000 ft2, this will be the number of bedrooms in the existing home plus the number of bedrooms in the addition.

- Select the Ventilation Operation Schedule method used from the choices provided:

- Continuous (the fan that provides ventilation will run 24/7)

- Intermittent (the fan that provides ventilation will be on some of the time and off some of the time)

- Select the Whole Building Ventilation Rate Calculation Method from the choices provided:

- Fan Ventilation Rate Method (only assumes ventilation from the ventilation fan)

- Total Ventilation Rate Method (assumes that some ventilation is provided by infiltration)

- Select the Whole Building Ventilation System Type from the choices provided:

- Standalone – Exhaust (ventilation fan[s] push air out of the house)

- Standalone – Supply (ventilation fan[s] push air into house)

- Standalone - Balanced (ventilation fan[s] push air into AND out of the house in equal amounts)

- Central Fan Integrated – CFI (central space condition system fan is used to pull air into the house)  Note: these may not run continuously.  If “Continuous” is chosen in A06 an error message will be shown.

- This information is automatically pulled from the CF2R.

Section B. Whole Building Continuous Ventilation – Total Ventilation Rate Method

- This value is automatically calculated using 62.2 equation 4.2a. The equation used to calculate this value in the field equals:

- If A02= Single Family then [(0.03 x conditioned floor area A04) + 7.5(Number of bedrooms A05 + 1)] = Required Continuous Whole-Building Ventilation Rate

- If A02= Multifamily then [(0.05 x conditioned floor area A04) + 7.5(Number of bedrooms A05 + 1)] = Required Continuous Whole-Building Ventilation Rate

- This information is automatically pulled from the registered MCH-24 for this dwelling unit.  Note:  The Total Ventilation Rate Method requires specific infiltration measurements that must be documented on either a MCH-24.

- This value is automatically calculated.  The equation used to calculate this value in the field equals: (CFM50 B02 x 0.055)/144 = Equivalent Leakage Area (ELA).

- This information is automatically pulled from the registered MCH-24 for this dwelling unit.  Note:  The Total Ventilation Rate Method requires specific infiltration measurements that must be documented on either a MCH-24.

- This value is automatically calculated.  The equation used to calculate this value in the field equals: (CFM50 B04 x 0.055)/144 = Equivalent Leakage Area (ELA).

- Calculated value.  This is the average of the pressurization and depressurization equivalent leakage areas.

- User entered value.  Enter the vertical distance from the lowest above-grade floor to the highest ceiling, in feet.

- User entered value.  Enter the Weather Shielding Factor (wsf) from 62.2 Appendix X Table X1.

| NORMATIVE APPENDIX X: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| INFILTRATION EFFECTIVENESS WEATHER AND SHIELDING FACTORS (WSF) |  |  |  |  |  |
| TABLE X1 U.S. Climates |  |  |  |  |  |
| TMY3 | wsf | Weather Station | Latitude | Longitude | State |
| 690150 | 0.5 | Twentynine Palms | 34.3 | –116.17 | California |
| 722860 | 0.43 | March AFB | 33.9 | –117.25 | California |
| 722868 | 0.45 | Palm Springs Intl | 33.83 | –116.50 | California |
| 722869 | 0.42 | Riverside Muni | 33.95 | –117.45 | California |
| 722880 | 0.39 | Burbank–Glendale–Pasadena AP | 34.2 | –118.35 | California |
| 722885 | 0.39 | Santa Monica Muni | 34.02 | –118.45 | California |
| 722886 | 0.39 | Van Nuys Airport | 34.22 | –118.48 | California |
| 722895 | 0.55 | Lompoc (AWOS) | 34.67 | –120.47 | California |
| 722897 | 0.51 | San Luis Co Rgnl | 35.23 | –120.63 | California |
| 722899 | 0.45 | Chino Airport | 33.97 | –117.63 | California |
| 722900 | 0.38 | San Diego Lindbergh Field | 32.73 | –117.17 | California |
| 722903 | 0.39 | San Diego/Montgomery | 32.82 | –117.13 | California |
| NORMATIVE APPENDIX X: |  |  |  |  |  |
| INFILTRATION EFFECTIVENESS WEATHER AND SHIELDING FACTORS (WSF) |  |  |  |  |  |
| TABLE X1 U.S. Climates |  |  |  |  |  |
| TMY3 | wsf | Weather Station | Latitude | Longitude | State |
| 722904 | 0.4 | Chula Vista Brown Field NAAS | 32.58 | –116.98 | California |
| 722906 | 0.39 | San Diego North Island NAS | 32.7 | –117.20 | California |
| 722926 | 0.4 | Camp Pendleton MCAS | 33.3 | –117.35 | California |
| 722927 | 0.38 | Carlsbad/Palomar | 33.13 | –117.28 | California |
| 722930 | 0.39 | San Diego Miramar NAS | 32.87 | –117.13 | California |
| 722950 | 0.42 | Los Angeles Intl Arpt | 33.93 | –118.40 | California |
| 722956 | 0.38 | Jack Northrop Fld H | 33.92 | –118.33 | California |
| 722970 | 0.38 | Long Beach Daugherty Fld | 33.83 | –118.17 | California |
| 722976 | 0.34 | Fullerton Municipal | 33.87 | –117.98 | California |
| 722977 | 0.36 | Santa Ana John Wayne AP | 33.68 | –117.87 | California |
| 723805 | 0.51 | Needles Airport | 34.77 | –114.62 | California |
| 723810 | 0.59 | Edwards AFB | 34.9 | –117.87 | California |
| 723815 | 0.58 | Daggett Barstow–Daggett AP | 34.85 | –116.80 | California |
| 723816 | 0.62 | Lancaster Gen Wm Fox Field | 34.73 | –118.22 | California |
| 723820 | 0.57 | Palmdale Airport | 34.63 | –118.08 | California |
| 723830 | 0.68 | Sandberg | 34.75 | –118.72 | California |
| 723840 | 0.43 | Bakersfield Meadows Field | 35.43 | –119.05 | California |
| 723890 | 0.45 | Fresno Yosemite Intl AP | 36.78 | –119.72 | California |
| 723895 | 0.42 | Porterville (AWOS) | 36.03 | –119.07 | California |
| 723896 | 0.43 | Visalia Muni (AWOS) | 36.32 | –119.40 | California |
| 723910 | 0.45 | Point Mugu Nf | 34.12 | –119.12 | California |
| 723925 | 0.44 | Santa Barbara Municipal AP | 34.43 | –119.85 | California |
| 723926 | 0.43 | Camarillo (AWOS) | 34.22 | –119.08 | California |
| 723927 | 0.45 | Oxnard Airport | 34.2 | –119.20 | California |
| 723940 | 0.52 | Santa Maria Public Arpt | 34.92 | –120.47 | California |
| 723965 | 0.53 | Paso Robles Municipal Arpt | 35.67 | –120.63 | California |
| 724800 | 0.55 | Bishop Airport | 37.37 | –118.35 | California |
| 724815 | 0.46 | Merced/Macready Fld | 37.28 | –120.52 | California |
| 724830 | 0.51 | Sacramento Executive Arpt | 38.5 | –121.50 | California |
| 724837 | 0.45 | Beale AFB | 39.13 | –121.43 | California |
| 724838 | 0.5 | Yuba Co | 39.1 | –121.57 | California |
| 724839 | 0.51 | Sacramento Metropolitan AP | 38.7 | –121.58 | California |
| 724915 | 0.49 | Monterey Naf | 36.6 | –121.87 | California |
| 724917 | 0.54 | Salinas Municipal AP | 36.67 | –121.60 | California |
| 724920 | 0.5 | Stockton Metropolitan Arpt | 37.9 | –121.23 | California |
| 724926 | 0.47 | Modesto City–County AP | 37.63 | –120.95 | California |
| 724927 | 0.53 | Livermore Municipal | 37.7 | –121.82 | California |
| 724930 | 0.54 | Oakland Metropolitan Arpt | 37.72 | –122.22 | California |
| 724935 | 0.47 | Hayward Air Term | 37.67 | –122.12 | California |
| 724936 | 0.53 | Concord–Buchanan Field | 38 | –122.05 | California |
| 724940 | 0.6 | San Francisco Intl AP | 37.62 | –122.40 | California |
| 724945 | 0.48 | San Jose Intl AP | 37.37 | –121.93 | California |
| 724955 | 0.55 | Napa Co. Airport | 38.22 | –122.28 | California |
| 724957 | 0.49 | Santa Rosa (AWOS) | 38.52 | –122.82 | California |
| 725845 | 0.44 | Blue Canyon AP | 39.3 | –120.72 | California |
| 725846 | 0.66 | Truckee–Tahoe | 39.32 | –120.13 | California |
| 725847 | 0.64 | South Lake Tahoe | 38.9 | –120.00 | California |
| 725905 | 0.47 | Ukiah Municipal AP | 39.13 | –123.20 | California |
| 725910 | 0.5 | Red Bluff Municipal Arpt 40.15 –122.25 California | 40.15 | –122.25 | California |
| 725920 | 0.47 | Redding Municipal Arpt 40.52 –122. | 40.52 | –122.32 | California |
| 725945 | 0.56 | Arcata Airport 40.98 –124.10 California | 40.98 | –124.10 | California |
| NORMATIVE APPENDIX X: |  |  |  |  |  |
| INFILTRATION EFFECTIVENESS WEATHER AND SHIELDING FACTORS (WSF) |  |  |  |  |  |
| TABLE X1 U.S. Climates |  |  |  |  |  |
| TMY3 | wsf | Weather Station | Latitude | Longitude | State |
| 725946 | 0.6 | Crescent City Faa Ai 41.78 –124.2 | 41.78 | –124.23 | California |
| 725955 | 0.55 | Montague Siskiyou County AP 41.78 –122.47 California | 41.78 | –122.47 | California |
| 725958 | 0.59 | Alturas 41.50 –120.5 | 41.5 | –120.53 | California |
| 745090 | 0.45 | Mountain View Moffett Fld NAS | 37.4 | –122.05 | California |
| 745160 | 0.67 | Travis Field AFB | 38.27 | –121.93 | California |
| 746120 | 0.52 | China Lake Naf | 35.68 | –117.68 | California |
| 747020 | 0.5 | Lemoore Reeves NAS | 36.33 | –119.95 | California |
| 747185 | 0.46 | Imperial | 32.83 | –115.58 | California |
| 747187 | 0.46 | Palm Springs Thermal AP | 33.63 | –116.17 | California |
| 747188 | 0.48 | Blythe Riverside Co Arpt | 33.62 | –114.72 | California |

- This value is automatically calculated using 62.2 equation 4.5. The equation used to calculate this value in the field equals: [1,000 x (Equivalent Leakage Area (ELA) B06/ conditioned floor area A04) x (Vertical  Distance B07/8.2)^0.4]= Normalized Leakage (NL).

- This value is automatically calculated using 62.2 equation 4.6a. The equation used to calculate this value in the field equals: (Normalized Leakage (NL) B09 x conditioned floor area A04)/7.3= Ventilation Provided by Infiltration in (CFM).

- This value is automatically calculated using 62.2 equation 4.7. It is the difference between the total required ventilation and the ventilation provided by infiltration.  The equation used to calculate this value in the field equals: (Required Continuous Whole-Building Ventilation Rate B01 - Ventilation Provided by Infiltration B10 = Required Continuous Whole-Building Ventilation Rate of the fan in (CFM).

Section C. Intermittent Ventilation

- Intermittent ventilation requires controls that ensure a regular operating schedule every 24 hours. Within a 24 hour period there will be one or more regular on off cycles. For a single on off cycle, enter the ON time in hours. This value will be verified by a HERS rater.

- Intermittent ventilation requires controls that ensure a regular operating schedule every 24 hours.  Within a 24 hour period there will be one or more regular on off cycles. For a single on off cycle, enter the OFF time in hours. This value will be verified by a HERS rater.

- This row performs an automatic check. The intermittent ventilation system must operate at least once every 24 hours. For this to occur, the on time plus the off time in a single on off cycle must be less than 24 hours. If this is true, “OK” will appear. If this is not true, an error will appear here and correct values will need to be entered into C01 and C02. The equation used to calculate this value in the field equals: Time on in hours C01 + Time off in hours C02.

- This value is automatically calculated. It is the daily fractional on time (f) used in 62.2 Table 4.2. A value of 0.60 means that in a 24 hour period the fan will run 60% of the time. The equation used to calculate this value in the field equals: On time in Hours C01/(On time in Hours C01 + Off time in Hours C02)= Daily fractional on time (decimal)

- This row performs an automatic check. The ventilation system must operate at least 10% of the time. C04 must be greater than or equal to 0.10. If this is true, “OK” will appear. If this is not true, an error message will appear here and correct values will need to be entered into C01 and C02.

- This value is automatically calculated. It is the turnover (N) used in 62.2 Table 4.2. The equation used to calculate this value in the field equals: [12.8 x Continuous Whole-Building Ventilation Rate B01 x (On time in Hours C01 + Off time in Hours C02)]/ Conditioned floor area of dwelling unit row A04= Turnover N

- User entered value from Table 4.2. Use the daily fractional time (f) from C04 and the turnover (N) from C06 to determine the ventilation effectiveness value (e) from 62.2 Table 4.2.

| TABLE 4.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Mechanical Ventilation Effectiveness for Intermittent Fans |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Turnover, N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fractional |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| On-Time, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f | 0 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5 | 6 | 8 | 12 | 20 | 40 | 100+ |  |
| 0.00 | 1.00 | 0.95 | 0.88 | 0.78 | 0.60 | 0.00 |  |  |  |  |  |  |  |  |  |  |
| 0.05 | 1.00 | 0.96 | 0.90 | 0.81 | 0.67 | 0.41 | 0.00 |  |  |  |  |  |  |  |  |  |
| 0.10 | 1.00 | 0.96 | 0.91 | 0.83 | 0.72 | 0.55 | 0.21 | 0.00 |  |  |  |  |  |  |  |  |
| 0.15 | 1.00 | 0.96 | 0.92 | 0.85 | 0.76 | 0.63 | 0.44 | 0.18 | 0.00 |  |  |  |  |  |  |  |
| 0.20 | 1.00 | 0.97 | 0.93 | 0.87 | 0.79 | 0.69 | 0.56 | 0.40 | 0.03 | 0.00 |  |  |  |  |  |  |
| 0.25 | 1.00 | 0.97 | 0.94 | 0.89 | 0.82 | 0.74 | 0.64 | 0.53 | 0.26 | 0.02 | 0.00 |  |  |  |  |  |
| 0.30 | 1.00 | 0.98 | 0.95 | 0.90 | 0.85 | 0.78 | 0.71 | 0.62 | 0.42 | 0.24 | 0.00 |  |  |  |  |  |
| 0.35 | 1.00 | 0.98 | 0.95 | 0.92 | 0.87 | 0.82 | 0.76 | 0.69 | 0.54 | 0.39 | 0.14 | 0.00 |  |  |  |  |
| 0.40 | 1.00 | 0.98 | 0.96 | 0.93 | 0.89 | 0.85 | 0.80 | 0.75 | 0.63 | 0.52 | 0.32 | 0.02 | 0.00 |  |  |  |
| 0.45 | 1.00 | 0.99 | 0.97 | 0.94 | 0.91 | 0.88 | 0.84 | 0.79 | 0.70 | 0.61 | 0.45 | 0.21 | 0.00 |  |  |  |
| 0.50 | 1.00 | 0.99 | 0.97 | 0.95 | 0.93 | 0.90 | 0.87 | 0.83 | 0.76 | 0.69 | 0.57 | 0.37 | 0.13 | 0.00 | 0.00 |  |
| 0.60 | 1.00 | 0.99 | 0.98 | 0.97 | 0.96 | 0.94 | 0.92 | 0.90 | 0.86 | 0.81 | 0.74 | 0.61 | 0.45 | 0.27 | 0.14 |  |
| 0.70 | 1.00 | 1.00 | 0.99 | 0.98 | 0.98 | 0.97 | 0.96 | 0.94 | 0.92 | 0.90 | 0.85 | 0.78 | 0.68 | 0.55 | 0.46 |  |
| 0.80 | 1.00 | 1.00 | 1.00 | 0.99 | 0.99 | 0.99 | 0.98 | 0.98 | 0.97 | 0.96 | 0.94 | 0.90 | 0.85 | 0.77 | 0.70 |  |
| 0.90 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 0.99 | 0.99 | 0.99 | 0.98 | 0.97 | 0.96 | 0.93 | 0.88 |  |
| 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |  |

- This value is automatically calculated using 62.2 equation 4.8. It represents the required airflow in cfm that must be delivered during the ventilation system ON times. This value will be verified by a HERS rater. The equation used to calculate this value in the field equals: Continuous Whole-Building Ventilation Rate B01/(Daily fractional on time C04 x ventilation effectiveness value C07= required Intermittent ventilation rate (CFM).

- User entered value equals the installed intermittent ventilation rate in (CFM). This value will be field verified by a HERS Rater.

- This information is automatically pulled from the registered MCH-22. Note: this line only visible if CFI System selected in A08.

- This information is automatically calculated based on C10. Note: this line only visible if CFI System selected in A08

### Title 24, Part 6, Section 150.0(o) Ventilation for Indoor Air Quality. All dwelling units shall meet the requirements of ANSI/ASHRAE Standard62.2. Ventilation and Acceptable Indoor Air Quality in Low-Rise Residential Buildings. Equation and table numbering on this form corresponds to the numbering for that information in the published ANSI/ASHRAE Standard 62.2-2010.

| A. Dwelling Mechanical Ventilation - General Information |  |  |
| --- | --- | --- |
| 01 | Dwelling Unit Name | <<calculated field, referenced data from CF1R.>> |
| 02 | Building Type | <<calculated field, referenced data from CF1R. (note: possible results are Single Family; Multifamily)>> |
| 03 | Project Scope | << calculated field, referenced data from CF1R>> |
| 04 | Total Conditioned Floor Area of Dwelling Unit (For addition projects the conditioned floor area equals existing area plus addition area) | <<calculated field: default value reference from MCH-01; or allow user to override default and input value xxxxx; flag overridden values and report in project status notes field >> |
| 05 | Number of Bedrooms in Dwelling Unit (For addition projects the number of bedrooms equals the existing bedrooms plus addition bedrooms) | <<calculated field: default value reference from MCH-01; or allow user to override default and input value xx; flag overridden values and report in project status notes field >> |
| 06 | Ventilation Operation Schedule | << user pick one from list: **Continuous; **or Intermittent>> |
| 07 | Whole-Building Ventilation Rate Calculation Method | << user pick one from list: **Fan Ventilation Rate Method (4.1.1), or **Total Ventilation Rate Method (4.1.2.>> |
| 08 | Whole Building Ventilation System Type | << calculated value if registered CF1R form equals CF1R-PRF-01, reference data from CF1R (note default report from CF1R equivalent to exhaust); else if registered CF1R form equals CF1R-NCB-01, user pick one from list: **Standalone - Exhaust; or **Standalone - Supply; or **Standalone – Balanced; or **Central Fan Integrated (CFI)>> if A06= Continuous and A08= Central Fan Integrated; then display method: Central Fan Integrated Ventilation System Not Allowed to Operate Continuously - Do Not Proceed>> |
| 09 | IAQ Fan Location | <<Auto filled text: referenced data from CF2R>> |
| 10 | determine compliance method for this document; display applicable tables below; (this row not visible to user) | <<calculated field: if A06= Continuous and A07= Fan Ventilation Rate Method; then display method: **27a - Continuous Ventilation Airflow - Fan Vent Rate Method; elsif A06= Continuous and A07= Total Ventilation Rate Method; then display method: **27b - Continuous Ventilation Airflow - Total Vent Rate Method; elsif A06= Intermittent and A07= Fan Ventilation Rate Method; **27c - Intermittent Ventilation Airflow - Fan Vent Rate Method; elsif A06= Intermittent and A07= Total Ventilation Rate Method; then display method: **27d - Intermittent Ventilation Airflow - Total Vent Rate Method;>> |

### MCH-27d - Intermittent Ventilation Airflow - Total Ventilation Rate Method

| B. Continuous Ventilation Airflow – Total Vent Rate Method A mechanical supply system, exhaust system, or combination thereof shall provide whole-building ventilation with outdoor air each hour at no less than the rate in 62.2 equation 4.7. |  |  |
| --- | --- | --- |
| 01 | Total Required Ventilation Rate ( fan + infiltration), (Qtot) | <<calculated field, numeric: (use equation 4.1a): {(Z x row A04) + [7.5(row A05 + 1)]}, (cfm). For single family Z = 0.03, for multifamily Z = 0.05>> |
| 02 | CFM50 – Depressurization | << calculated field, if a registered MCH-24a-e form is found, then display: CFM50 depressurization value elseif no registered no MCH-24a-e is found, then display text: “Registered MCH-24a-e required”, do not proceed >> |
| 03 | Equivalent Leakage Area Depressurization | <<calculated field, equals (row B02 x 0.055)/144>> |
| 04 | CFM50 – Pressurization | << calculated field, referenced data fromMCH-24a-e, display: CFM50 pressurization value>> |
| 05 | Equivalent Leakage Area Pressurization | <<calculated field, equals (row B04 x 0.055)/144>> |
| 06 | Equivalent Leakage Area used for ventilation | <<calculated field, equals row (B03 + B05)/2>> |
| 07 | What is the vertical distance from the lowest above-grade floor to the highest ceiling in feet? | << user input, (ft)>> |
| 08 | What is the weather and shielding factor (wsf) for the city listed in 62.2 Appendix X Table X1 ? | <<user input, drop down selection from California Energy Commission Adaptation of ANSI/ASHRAE Standard 62.2-2010>> Note: See reprint at end of document |
| 09 | Normalized Leakage (NL) | << calculated using 62.2 equation 4.5: 1000 x (row B06/row A04) x (row B07 / 8.2)^0.4>> |
| 10 | Ventilation Provided by Infiltration In (Qinf) | << calculated using 62.2 equation 4.6a: (row B09 x row B08 x A04)/7.3, (CFM)>> |
| 11 | Required Continuous Whole-Building Ventilation Rate (Qfan) | <<calculated using equation 4.7: row B01 – row B10, (CFM)>> |

| C. Intermittent Ventilation The effective ventilation rate of an intermittent system is the combination of its delivered capacity, its fractional on-time, cycle time, and the ventilation effectiveness from Table 4.2. |  |  |
| --- | --- | --- |
| 01 | In a single on off cycle, what is the ON time in hours? | <<user entry (hours)>> |
| 02 | In a single on off cycle, what is the OFF time in hours? | <<user entry (hours)>> |
| 03 | Fan Cycle Time Check | <<calculated value, (row C01 + C02), if less than or equal to 24 Hours, report “Fan Cycle Time Meets Requirement; if greater than 24 hours, report “Fan Cycle Time Does Not Meet Requirement - Do Not Proceed”>> |
| 04 | Daily Fractional On Time (f used in Table 4.2) | <<calculated value: row C01 / (row C01 + row C02)>> |
| 05 | Daily Fractional On Time Check | <<calculated value, (row C04), if greater than or equal to 0.1, report “Daily Fractional on Time Check Meets Requirement; if less than 0.1, report “Daily Fractional on Time Check Does Not Meet Requirement - Do Not Proceed”>> |
| 06 | Turnover (N used in Table 4.2) | <<calculated value: 62.2 Equation 4.9(a): 12.8 x row B01 x (row C01 + row C02) / row A03 >> |
| 07 | Ventilation Effectiveness (e, from Table 4.2) | <<use values in row C04 and row C06 to lookup value from California Energy Commission Adaptation of ANSI/ASHRAE Standard 62.2 Table 4.2, interpolate as needed; interpolated value must be greater than zero if not, report “Fan Cycle on/off time must be adjusted – Do Not Proceed”>> Note: See reprint at end of document |
| 08 | Intermittent Ventilation Rate | <<calculated value: equation 4.8: row B01 / (row C04 x row C07), (cfm)>> |
| 09 | Installed Intermittent Ventilation Rate | <<user entry (CFM)>> |
| 10 | <<this line only visible if CFI System selected in A06>> System Fan Efficacy Compliance Status | << calculated field, if a registered MCH-22 form is found, then display: Actual Fan Efficacy Watts/CFM value from the MCH-22 elseif no registered no MCH-22 is found, then display text: “Registered MCH-22 required – Do Not Proceed” >> |
| 11 | <<this line only visible if CFI System selected in A06>> System Fan Efficacy Compliance | << calculated field, if row C10 is less than or equal to 0.58 watts/CFM, then display text: Pass elseif row C10 is greater than 0.58/watts CFM, then display text: Fail>> |

| D. Compliance Statement |  |
| --- | --- |
| 01 | <<If line A08 equals Exhaust, Supply or Balanced, and if line C03 equals Fan Cycle Time Meets Requirement, and if C05 equals Daily Fractional on Time Check Meets Requirement, and if C09 is greater than or equal to C08 then display text: "Building Passes Intermittent Ventilation Rate test"; elsif line A08 equals Exhaust, Supply or Balanced, and if line C03 equals Fan Cycle Time Does Not Meet Requirement - Do Not Proceed, or if C05 equals Daily Fractional on Time Check Does Not Meet Requirement - Do Not Proceed, or if C09 is less than C08 then display text: "Building Fails Intermittent Ventilation Rate test"; elsif line A08 equals Central Fan Integrated, and if line C03 equals Fan Cycle Time Meets Requirement, and if C05 equals Daily Fractional on Time Check Meets Requirement, and if C09 is greater than or equal to C08, and if C11 is equal to Pass then display text equals : "Building Passes Intermittent Ventilation Rate test"; elsif line A08 equals Central Fan Integrated, and if line C03 equals Fan Cycle Time Does Not Meet Requirement - Do Not Proceed, or if C05 equals Daily Fractional on Time Check Does Not Meet Requirement - Do Not Proceed, or if C09 is less than C08 then display text, or C11 is equal to Fail then display text equals : "Building Fails Intermittent Ventilation Rate test" |

| E. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 | <<if D01 = Building Passes Intermittent Ventilation Rate test then display: Complies: All specified verification protocol requirements on this document are met; else display: Does not comply: One or more specified verification protocol requirements on this document are not met>> |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Verification documentation is accurate and complete. |  |  |  |
| Documentation Author Name: | Documentation Author Signature: |  |  |
| Company: | Date Signed: |  |  |
| Address: | CEA/HERS Certification Information (if applicable): |  |  |
| City/State/Zip: | Phone: |  |  |
| Responsible Person's Declaration statement |  |  |  |
| I certify the following under penalty of perjury, under the laws of the State of California: - The information provided on this Certificate of Verification is true and correct. - I am the certified HERS Rater who performed the verification identified and reported on this Certificate of Verification (responsible rater). - The installed features, materials, components, manufactured devices, or system performance diagnostic results that require HERS verification identified on this Certificate of Verification comply with the applicable requirements in Reference Appendices RA2, RA3, and the requirements specified on the Certificate of Compliance for the building approved by the enforcement agency. - The information reported on applicable sections of the Certificate(s) of Installation (CF2R) signed and submitted by the person(s) responsible for the construction or installation conforms to the requirements specified on the Certificate(s) of Compliance (CF1R) approved by the enforcement agency. - I will ensure that a registered copy of this Certificate of Verification shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Verification is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| BUILDER OR INSTALLER INFORMATION AS SHOWN ON THE CERTIFICATE OF INSTALLATION |  |  |  |
| Company Name (Installing Subcontractor, General Contractor, or Builder/Owner): |  |  |  |
| Responsible Builder or Installer Name: |  | CSLB License: |  |
| HERS PROVIDER DATA REGISTRY INFORMATION |  |  |  |
| Sample Group Number (if applicable): |  |  | Dwelling Test Status in Sample Group (if applicable): |
| HERS RATER INFORMATION |  |  |  |
| HERS Rater Company Name: |  |  |  |
| Responsible Rater Name: |  |  | Responsible Rater Signature: |
| Responsible Rater Certification Number w/ this HERS Provider: |  |  | Date Signed: |