| A. General Information |  |  |
| --- | --- | --- |
| 01 | Dwelling Unit Name |  |

| B. Design HERS Verified Dwelling Unit Water Heating Systems Information This table reports the water heating system features that were specified on the registered CF1R compliance document for this project. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |

| C. Installed HERS Verified Dwelling Unit Water Heating Systems Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 |  | 02 | 03 | 04 |  | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 |
| Water Heating System ID or Name |  | Water Heating System Type | Water Heater Type | # of Water Heaters in System |  | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |
| 15 | Compliance Statement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| D. Installed Water Heater Manufacturer Information |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Manufacturer | Model Number |

| E. Mandatory Measures for All Domestic Hot Water Distribution Systems |  |  |
| --- | --- | --- |
| 01 | The following pipes are insulated, to the thicknesses required by Table 120.3A, except for those sections of pipe that are subject to one of the exceptions below: (RA4.4.1) - The first 5 feet (1.5 meters) of hot and cold water pipes from the storage tank. - All piping with a nominal diameter of 3/4 inch (19 millimeter) or larger. - All piping associated with a domestic hot water recirculation system regardless of the pipe diameter, except when cold water return is used in a demand system. - Piping from the heating source to storage tank or between tanks. - Piping buried below grade. - All hot water pipes from the heating source to the kitchen fixtures. The following sections of pipe do not have to be insulated: (RA4.4.1) - Piping installed in interior or exterior walls that is surrounded on all sides by at least 1 inch of insulation. - Piping installed in attics with a minimum of 4 inches (10 cm) of attic insulation on top - Piping that penetrates framing members shall not be required to have pipe insulation for the distance of the framing penetration. Metal piping that penetrates metal framing shall use grommets, plugs, wrapping or other insulating material to assure that no contact is made with the metal framing. Insulation shall butt securely against all framing members. |  |
| 02 | Piping buried below grade must be installed in a water proof and non-crushable casing or sleeve that allows for installation, removal, and replacement of the enclosed pipe and insulation. (Section 150.0(j)) |  |
| 03 | All elbows and tees shall be fully insulated. (RA4.4.1) |  |
| 04 | Where insulation is required, no piping shall be visible due to insulation voids, and all insulation shall fit tightly to the pipe. (RA4.4.1) |  |
| 05 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 06 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| F. HERS-Verified Pipe Insulation Credit Requirements Systems that utilize this distribution type shall comply with these requirements. |  |  |
| --- | --- | --- |
| 01 | All hot water piping shall comply with the insulation requirements in Table 120.3-A. (RA 4.4.14) |  |
| 02 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 03 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| G. HERS-Verified Parallel Piping Requirements Systems that utilize this distribution type shall comply with these requirements. |  |  |
| --- | --- | --- |
| 01 | Each central manifold has 5 feet or less of pipe between manifold and water heater. (RA 4.4.15) |  |
| 02 | For manifolds that include valves, the manifold must be readily accessible in accordance with the plumbing code. (RA 4.4.4) |  |
| 03 | Hot water distribution system piping from the manifold to the fixtures and appliances must take the most direct path. For example, piping from a second story manifold cannot supply the first floor. (RA 4.4.4) |  |
| 04 | The hot water distribution piping must be separated by at least 2 inches from any other hot water supply piping, and at least 6 inches from any cold water supply piping. Alternatively, the hot water supply piping must be insulated to the thicknesses shown in TABLE 120.3-A. (RA 4.4.4) |  |
| 05 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 06 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| H. HERS-Verified Compact Hot Water Distribution System Requirements Systems that utilize this distribution type shall comply with these requirements |  |  |  |
| --- | --- | --- | --- |
| 01 | Total Conditioned Floor Area (ft2): |  |  |
| 02 | Maximum allowed pipe run length from the water heater to the furthest point of use For the floor area served (feet): |  |  |
| 03 | The pipe run length from each water heater to the furthest fitting served by that water heater must be no greater than the maximum pipe run length above. |  |  |
| 04 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |  |
| 05 | Correction Notes: |  |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |  |

| I. HERS-Verified Demand Recirculation Manual Control Requirements Systems that utilize this distribution type shall comply with these requirements |  |  |
| --- | --- | --- |
| 01 | The system operates “on-demand”, meaning that the pump begins to operate shortly before or immediately after hot water draw begins, and stops when the return water temperature reaches a certain threshold value. (RA4.4.9/RA4.4.13) |  |
| 02 | After the pump has been activated, the controls shall allow the pump to operate until the water temperature at the thermo-sensor rises to one of the following values: (RA4.4.9(f)/RA4.4.13(d)) - Not more than 10°F ( 5.6°C) above the initial temperature of the water in the pipe - Not more than 102°F (38.9°C). |  |
| 03 | The controls shall limit pump operation to a maximum of 5 minutes for single dwellings, and 10 minutes for multiple dwellings, following any activation. This is provided in the event that the normal means of shutting off the pump have failed. (RA4.4.9(f)3/RA4.4.13(d)3) |  |
| 04 | Pump and control placement shall meet one of the following criteria: (RA4.4.9(d)/RA4.4.13(b)) - When a dedicated return line has been installed the pump, controls and thermo-sensor are installed at the end of the supply portion of the recirculation loop; or - The pump and controls are installed on the dedicated return line near the water heater and the thermo-sensor is installed in an accessible location as close to the end of the supply portion of the recirculation loop as possible; or - When the cold water line is used as the return, the pump, demand controls and thermo-sensor shall be installed in an accessible location at the end of supply portion of the hot water distribution line (typically under a sink). |  |
| 05 | Insulation is not required on the cold water line when it is used as the return. (RA4.4.9(e)/RA4.4.13(c)) |  |
| 06 | Each control shall have standby power of 1 Watt or less. Controls may be located in individual units or on the loop. Controls may be activated by wired or wireless mechanisms, including buttons, motion sensors, door switches and flow switches. (RA4.4.9(c)/RA4.4.13(a)) |  |
| 07 | If more than one loop installed each loop shall have its own pump and controls |  |
| 08 | Automatic air release valve is installed on the inlet side of the recirculation pump per Section 110.3(c)5A. |  |
| 09 | A check valve, or similar device, is located between the recirculation pump and the water heater per Section 110.3(c)5B. |  |
| 10 | Hose bibb is installed between the pump and the water heating equipment with an isolation valve between the hose bibb and the water heating equipment per Section 110.3(c)5C. |  |
| 11 | Isolation valves are installed on both sides of the pump. One of the isolation valves may be the same isolation valve as in item 10 above per Section 110.3(c)5D. |  |
| 12 | The cold water supply piping and the recirculation loop piping is not connected to the hot water storage tank drain port per Section 110.3(c)5E. |  |
| 13 | A check valve is installed on the cold water supply line between the hot water system and the next closest tee on the cold water supply line per Section 110.3(c)5F. |  |
| 14 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 15 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| J. HERS-Verified Demand Recirculation Sensor Control Requirements Systems that utilize this distribution type shall comply with these requirements |  |  |
| --- | --- | --- |
| 01 | The system operates “on-demand”, meaning that the pump begins to operate shortly before or immediately after hot water draw begins, and stops when the return water temperature reaches a certain threshold value. (RA4.4.10/RA4.4.13) |  |
| 02 | After the pump has been activated, the controls shall allow the pump to operate until the water temperature at the thermo-sensor rises to one of the following values: (RA4.4.10(f)/RA4.4.13(d)) - Not more than 10°F ( 5.6°C) above the initial temperature of the water in the pipe - Not more than 102°F (38.9°C). |  |
| 03 | The controls shall limit pump operation to a maximum of 5 minutes for single dwellings, and 10 minutes for multiple dwellings, following any activation. This is provided in the event that the normal means of shutting off the pump have failed. (RA4.4.10(f)3/RA4.4.13(d)3) |  |
| 04 | Pump and control placement shall meet one of the following criteria: (RA4.4.10(d)/RA4.4.13(b)) - When a dedicated return line has been installed the pump, controls and thermo-sensor are installed at the end of the supply portion of the recirculation loop; or - The pump and controls are installed on the dedicated return line near the water heater and the thermo-sensor is installed in an accessible location as close to the end of the supply portion of the recirculation loop as possible; or - When the cold water line is used as the return, the pump, demand controls and thermo-sensor shall be installed in an accessible location at the end of supply portion of the hot water distribution line (typically under a sink). |  |
| 05 | Insulation is not required on the cold water line when it is used as the return. (RA4.4.10(e)/RA4.4.13(c)) |  |
| 06 | Each control shall have standby power of 1 Watt or less. Controls may be located in individual units or on the loop. Controls may be activated by wired or wireless mechanisms, including buttons, motion sensors, door switches and flow switches. (RA4.4.10(c)/RA4.4.13(a)) |  |
| 07 | If more than one loop installed each loop shall have its own pump and controls |  |
| 08 | Automatic air release valve is installed on the inlet side of the recirculation pump per Section 110.3(c)5A. |  |
| 09 | A check valve, or similar device, is located between the recirculation pump and the water heater per Section 110.3(c)5B. |  |
| 10 | Hose bibb is installed between the pump and the water heating equipment with an isolation valve between the hose bibb and the water heating equipment per Section 110.3(c)5C. |  |
| 11 | Isolation valves are installed on both sides of the pump. One of the isolation valves may be the same isolation valve as in item 10 above per Section 110.3(c)5D. |  |
| 12 | The cold water supply piping and the recirculation loop piping is not connected to the hot water storage tank drain port per Section 110.3(c)5E. |  |
| 13 | A check valve is installed on the cold water supply line between the hot water system and the next closest tee on the cold water supply line per Section 110.3(c)5F. |  |
| 14 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 15 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| K. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Verification documentation is accurate and complete. |  |  |  |
| Documentation Author Name: | Documentation Author Signature: |  |  |
| Company: | Date Signed: |  |  |
| Address: | CEA/HERS Certification Information (if applicable): |  |  |
| City/State/Zip: | Phone: |  |  |
| Responsible Person's Declaration statement |  |  |  |
| I certify the following under penalty of perjury, under the laws of the State of California: - The information provided on this Certificate of Verification is true and correct. - I am the certified HERS Rater who performed the verification identified and reported on this Certificate of Verification (responsible rater). - The installed features, materials, components, manufactured devices, or system performance diagnostic results that require HERS verification identified on this Certificate of Verification comply with the applicable requirements in Reference Appendices RA2, RA3, and the requirements specified on the Certificate of Compliance for the building approved by the enforcement agency. - The information reported on applicable sections of the Certificate(s) of Installation (CF2R) signed and submitted by the person(s) responsible for the construction or installation conforms to the requirements specified on the Certificate(s) of Compliance (CF1R) approved by the enforcement agency. - I will ensure that a registered copy of this Certificate of Verification shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a registered copy of this Certificate of Verification is required to be included with the documentation the builder provides to the building owner at occupancy. |  |  |  |
| BUILDER OR INSTALLER INFORMATION AS SHOWN ON THE CERTIFICATE OF INSTALLATION |  |  |  |
| Company Name (Installing Subcontractor, General Contractor, or Builder/Owner): |  |  |  |
| Responsible Builder or Installer Name: |  | CSLB License: |  |
| HERS PROVIDER DATA REGISTRY INFORMATION |  |  |  |
| Sample Group Number (if applicable): |  |  | Dwelling Test Status in Sample Group (if applicable): |
| HERS RATER INFORMATION |  |  |  |
| HERS Rater Company Name: |  |  |  |
| Responsible Rater Name: |  |  | Responsible Rater Signature: |
| Responsible Rater Certification Number w/ this HERS Provider: |  |  | Date Signed: |

CF3R-PLB-22-H User Instructions

A. Dwelling Unit Name

01 This identifies the dwelling unit on this form and is reference from the CF1R.  One form is required for each dwelling unit in the building.

B. Design Central Water Heating Systems Information

This table reports the water heating system features that were specified on the registered CF1R compliance document for this project.    For information only and requires no user input.

C. Installed Central Water Heating Systems Information

This table reports the water heating system information that is being installed.  Require one line for each central system.

01 Water Heating System ID or Name – Reference information from CF1R.

02 Water Heating System Type – Reference information from CF1R.  The different kinds of water heating system type are DHW or Combined Hydronic.

03 Water Heater Type – Information from CF1R. The different kinds of water heaters are Large Storage, Small Storage, Heat Pump, Boiler, Large Instantaneous, Small Instantaneous or Indirect.

04 # of Water Heaters in system – Reference information from CF1R.

05 Water Heater Storage Volume (gal) – User input. Value may be N/A if water heater type is instantaneous with zero storage.

06 Fuel Type – Reference information from CF1R. The different kinds of fuel types are natural gas, propane, oil, or electricity.

07 Rated Input Type – Reference information from CF1R. For natural gas, propane and oil fuel type the input type is Btu/Hr.  For electric the input type is kW.

08 Rated Input Value – User input. Numerical value of the rated input. Must be equal to or less than value indicated on the CF1R.

09 Heating Efficiency Type – Reference information from CF1R. Different efficiency types are Energy Factor, AFUE, and Thermal Efficiency.

10 Heating Efficiency Value – User input. Numerical value of the Heating Efficiency. Must be equal to or higher efficiency than value indicated on the CF1R.

11 Standby Loss – User input. Must be equal to or less than value indicated on the CF1R. Value may be N/A if CF1R value is N/A.

12 Exterior Insul. R-Value – User input. Must be equal to or higher than value indicated on the CF1R. Value may be N/A if CF1R value is N/A.

13 Central DHW System Distribution Type - Reference information from CF1R.

14 Dwelling Unit DHW System Distribution Type - Reference information from CF1R.

D. Installed Water Heater Manufacturer Information

This table reports the manufacturer information of the installed water heater(s). Require one line for each installed water heater.

01 Water Heating System ID or Name – Reference information from CF1R.

02 Manufacturer – User input. Enter the name of the water heater manufacturer.

03 Model Number – User input. Enter the model number of the water heater.

E. Mandatory Measures for All Domestic Hot Water Distribution Systems

This table lists the requirements for all central recirculation systems. HERS rater must ensure all the requirements in this table are met.

F. HERS-Verified Pipe Insulation Credit Requirements

This table only applies to systems indicated in B14 and C14 as HERS-Verified Pipe Insulation Credit. In addition to the mandatory requirements in Table E, the HERS rater must ensure the requirements in this table are met.

G. HERS-Verified Parallel Piping Requirements

This table only applies to systems indicated in B14 and C14 as HERS-Verified Parallel Piping. In addition to the mandatory requirements in Table E, the HERS rater must ensure the requirements in this table are met.

H. HERS-Verified Compact Hot Water Distribution System Requirements

This table only applies to systems indicated in B14 and C14 as HERS-Verified Compact Hot Water Distribution System. In additional the mandatory requirements in Table E, the HERS rater must ensure the distance between the water heater to furthest point of water use does not exceed the maximum indicated in Table H1 below. Calculated the Floor Area Served by dividing the conditioned floor area by the number of installed water heaters (Floor Area Served= CFA/# of WH).  In addition all hot water lines shall be insulated.

| TABLE H1 Compact Hot Water Distribution System-(CHWDS) |  |
| --- | --- |
| Floor Area Served (ft2) | Maximum Measured Water Heater To Use Point Distance (ft) |
| < 1000 | 28 |
| 1001 – 1600 | 43 |
| 1601 – 2200 | 53 |
| 2201 – 2800 | 62 |
| >2800 | 68 |

I. HERS-Verified Demand Recirculation Manual Control Requirements

This table only applies to systems indicated in B14 and C14 as HERS-Verified Demand Recirculation Manual Control. In addition to the mandatory requirements in Table E, the HERS rater must ensure the requirements in this table are met.

J. HERS-Verified Demand Recirculation Sensor Control Requirements

This table only applies to systems indicated in B14 and C14 as HERS-Verified Demand Recirculation Sensor Control. In addition to the mandatory requirements in Table E, the HERS rater must ensure the requirements in this table are met.

| A. General Information |  |  |
| --- | --- | --- |
| 01 | Dwelling Unit Name | <<reference Dwelling Unit Name from CF1R>> |

| B. Design HERS Verified Dwelling Unit Water Heating Systems Information This table reports the water heating system features that were specified on the registered CF1R compliance document for this project. <<require one row of data for each Dwelling Unit Water Heating System identified on the CF1R report systems that has a Dwelling Unit DHW System Distribution types identified in the following list: HERS-Verified Pipe Insulation Credit, or HERS-Verified Parallel Piping, or HERS-Verified Compact Hot Water Distribution System, or HERS-Verified Point of Use, or HERS-Verified Demand Recirculation Manual Control, or HERS-Verified Demand Recirculation Sensor Control>> |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |
| <<reference values from CF1R (see rule in header)>> | <<reference values from CF1R allowed values= DHW, Combined Hydronic, >> | <<reference values from CF1R Allowed values = Large Storage, Small Storage, Heat Pump, Boiler, Large Instantaneous, Small Instantaneous or Indirect >> | <<reference values from CF1R >> | <<reference values from CF1R N/A is allowed only if Water Heater Type = Small Instantaneous or Large Instantaneous >> | <<reference values from CF1R. Allowed values are Natural Gas, Propane, Oil, or Electricity>> | <<if B03 = Heat Pump, then result = NA; Else reference values from CF1R. Allowed values: If Fuel Type B06 = Natural Gas, Propane, Oil then Rated Input Type = Btu/Hr. Else if Fuel Type = Electricity then Rated Input = kW >> | <<if B03 = Heat Pump, then result = NA; Else reference values from CF1R > | <<reference values from CF1R. Allowed values are *Energy Factor, *AFUE *Thermal Efficiency *Uniform Energy Factor>> | <<reference values from CF1R >> | <<reference values from CF1R Values = N/A if water heater type = Small Storage, Heat Pump, Boiler, Large Instantaneous, Small Instantaneous or indirect >> | <<reference values from CF1R Values = N/A if water heater type = Large Storage, Small Storage, Heat Pump, Boiler, Large Instantaneous, or Small Instantaneous >> | <<reference values from CF1R. Allowed values are *N/A *Multi-family: Recirculating with temperature modulation; *Multi-family: Recirculating with temperature modulation and monitoring; *Multi-family: Recirculating demand control; *Multi-family: Recirculating with no control (continuous pumping); *Multi-family: No loops or recirc pump>> | <<reference values from CF1R If B13 = N/A then allowed values are * HERS-Verified Pipe Insulation Credit * HERS-Verified Parallel Piping * HERS-Verified Compact Hot Water Distribution System * HERS-Verified Demand Recirculation Manual Control * HERS-Verified Demand Recirculation Sensor Control If B13 ≠ N/A then allowed values are * HERS-Verified Pipe Insulation Credit >> |

| C. Installed HERS Verified Dwelling Unit Water Heating Systems Information <<require one row of data for each Water Heating System in Section B>> |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 |  | 02 | 03 | 04 | 05 |  | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 |
| Water Heating System ID or Name |  | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) |  | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |
| <<reference value from B01>> |  | <<reference value from B02>> | <<reference value from B03>> | <<reference value from B04>> | <<user enter number xx.x. Value may be N/A if CF1R value is N/A >> |  | <<reference value from B06>> | <<if C03 = Heat Pump, then result = NA; Else reference value from B07>> | <<User input value which must pass the following range tests: If C06 = Natural Gas or Propane, then If C03 = Large Storage, then value must be > 75,000 Btu/hr; If C03 = Small Storage, then value must be ≤ 75,000 Btu/hr; If C03 = Large Instant, then value must be > 200,000 Btu/hr; Else if C03 = Small Instant, then value must be ≤ 200,000 Btu/hr; Else if C06 = Oil, then If C03 = Large Storage, then value must be > 105,000 Btu/hr; If C03 = Small Storage, then value must be ≤ 105,000 Btu/hr; If C03 = Large Instant, then value must be > 210,000 Btu/hr; Else if C03 = Small Instant, then value must be ≤ 210,000 Btu/hr; Else if C06 = Electricity, then If C03 = Large Storage or Large Instant, then value must be > 12 kW; Else if C03 = Small Storage or Small Instant, then value must be ≤ 12 kW; End if Last range check: If B08 ≠ NA, then value must be +/-10% of the reported value in B08. If the value passes all range tests, it is stored in WaterHeaterElectricFiredRatedInput, if C06 = Electricity. Otherwise the value is stored in WaterHeaterGasFiredRatedInput>> | <<reference value from B09>> | <<User input, value >> | <<User input, value Values = N/A if water heater type = Small Storage, Heat Pump, Boiler, Large Instantaneous, Small Instantaneous or indirect >> | <<User input, value values from CF1R Values = N/A if water heater type = Large Storage, Small Storage, Heat Pump, Boiler, Large Instantaneous, or Small Instantaneous >> | <<referenced from B13>> | <<referenced from B14>> |
| 15 | Compliance Statement |  |  |  |  | <<calculated field: If C08 ≤B08, and C10 ≥ value in B10, and C11 ≤ value in B11, and C12 ≥ value in B12, then display result = System complies; else display result = system does not comply>> |  |  |  |  |  |  |  |  |  |

| D. Installed Water Heater Manufacturer Information << require one row of data in this table for each of the Water Heaters listed in Section A04>> |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Manufacturer | Model Number |
| <<reference value from B01>> | <<User input>> | <<User input>> |

| E. Mandatory Measures for All Domestic Hot Water Distribution Systems |  |  |
| --- | --- | --- |
| 01 | The following pipes are insulated, to the thicknesses required by Table 120.3A, except for those sections of pipe that are subject to one of the exceptions below: (RA4.4.1) - The first 5 feet (1.5 meters) of hot and cold water pipes from the storage tank. - All piping with a nominal diameter of 3/4 inch (19 millimeter) or larger. - All piping associated with a domestic hot water recirculation system regardless of the pipe diameter, except when cold water return is used in a demand system. - Piping from the heating source to storage tank or between tanks. - Piping buried below grade. - All hot water pipes from the heating source to the kitchen fixtures. The following sections of pipe do not have to be insulated: (RA4.4.1) - Piping installed in interior or exterior walls that is surrounded on all sides by at least 1 inch of insulation. - Piping installed in attics with a minimum of 4 inches (10 cm) of attic insulation on top - Piping that penetrates framing members shall not be required to have pipe insulation for the distance of the framing penetration. Metal piping that penetrates metal framing shall use grommets, plugs, wrapping or other insulating material to assure that no contact is made with the metal framing. Insulation shall butt securely against all framing members. |  |
| 02 | Piping buried below grade must be installed in a water proof and non-crushable casing or sleeve that allows for installation, removal, and replacement of the enclosed pipe and insulation. (Section 150.0(j)) |  |
| 03 | All elbows and tees shall be fully insulated. (RA4.4.1) |  |
| 04 | Where insulation is required, no piping shall be visible due to insulation voids, and all insulation shall fit tightly to the pipe. (RA4.4.1) |  |
| 05 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 06 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| F. HERS-Verified Pipe Insulation Credit Requirements Systems that utilize this distribution type shall comply with these requirements <<If there are no systems in column B14 that have a value = “HERS-Verified Pipe Insulation Credit”, then display the "section does not apply" message; else display this entire table >> |  |  |
| --- | --- | --- |
| 01 | All hot water piping shall comply with the insulation requirements in Table 120.3-A. (RA 4.4.14) |  |
| 02 | Verification Status: | <<user pick from list: *** Pass - all applicable requirements are met; or *** Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or *** All n/a - This entire table is not applicable |
| 03 | Correction Notes: <<if Verification Status= Fail, then text entry in this Corrections Notes field is required; user input text>> |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| G. HERS-Verified Parallel Piping Requirements Systems that utilize this distribution type shall comply with these requirements << If there are no systems in column B14 that have a value = “HERS-Verified Parallel Piping”, then display the "section does not apply" message; else display this entire table >> |  |  |
| --- | --- | --- |
| 01 | Each central manifold has 5 feet or less of pipe between manifold and water heater. (RA 4.4.15) |  |
| 02 | For manifolds that include valves, the manifold must be readily accessible in accordance with the plumbing code. (RA 4.4.4) |  |
| 03 | Hot water distribution system piping from the manifold to the fixtures and appliances must take the most direct path. For example, piping from a second story manifold cannot supply the first floor. (RA 4.4.4) |  |
| 04 | The hot water distribution piping must be separated by at least 2 inches from any other hot water supply piping, and at least 6 inches from any cold water supply piping. Alternatively, the hot water supply piping must be insulated to the thicknesses shown in TABLE 120.3-A. (RA 4.4.4) |  |
| 05 | Verification Status: | <<user pick from list: *** Pass - all applicable requirements are met; or *** Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or *** All n/a - This entire table is not applicable |
| 06 | Correction Notes: <<if Verification Status= Fail, then text entry in this Corrections Notes field is required; user input text>> |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| H. HERS-Verified Compact Hot Water Distribution System Requirements Systems that utilize this distribution type shall comply with these requirements << If there are no systems in column B14 that have a value = “HERS-Verified Compact Hot Water Distribution System”, then display the "section does not apply" message; else display this entire table >> |  |  |  |
| --- | --- | --- | --- |
| 01 | Total Conditioned Floor Area (ft2) |  | <<numeric (data from CF1R)>> |
| 02 | Maximum allowed pipe run length from the water heater to the furthest point of use For the floor area served (feet). |  | << Floor Area Served = Total Conditioned Floor Area/Number of Water Heating Systems (H01/B04). Then display Maximum Measured Water Heater To Use Point Distance based on Floor Area Served using the following table H1. TABLE H1 should be invisible to users. TABLE H1 Compact Hot Water Distribution System. Floor Area Served (square feet); Maximum Measured Water Heater To Use Point Distance (feet). < 1000; 28. 1001 – 1600; 43. 1601 – 2200; 53. 2201 – 2800; 62. >2800; 68. >> |
| 03 | The pipe run length from each water heater to the furthest fitting served by that water heater must be no greater than the maximum pipe run length above. |  |  |
| 04 | Verification Status: | <<user pick from list: *** Pass - all applicable requirements are met; or *** Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or *** All n/a - This entire table is not applicable |  |
| 05 | Correction Notes: <<if Verification Status= Fail, then text entry in this Corrections Notes field is required; user input text>> |  |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |  |

| I. HERS-Verified Demand Recirculation Manual Control Requirements Systems that utilize this distribution type shall comply with these requirements << If there are no systems in column B14 that have a value = “HERS-Verified Demand Recirculation Manual Control”, then display the "section does not apply" message; else display this entire table >> |  |  |
| --- | --- | --- |
| 01 | The system operates “on-demand”, meaning that the pump begins to operate shortly before or immediately after hot water draw begins, and stops when the return water temperature reaches a certain threshold value. (RA4.4.9/RA4.4.13) |  |
| 02 | After the pump has been activated, the controls shall allow the pump to operate until the water temperature at the thermo-sensor rises to one of the following values: (RA4.4.9(f)/RA4.4.13(d)) - Not more than 10°F ( 5.6°C) above the initial temperature of the water in the pipe - Not more than 102°F (38.9°C). |  |
| 03 | The controls shall limit pump operation to a maximum of 5 minutes for single dwellings, and 10 minutes for multiple dwellings, following any activation. This is provided in the event that the normal means of shutting off the pump have failed. (RA4.4.9(f)3/RA4.4.13(d)3) |  |
| 04 | Pump and control placement shall meet one of the following criteria: (RA4.4.9(d)/RA4.4.13(b)) - When a dedicated return line has been installed the pump, controls and thermo-sensor are installed at the end of the supply portion of the recirculation loop; or - The pump and controls are installed on the dedicated return line near the water heater and the thermo-sensor is installed in an accessible location as close to the end of the supply portion of the recirculation loop as possible, or - When the cold water line is used as the return, the pump, demand controls and thermo-sensor shall be installed in an accessible location at the end of supply portion of the hot water distribution line (typically under a sink). |  |
| 05 | Insulation is not required on the cold water line when it is used as the return. (RA4.4.9(e)/RA4.4.13(c)) |  |
| 06 | Each control shall have standby power of 1 Watt or less. Controls may be located in individual units or on the loop. Controls may be activated by wired or wireless mechanisms, including buttons, motion sensors, door switches and flow switches. (RA4.4.9(c)/RA4.4.13(a)) |  |
| 07 | If more than one loop installed each loop shall have its own pump and controls. |  |
| 08 | Automatic air release valve is installed on the inlet side of the recirculation pump per Section 110.3(c)5A. |  |
| 09 | A check valve, or similar device, is located between the recirculation pump and the water heater per Section 110.3(c)5B. |  |
| 10 | Hose bibb is installed between the pump and the water heating equipment with an isolation valve between the hose bibb and the water heating equipment per Section 110.3(c)5C. |  |
| 11 | Isolation valves are installed on both sides of the pump. One of the isolation valves may be the same isolation valve as in item 10 above per Section 110.3(c)5D. |  |
| 12 | The cold water supply piping and the recirculation loop piping is not connected to the hot water storage tank drain port per Section 110.3(c)5E. |  |
| 13 | A check valve is installed on the cold water supply line between the hot water system and the next closest tee on the cold water supply line per Section 110.3(c)5F. |  |
| 14 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 15 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| J. HERS-Verified Demand Recirculation Sensor Control Requirements Systems that utilize this distribution type shall comply with these requirements << If there are no systems in column B14 that have a value = “HERS-Verified Demand Recirculation Sensor Control”, then display the "section does not apply" message; else display this entire table >> |  |  |
| --- | --- | --- |
| 01 | The system operates “on-demand”, meaning that the pump begins to operate shortly before or immediately after hot water draw begins, and stops when the return water temperature reaches a certain threshold value. (RA4.4.10/RA4.4.13) |  |
| 02 | After the pump has been activated, the controls shall allow the pump to operate until the water temperature at the thermo-sensor rises to one of the following values: (RA4.4.10(f)/RA4.4.13(d)) - Not more than 10°F ( 5.6°C) above the initial temperature of the water in the pipe - Not more than 102°F (38.9°C). |  |
| 03 | The controls shall limit pump operation to a maximum of 5 minutes for single dwellings, and 10 minutes for multiple dwellings, following any activation. This is provided in the event that the normal means of shutting off the pump have failed. (RA4.4.10(f)3/RA4.4.13(d)3) |  |
| 04 | Pump and control placement shall meet one of the following criteria: (RA4.4.10(d)/RA4.4.13(b)) - When a dedicated return line has been installed the pump, controls and thermo-sensor are installed at the end of the supply portion of the recirculation loop; or - The pump and controls are installed on the dedicated return line near the water heater and the thermo-sensor is installed in an accessible location as close to the end of the supply portion of the recirculation loop as possible, or - When the cold water line is used as the return, the pump, demand controls and thermo-sensor shall be installed in an accessible location at the end of supply portion of the hot water distribution line (typically under a sink). |  |
| 05 | Insulation is not required on the cold water line when it is used as the return. (RA4.4.10(e)/RA4.4.13(c)) |  |
| 06 | Each control shall have standby power of 1 Watt or less. Controls may be located in individual units or on the loop. Controls may be activated by wired or wireless mechanisms, including buttons, motion sensors, door switches and flow switches. (RA4.4.10(c)/RA4.4.13(a)) |  |
| 07 | If more than one loop installed each loop shall have its own pump and controls |  |
| 08 | Automatic air release valve is installed on the inlet side of the recirculation pump per Section 110.3(c)5A. |  |
| 09 | A check valve, or similar device, is located between the recirculation pump and the water heater per Section 110.3(c)5B. |  |
| 10 | Hose bibb is installed between the pump and the water heating equipment with an isolation valve between the hose bibb and the water heating equipment per Section 110.3(c)5C. |  |
| 11 | Isolation valves are installed on both sides of the pump. One of the isolation valves may be the same isolation valve as in item 10 above per Section 110.3(c)5D. |  |
| 12 | The cold water supply piping and the recirculation loop piping is not connected to the hot water storage tank drain port per Section 110.3(c)5E. |  |
| 13 | A check valve is installed on the cold water supply line between the hot water system and the next closest tee on the cold water supply line per Section 110.3(c)5F. |  |
| 14 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 15 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| # K. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 | << If C15 result = System Complies, and results for all applicable sections E, F, G, H, I, J, K do not = fail, then display: Complies: All specified verification protocol requirements on this document are met; else display: Does not comply: One or more specified verification protocol requirements on this document are not met.>> |