| Project Name and Address | Authority Having Jurisdiction |
| --- | --- |
| Name: Project Name | Enforcement Agency: Agency |
| Address: Project Address | Permit Number: Permit # |
| City, Zip: City, Zip Code | Permit Iss. Date: Date |

| Building: Enter Value | Floor: Enter Value | Room: Enter Value | Control: Enter Value |
| --- | --- | --- | --- |

| Construction Inspection and Functional Testing Comply Does not comply | Date Submitted to AHJ: Date |
| --- | --- |

| Intent: | This acceptance test is intended for Thermal Energy Storage (TES) Systems that are used in conjunction with chilled water air conditioning systems as limited under Eligibility Criteria in Table A-2. Submit one Certificate of Acceptance for each system that must demonstrate compliance. References: §120.5(a)15, §160.3(d)1N, and NA7.5.14. |
| --- | --- |

Table A-1. Construction Inspection
Prior to functional testing, verify access to the following documentation

| Step | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail | Designs, plans, schematics, and schedules as approved by the authority have jurisdiction. | §10-103(a) |
| 2 | Pass Fail | Using a California Energy Commission approved compliance software; software inputs and output results for the TES system as approved by the authority having jurisdiction. | NA7.5.14.1 |
| 3 | Pass Fail | Manufacturer specifications or tear sheets for the installed TES system as available. | NA7.5.14.1 |

Table A-2: Construction Inspection

Verify system eligibility (check one)

| Step | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1 |  | Chilled Water Storage | NA7.5.14.1(a) |
| 2 |  | Ice-on-Coil Internal Melt | NA7.5.14.1(b) |
| 3 |  | Ice-on-Coil External Melt | NA7.5.14.1(c) |
| 4 |  | Ice Harvester | NA7.5.14.1(d) |
| 5 |  | Brine | NA7.5.14.1(e) |
| 6 |  | Ice-Slurry | NA7.5.14.1(f) |
| 7 |  | Eutectic Salt | NA7.5.14.1(g) |
| 8 |  | Clathrate Hydrate Slurry (CHS) | NA7.5.14.1(h) |
| 9 |  | Cryogenic | NA7.5.14.1(i) |
| 10 |  | Encapsulated (e.g. Ice Balls) | NA7.5.14.1(j) |

Table A-3: Construction Inspection

Compare the installed unit to the documentation from Table A-1, Step 2 (Check all of the following)

| Step | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1 | No Entry | TES System Chiller | NA7.5.14.1 |
| 1.1 | Pass Fail | Brand and Model | NA7.5.14.1(k) |
| 1.2 | Pass Fail | Type (Centrifugal, Reciprocating, Other) | NA7.5.14.1(l) |
| 1.3 | Pass Fail | Heat Rejection Type (Air, Water, Other) | NA7.5.14.1(m) |
| 1.4 | Pass Fail | Charge Mode Capacity (Tons) | NA7.5.14.1(n) |
| 1.5 | Pass Fail | Discharge Mode Capacity (Tons) | NA7.5.14.1(o) |
| 1.6 | Pass Fail | Discharge Mode Efficiency (kW/Ton or EER) | NA7.5.14.1(p) |
| 1.7 | Pass Fail | Charge Mode Efficiency (kW/Ton or EER) | NA7.5.14.1(q) |
| 1.8 | Pass Fail | Fluid Type and Percentage | NA7.5.14.1(r) |
| 2 | No Entry | TES System Storage | NA7.5.14.1 |
| 2.1 | Pass Fail | Brand and Model | NA7.5.14.1(s) |
| 2.2 | Pass Fail | Number of Tanks | NA7.5.14.1(t) |
| 2.3 | Pass Fail | Storage Capacity per Tank (ton-hours) | NA7.5.14.1(u) |
| 2.4 | Pass Fail | Storage Rate (tons) | NA7.5.14.1(v) |
| 2.5 | Pass Fail | Minimum Charging Temperature | NA7.5.14.1(w) |
| 2.6 | Pass Fail | Discharge Rate (tons) | NA7.5.14.1(x) |
| 3 | Pass Fail | Indicate that the Construction Inspection complies with ALL requirements. | NA |

Table B: Functional Testing

| Step | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail | Chiller(s) start-up procedure has been completed. | NA7.5.14.2 (Part 1)(a) |
| 2 | Pass Fail | System fluid test and balance has been completed. | NA7.5.14.2 (Part 1)(b) |
| 3 | Pass Fail | Air separation and purge has been completed. | NA7.5.14.2 (Part 1)(c) |
| 4 | Pass Fail | Fluid (e.g. glycol has been verified at the concentration and type indicated on the design documents. | NA7.5.14.2 (Part 1)(d) |
| 5 | Pass Fail | The TES system has been fully charged at least once and the charge duration noted. | NA7.5.14.2 (Part 1)(e) |
| 6 | Pass Fail | The system has been partially discharged at least once and the discharge duration noted. | NA7.5.14.2 (Part 1)(f) |
| 7 | Pass Fail | The system is in a partial charge state in preparation for step 2 tests. | NA7.5.14.2 (Part 1)(g) |
| 8 | Pass Fail | The schedule of operation has been activated as designed. | NA7.5.14.2 (Part 1)(h) |
| 9 | Pass Fail | Mode documentation describes the state of system components in each mode of operation. | NA7.5.14.2 (Part 1)(i) |
| 10 | Pass Fail | Verify that the TES system and the chilled water plant is controlled and monitored by an energy management system (EMS). | NA7.5.14.2 (Part 2)(a) |
| 11 | M E | Indicate one of the following methods of simulation that will be used during the test. Manual selection (M) or use of an EMS by inputting the schedule as indicated by the designer or manufacturer (E). | NA7.5.14.2 (Part 2)(b) |
| 12 | Pass Fail | Storage/charge mode. Verify that TES system stores energy. | NA7.5.14.2 (Part 2)(c) |
| 13 | Pass Fail | End of charge signal. Simulate a full storage charge by changing the (manufacturer recommended) thermal storage end of charge output sensor to the EMS. Verify that the storage charging has stopped. | NA7.5.14.2 (Part 2)(d) |
| 14 | Pass Fail | Discharge mode. Generate a call for cooling. Verify that the storage starts discharging with the compressors off. Return to the off/secured mode. | NA7.5.14.2 (Part 2)(e) |
| 15 | Pass Fail | Mechanical cooling only mode. Generate a call for cooling. Verify that the storage does not discharge and the cooling load is met by the compressor only. Return to the off/secure mode. | NA7.5.14.2 (Part 2)(f) |
| 16 | Pass Fail | Discharge and mechanical cooling mode. Generate a call for cooling. Verify that the TES system discharges with the compressor sharing the load. | NA7.5.14.2 (Part 2)(g) |
| 17 | Pass Fail | Off/storage-secured mode. Verify that the storage does not discharge and all compressors are off, regardless of the presence of calls for cooling. | NA7.5.14.2 (Part 2)(h) |
| 18 | Pass Fail | Charge plus cool mode. If provisions for this mode have been made by the system designer, then verify that the tank(s) can be charged while serving an active cooling load. Else verify that the energy storage is disallowed or discontinued while an active cooling load is present. | NA7.5.14.2 (Part 2)(i) |

| Declaration Statement | Signatory |
| --- | --- |
| Document Author I assert that this Certificate of Acceptance documentation is accurate and complete. | Name Company Name Author Signature Date Signed |
| Field Technician I certify the following under penalty of perjury, under the laws of the State of California: The information provided on this Certificate of Acceptance is true and correct. I am the person who performed the acceptance verification reported on this Certificate of Acceptance (Field Technician). The construction or installation identified on this Certificate of Acceptance complies with the applicable acceptance requirements indicated in the plans and specifications approved by the enforcement agency, and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and signed by the responsible builder/installer and has been posted or made available with the building permit(s) issued for the building. | Name Company Name ATT No.: ATT Cert. No. Title Phone Signature Date Signed |
| Responsible Person I certify the following under penalty of perjury, under the laws of the State of California: I am the Field Technician, or the Field Technician is acting on my behalf as my employee or my agent and I have reviewed the information provided on this Certificate of Acceptance. I am eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Acceptance and attest to the declarations in this statement (responsible acceptance person). The information provided on this Certificate of Acceptance substantiates that the construction or installation identified on this Certificate of Acceptance complies with the acceptance requirements indicated in the plans and specifications approved by the enforcement agency, and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and is posted or made available with the building permit(s) issued for the building. I will ensure that a completed, signed copy of this Certificate of Acceptance shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a signed copy of this Certificate of Acceptance is required to be included with the documentation the builder provides to the building owner at occupancy. | Name Company Name Lic. No.: License No. Title Phone Signature Date Signed |