| Project Name and Address | Authority Having Jurisdiction |
| --- | --- |
| Name: Project Name | Enforcement Agency: Agency |
| Address: Project Address | Permit Number: Permit # |
| City, Zip: City, Zip Code | Permit Iss. Date: Date |

| Building: Enter Value | Floor: Enter Value | Room: Enter Value | Control: Enter Value |
| --- | --- | --- | --- |

| Construction Inspection and Functional Testing Comply Does not comply | Date Submitted to AHJ: Date |
| --- | --- |

| Intent: | - This acceptance test is intended for multifamily dwelling units where CONTINUOUS ventilation is used. This acceptance test is not permitted for Central Fan Integration (CFI) systems or other intermittent ventilation systems. - Submit one Certificate of Acceptance for each ventilation system installed to verify conformance with the requirements of the Energy Standards §160.2(b)2, Nonresidential Reference Appendices NA7.18.1.1 and NA2.2, and California Energy Commission adopted version of ANSI/ASHRAE Standards 62.2-2019. - If using Supply-only or Exhaust-only ventilation, Certificate of Acceptance NRCA-MCH-21-H must be completed prior to beginning NRCA-MCH-20a-H. NOTE: An uncertified technician may complete this acceptance test using this form if a HERS Rater performs the required Verification or a certified ATT may perform this acceptance test with no HERS Rater Verification needed. |
| --- | --- |

Table A-1. Construction Documents and Inspection
Prior to functional testing, verify and document all of the following

| Step | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1.0 | Pass Fail | Design, drawings, and cut-sheets as approved by the authority having jurisdiction. | N/A |
| 2.0 | Pass Fail | NRCC-MCH-E, as approved by the authority having jurisdiction. | §10-103(a)2A |
| 3.0 | Pass Fail | NRCA-MCH-21-H, if using Supply-only or Exhaust-only ventilation. | N/A |
| 4.0 | Pass Fail | Verify that the system is connected and able to deliver outside air to the dwelling unit when the system is operating. | NA7.18.1.1.1(a) |
| 5.0 | B, S, E | Specify the ventilation system type as one of the following: B – Balanced S – Supply Only E – Exhaust Only | NA7.18.1.1.1(b) |
| 6.0 | Pass Fail | Verify that the installed ventilation system is a continuous ventilation system. | NA7.18.1.1.1(c) ASHRAE 62.2 §4.1 |
| 7.0 | C,O,V,X, N/A | If using multifamily building central ventilation systems to serve multiple dwelling units, specify the balancing system as one of the following: C – Constant Air Regulator O – Orifice Plate V – Variable Speed Central Plate or Fan X - Other N/A | NA7.18.1.1.1(c) §160.2(b)2Av |
| 8.0 | Pass Fail | Confirm the kitchen range hood is ventilated to the outside. | NA7.18.1.1.1(d) |
| 9.0 | Pass Fail | Verify that a manual ON/OFF switch associated with dwelling unit ventilation system is operational and labeled with the following or equivalent text: “This switch controls the indoor air quality ventilation for the home. Leave it on unless the outdoor air quality is very poor.” | §160.2(b)2Aix |
| 10.0 | Pass Fail | Verify that Table A-1 is completed as required | N/A |

Table A-2. Instrumentation Specific Requirements

| Step | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1.0 | Pass Fail | Verify that pressure measurement instrumentation is accurate to plus or minus 0.2 Pa or plus or minus 1% of the pressure reading. | NA 2.2.2.1 |
| 2.0 | Pass Fail | Verify that pressure measurement instrumentation includes a sensor plus data acquisition system. | NA 2.2.2.1 |
| 3.0 | Pass Fail | Verify that pressure measurement instrumentation makes use of a static pressure probe. | NA 2.2.2.1 |
| 4.0 | Pass Fail | Verify that ventilation system airflow rate measurement apparatus is listed on the Energy Commission website: Airflow Measurement Apparatus (ca.gov), https://www.energy.ca.gov/rules-and-regulations/building-energy-efficiency/manufacturer-certification-building-equipment-9 | NA 2.2.2.2 NA2.2.3 |
| 5.0 | Pass Fail | Verify that ventilation system airflow rate measurement apparatus is calibrated according to the manufacturer procedures. | NA 2.2.2.2 NA2.2.3 |
| 6.0 | Pass Fail | Verify that Table A-2 is completed as required | N/A |

Table A-3. Acceptance Test Compliance Documents s to be Completed

Consulting compliance document NRCC-MCH-E identify which of the following acceptance test compliance documents are to be completed.

| Step | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1.0 |  | NRCA-MCH-20b-H – Kitchen Range Hood | N/A |
| 2.0 |  | NRCA-MCH-20c-H – IAQ Ventilation System | N/A |
| 3.0 |  | NRCA-MCH-20d-H – HRV or ERV System | N/A |

| Declaration Statement | Signatory |
| --- | --- |
| Document Author I assert that this Certificate of Acceptance documentation is accurate and complete. | Name Company Name Author Signature Date Signed |
| Field Technician I certify the following under penalty of perjury, under the laws of the State of California: The information provided on this Certificate of Acceptance is true and correct. I am the person who performed the acceptance verification reported on this Certificate of Acceptance (Field Technician). The construction or installation identified on this Certificate of Acceptance complies with the applicable acceptance requirements indicated in the plans and specifications approved by the enforcement agency, and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and signed by the responsible builder/installer and has been posted or made available with the building permit(s) issued for the building. | Name Company Name ATT No.: ATT Cert. No. Title Phone Signature Date Signed |
| Responsible Person I certify the following under penalty of perjury, under the laws of the State of California: I am the Field Technician, or the Field Technician is acting on my behalf as my employee or my agent and I have reviewed the information provided on this Certificate of Acceptance. I am eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Acceptance and attest to the declarations in this statement (responsible acceptance person). The information provided on this Certificate of Acceptance substantiates that the construction or installation identified on this Certificate of Acceptance complies with the acceptance requirements indicated in the plans and specifications approved by the enforcement agency, and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and is posted or made available with the building permit(s) issued for the building. I will ensure that a completed, signed copy of this Certificate of Acceptance shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a signed copy of this Certificate of Acceptance is required to be included with the documentation the builder provides to the building owner at occupancy. | Name Company Name Lic. No.: License No. Title Phone Signature Date Signed |