| Project Name and Address | Authority Having Jurisdiction |
| --- | --- |
| Name: Project Name | Enforcement Agency: Enforcement Agency |
| Address: Project Address | Permit Number: Permit Number |
| City, Zip Code: City, Zip Code | Permit Issue Date: Permit Issue Date |

| Building: Enter Value | Floor: Enter Value | Room: Enter Value | Control: Enter Value |
| --- | --- | --- | --- |

| Construction inspection and functional testing comply Does not comply | Date Submitted to AHJ: Date |
| --- | --- |

| Intent: | The document is used to demonstrate compliance with acceptance requirements §140.9(c)3 and Reference Nonresidential Appendix NA7.16 |
| --- | --- |

Table A-1. Construction Inspection

Wind Speed/Direction Control

| STEP | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail | Anemometer sensor factory calibration certificate is valid or recalibrated within manufacturer’s recommendations or no more than 5 years. | NA7.16.1 §140.9(c)3Ciii |
| 2 | Pass Fail | Sensor located at a height outside the wake region of nearby structures and experiences similar wind conditions to the free stream environment above the exhaust stacks | NA7.16.1(b) §140.9(c)3ci |
| 3 | Pass Fail | Sensor installed in close proximity to the fan it controls so that it captures a representative wind speed/direction | NA7.16.1(c) §140.9(c)3Ci |
| 4 | Pass Fail | Sensor wired correctly to controls ensuring proper volume flow rate control | NA7.16.1(d) §140.9(c)3Civ |
| 5 | Pass Fail | Wind speed/direction look-up table establish and match dispersion analysis results | NA7.16.1(e) §140.9(c)3Cii |
| 6 | airflow static press speed/vol other: Enter Value | Verify methodology used to measure volume flow rate. Method used (airflow sensor, static pressure, fan speed to volume flow rate curve, specified-other): | NA7.16.1(f) |
| 7 | Pass Fail | Verify that the Construction Inspection complies with all requirements. | N/A |

Table B-1. Functional Testing

Wind Speed/Direction Control

| STEP | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1.1 |  | Simulate minimum look-up table wind speed by either covering the anemometer sensor or overriding the curve points so that the current wind speed is below the speed correlating to the minimum volume flow rate at the stack. | NA7.16.2 step 1 |
| 1.2 | Pass Fail | With all sensors active and reading below the minimum wind speed, verify that stack volume flow rate matches minimum flow rate from look-up table. | NA7.16.2 step 1(a), §140.9(c)3Cii |
| 1.3 |  | Restore all curve points. | NA7.16.2 step 1(b) |
| 2.1 |  | Simulate mid-range look-up table wind speed by either inducing a wind current, with an air speed accuracy of +/- 2%, or overriding the curve points so that the current wind speed correlates to a mid-range stack volume flow rate. | NA7.16.2 step 2, §140.9(c)3Cii |
| 2.2 | Pass Fail | With all sensors active and reading a mid-range wind speed, verify that the stack volume flow rate matches mid-range flow rate from corresponding wind speed in look-up table. | NA7.16.2 step 2(a), §140.9(c)3Cii |
| 2.3 |  | Restore all curve points. | NA7.16.2 step 2(b) |
| 3.1 | Pass Fail | Simulate maximum look-up table wind speed by either inducing a wind current, with an air speed accuracy of +/- 2%, or overriding the curve points so that the current wind speed correlates to the maximum stack volume flow rate at the stack. | NA7.16.2 step 3 |
| 3.2 |  | Verify that the stack volume flow rate matches maximum flow rate from look-up table. | NA7.16.2 step 3(a), §140.9(c)3Cii |
| 3.3 |  | Restore all curve points. | NA7.16.2 step 3(b) |
| 4.1 |  | Temporarily override the sensor calibration/replacement period to 5 minutes. Wait 5 minutes. | NA7.16.2 step 4, §140.9(c)3Civ |
| 4.2 | Pass Fail | Verify that the minimum stack volume flow rate is matches the flow rate corresponding to worst-case wind conditions documented in dispersion analysis and alarm is received by facility operators | NA7.16.2 step 4, §140.9(c)3Civ |
| 4.3 |  | Restore calibration/replacement period. | NA7.16.2 step 4 |
| 5.1 |  | Simulate sensor failure by disconnecting the anemometer. | NA7.16.2 step 5 |
| 5.2 | Pass Fail | Verify that the minimum stack volume flow rate matches the flow rate corresponding to worst-case wind conditions documented in dispersion analysis and alarm is received by facility operators | NA7.16.2 step 5, §140.9(c)3Civ |
| 5.3 |  | Reconnect sensor. | NA7.16.2 step 5 |
| 6 | Pass Fail | Verify that the Functional Test complies with all requirements. | N/A |

Table A-2. Construction Inspection

Contaminant Concentration Control Construction Inspection

| STEP | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail | Contaminant sensor factory calibration certificate is valid or recalibrated within manufacturer’s recommendations. | NA7.16.3(a), §140.9(c)3Dii |
| 2 | Pass Fail | Contaminant sensor located within each exhaust plenum | NA7.16.3(b), §140.9(c)3D |
| 3 | Pass Fail | Contaminant sensor wired correctly to controls ensuring proper volume flow rate control | NA7.16.3(c), §140.9.(c)3Di |
| 4 | Pass Fail | Contaminant concentration threshold established and matches dispersion analysis result | NA7.16.3(d), §140.9(c)3Di |
| 5 | Pass Fail | Verify methodology used to measure volume flow rate. Method used (airflow sensor, static pressure, fan speed to volume flow rate curve, specific-other) | NA7.16.3(e) |
| 6 | airflow static press speed/vol other: Enter Value | Verify methodology used to measure volume flow rate. Method used (airflow sensor, static pressure, fan speed to volume flow rate curve, specified-other): | NA7.16.3(e) |
| 7 | Pass Fail | If multiple sensors are present, fan control is based on highest concentration reading | NA7.16.3(f) |
| 8 | Pass Fail | Check if construction inspection complies with all requirements. | N/A |

Table B-2. Functional Testing

Contaminant Concentration Control Construction Inspection

| STEP | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail | Ensure that no contaminant event is active. Simulate a minimum exhaust air demand in all lab spaces. Verify that the stack volume flow rate is equal to or greater than corresponding non-event value. | NA7.16.4 step 1, §140.9(c)3Di |
| 2 | Pass Fail | Simulate a mid-range exhaust air demand in all lab spaces. Verify that the stack volume flow rate is greater than, or equal to the corresponding non-event value. | NA7.16.4 step 2, §140.9(c)3Di |
| 3.1 |  | Simulate a mid-range exhaust air demand in all lab spaces. | NA7.16.4 step 3 |
| 3.2 |  | Simulate a contamination event. | NA7.16.4 step 3 |
| 3.3 | Pass Fail | Verify that the volume flow rate at the stack is at or above the minimum event value. | NA7.16.4 step 3, §140.9(c)3Diii |
| 4 | Pass Fail | Increase exhaust air demand at the lab spaces. Verify the stack volume flow rate is at or above the minimum value. | NA7.16.4 step 4 |
| 5.1 |  | Temporarily override the sensor calibration/ replacement period to 5 minutes. | NA7.16.4 step 5 |
| 5.2 |  | Wait 5 minutes. | NA7.16.4 step 5 |
| 5.3 | Pass Fail | Restore calibration/replacement period. | NA7.16.4 step 5 |
| 6.1 | Pass Fail | Simulate sensor failure by disconnecting the sensor. Verify that the volume flow rate is at or above the required for a contaminant event or greater and that an alarm is received by the facility operators. | NA7.16.4 step 6, §140.9(c)3Diii |
| 6.2 |  | Reconnect sensor | NA7.16.4 step 6 |
| 7 | Pass Fail | Verify that the Functional Test complies with all requirements. | N/A |

|  | Signatory |
| --- | --- |
| Document Author I assert that this Certificate of Acceptance documentation is accurate and complete. | Name Company Name Author Signature Date Signed |
| Field Technician I certify the following under penalty of perjury, under the laws of the State of California: The information provided on this Certificate of Acceptance is true and correct. I am the person who performed the acceptance verification reported on this Certificate of Acceptance (Field Technician). The construction or installation identified on this Certificate of Acceptance complies with the applicable acceptance requirements indicated in the plans and specifications approved by the enforcement agency, and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and signed by the responsible builder/installer and has been posted or made available with the building permit(s) issued for the building. | Name Company Name ATT No.: ATT Cert. No. Title Phone Signature Date Signed |
| Responsible Person I certify the following under penalty of perjury, under the laws of the State of California: I am the Field Technician, or the Field Technician is acting on my behalf as my employee or my agent and I have reviewed the information provided on this Certificate of Acceptance. I am eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Acceptance and attest to the declarations in this statement (responsible acceptance person). The information provided on this Certificate of Acceptance substantiates that the construction or installation identified on this Certificate of Acceptance complies with the acceptance requirements indicated in the plans and specifications approved by the enforcement agency, and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and is posted or made available with the building permit(s) issued for the building. I will ensure that a completed, signed copy of this Certificate of Acceptance shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a signed copy of this Certificate of Acceptance is required to be included with the documentation the builder provides to the building owner at occupancy. | Name Company Name Lic. No.: License No. Title Phone Signature Date Signed |