CERTIFICATE OF VERIFICATION
Note: This table completed by HERS Registry.

| Project Name: | Enforcement Agency: |
| --- | --- |
| Dwelling Address: | Permit Number: |
| City and Zip Code: | Permit Application Date: |

| A. Enclosure Air Leakage – General Information |  |  |
| --- | --- | --- |
| 01 | Is HERS verification of building enclosure air leakage to outside required by CF1R? |  |
| 02 | Target Enclosure Air Leakage from CF1R (CFM50) |  |
| 03 | Indoor temperature during test (degrees Fahrenheit (°F)) |  |
| 04 | Outdoor temperature during test (degrees Fahrenheit (°F)) |  |
| 05 | Blower Door Location |  |
| 06 | Building Elevation Above Sea Level (ft) |  |
| 07 | Date of the Diagnostic Test for this Dwelling |  |
| 08 | Test Procedure used |  |
|  | this field not visible on completed document, used only to determine the variant for completion of the document. |  |

| B. Diagnostic Equipment Information |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | Number of Manometers Used to Measure Home Pressurization |  |  |  |  |  |  |  |  |
| 02 |  | 03 |  | 04 |  |  | 05 |  | 06 |
| Manometer Make |  | Manometer Model |  | Manometer Serial Number |  |  | Manometer Calibration Date |  | Manometer Calibration Status |
| 07 | Number of Fans Used to Pressurize Home |  |  |  |  |  |  |  |  |
| 08 |  |  | 09 |  | 10 |  |  | 11 |  |
| Fan Make |  |  | Fan Model |  | Fan Serial Number |  |  | Fan Configuration (rings) |  |

ENV20b - Single Point Air Tightness Test With Automatic Meter

| C. Enclosure Air Leakage Diagnostic Test |  |  |
| --- | --- | --- |
| 01 | Time Average Period of Meter (seconds) |  |
| 02 | Test Methodology |  |
| 03 | Pre-Test Baseline Enclosure Pressure (Pa) (May be positive or negative) |  |
| 04 | Induced Enclosure Pressure from Manometer (Pa) Goal = 50 ± 3 (Pressurization is positive; Depressurization is negative) |  |
| 05 | Induced Enclosure Pressure Check |  |
| 06 | Nominal CFM50 |  |

| D. Altitude and Temperature Correction |  |  |
| --- | --- | --- |
| 01 | Altitude and Temperature Correction Factor |  |
| 02 | Corrected CFM50 |  |

| E. Accuracy Adjustment |  |  |
| --- | --- | --- |
| 01 | Adjusted CFM50 (measured air leakage rate) |  |

| F. Compliance Statement |  |
| --- | --- |
| 01 |  |

| G. Additional Requirements for Compliance |  |  |
| --- | --- | --- |
| 01 | The procedure for preparing the enclosure for testing is detailed in RESNET 380-2019 Section 3.2. |  |
| 02 | The procedure for installation of the test apparatus, and preparations for measurement shall conform to RESNET 380-2019 Section 3.3 |  |
| 03 | The procedure for the conduct of the enclosure air leakage test shall conform to the One-Point Airtightness Test specified in RESNET 380-2019 Section 3.4.1 |  |
| 04 | Verification Status: | - Pass - all applicable requirements are met; or - Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or - All N/A - This entire table is not applicable |
| 05 | Correction Notes: |  |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| H. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Verification documentation is accurate and complete. |  |  |  |
| Documentation Author Name: | Documentation Author Signature: |  |  |
| Company: | Date Signed: |  |  |
| Address: | CEA/HERS Certification Information (if applicable): |  |  |
| City/State/Zip: | Phone: |  |  |
| Responsible Person's Declaration statement |  |  |  |
| I certify the following under penalty of perjury, under the laws of the State of California: - The information provided on this Certificate of Verification is true and correct. - I am the certified HERS Rater who performed the verification identified and reported on this Certificate of Verification (responsible rater). - The installed features, materials, components, manufactured devices, or system performance diagnostic results that require HERS verification identified on this Certificate of Verification comply with the applicable requirements in Reference Appendices RA2, RA3, and the requirements specified on the Certificate of Compliance for the building approved by the enforcement agency. - The information reported on applicable sections of the Certificate(s) of Installation (CF2R) signed and submitted by the person(s) responsible for the construction or installation conforms to the requirements specified on the Certificate(s) of Compliance (CF1R) approved by the enforcement agency. - I understand that a registered copy of this Certificate of Verification shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections, and I will take the necessary steps to ensure this requirement is accomplished. - I understand that a registered copy of this Certificate of Verification is required to be included with the documentation the builder provides to the building owner at occupancy, and I will take the necessary steps to ensure this requirement is accomplished. |  |  |  |
| BUILDER OR INSTALLER INFORMATION AS SHOWN ON THE CERTIFICATE OF INSTALLATION |  |  |  |
| Company Name (Installing Subcontractor, General Contractor, or Builder/Owner): |  |  |  |
| Responsible Builder or Installer Name: |  | CSLB License: |  |
| HERS PROVIDER DATA REGISTRY INFORMATION |  |  |  |
| Sample Group Number (if applicable): |  |  | Dwelling Test Status in Sample Group (if applicable): |
| HERS RATER INFORMATION |  |  |  |
| HERS Rater Company Name: |  |  |  |
| Responsible Rater Name: |  |  | Responsible Rater Signature: |
| Responsible Rater Certification Number w/ this HERS Provider: |  |  | Date Signed: |

CF3R-ENV-20b-H User Instructions

Section A. Enclosure Air Leakage – General Information

- This field is automatically filled from the CF1R which determines if a CFM50 compliance target value is required.

- This field determines the CFM50 target enclosure air leakage from the CF1R if HERS verification of enclosure air leakage is required.

- Enter the indoor temperature measured at the time that the enclosure air leakage test was performed.

- Enter the outdoor temperature measured at the time that the enclosure air leakage test was performed.

- Provide a brief description of the location where the blower door was installed for the test. Examples: “front entry door on west side of house”, “door between house and garage”, “large window in family room”.

- Enter the building elevation above sea level. Use the value for the closest city found in Reference Appendices, Joint Appendix JA2.2.

- Enter the date that the enclosure air leakage test data was collected.

- Select the appropriate test procedure. This selection will determine which version of this document will be used (a or b). Not that newer manometers have automatic functions for compensating baseline (automatic baseline) and compensating for house pressures other than the target (50 Pa). It is preferable to use these when available.

Section B. Diagnostic Equipment Information

- Enter the number of manometers used to measure the enclosure pressurization. If more than one system is used, the fan flow numbers need to be manually added together, unless blower door software is used that will accommodate multiple fan systems running simultaneously.

- Enter the make (brand) of the manometer used to collect the enclosure air leakage data. Examples: Retrotec, Energy Conservatory.

- Enter the model of the manometer used to collect the enclosure air leakage data. Examples: DM-2 Mark II, DG700.

- Enter the serial number of the manometer used to collect the enclosure air leakage data.

- Enter the most recent date that the manometer was calibrated by following manufacturer’s calibration specifications.

- This field is automatically filled. If the calibration date was more than 12 months prior to the test date entered in Row A08 above, an error will appear.

- Enter the number of blower door fan systems required to run simultaneously to pressurize the enclosure for the enclosure air leakage test. If more than one system is used, the fan flow numbers need to be manually added together, unless blower door software is used that will accommodate multiple fan systems running simultaneously.

- Enter the make (brand) of the fan used to collect the enclosure air leakage data. Examples: Retrotec, Energy Conservatory.

- Enter the model of the fan used to collect the enclosure air leakage data. Examples: US1000, Q46, BD3, BD4.

- Enter the serial number of the fan used to collect the enclosure air leakage data.

- Enter the fan configuration shown on the meter. This is sometimes referred to as “range configuration”, “CONFIG” or “rings”. Examples: Open, A, B, C8.

Section C. Enclosure Air Leakage Test (ENV20b)

- Enter the time average period used on the manometer during the test. Must be at least 10 seconds.

- Select the type of test being performed: Pressurization (air blowing into house) or depressurization (air blowing out of house).

- Enter the pre-test baseline enclosure pressure. This is the reading on the automatic manometer with no fans turned on.

- Enter the induced enclosure pressure from the automatic manometer. The goal is to achieve 50 ± 3 Pa.

- This field is automatically calculated. This field determines if the pressure achieved is acceptable to proceed with the enclosure air leakage test.

- Enter the measured nominal CFM50  from the automatic manometer.

Section D. Altitude and Temperature Correction

- This field is automatically calculated. This factor is determined based on the altitude and temperature of the building location using equation 4 in Section 9 of ASTM E779-19.

- This field is automatically calculated. The corrected CFM50 is the nominal CFM50 from Section C multiplied by the altitude and temperature correction factor.

Section E. Accuracy Adjustment

- This field is automatically calculated. This value is determined from Equation 5a from ANSI/RESNET/ICC 380-2019.

Section F. Compliance Statement

- This field is automatically calculated. A check is performed to make sure that the meter has been properly calibrated and that the measured enclosure air leakage is less than the target enclosure air leakage.

Section G. Additional Requirements for Compliance

- This statement must be true (or not applicable) for the test to conform to the protocols.

- This statement must be true (or not applicable) for the test to conform to the protocols.

- This statement must be true (or not applicable) for the test to conform to the protocols.

| A. Enclosure Air Leakage – General Information |  |  |
| --- | --- | --- |
| 01 | Is HERS verification of building enclosure air leakage to outside required by CF1R? | <<calculated field: If CF1R requires HERS verification of building enclosure air leakage, then value = Required, else value = N/A>> |
| 02 | Target Enclosure Air Leakage from CF1R (CFM50) | <<if A01=required, then value = the CFM50 target value specified on the CF1R; else value = N/A>> |
| 03 | Indoor temperature during test (degrees Fahrenheit (°F)) | <<user input, numeric, x.x degF>> |
| 04 | Outdoor temperature during test (degrees Fahrenheit (°F)) | <<user input, numeric, x.x degF>> |
| 05 | Blower Door Location | <<user input, text, maximum 50 characters>> |
| 06 | Building Elevation Above Sea Level (feet (ft)) | <<user input, integer, xxxxx >> |
| 07 | Date of the Diagnostic Test for this Dwelling | <<user input: date (use date format validation control)>> |
| 08 | Test Procedure used | << user pick text value from following list of two: **Single-Point Test with Manual Meter **Single-Point Test with Automatic Meter>> |
|  | this field not visible on completed document, used only to determine the variant for completion of the document. | << if A08= Single-Point Test with Manual Meter, then use variant ENV-20a; Else if A15=Single-Point Test with Automatic Meter, then use variant ENV-20b>> |

| B. Diagnostic Equipment Information |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | Number of Manometers Used to Measure Home Pressurization |  |  |  |  | <<user input, integer>> For entries >1, duplicate lines B. 2-6 |  |  |  |
| 02 |  | 03 |  | 04 |  |  | 05 |  | 06 |
| Manometer Make |  | Manometer Model |  | Manometer Serial Number |  |  | Manometer Calibration Date |  | Manometer Calibration Status |
| <<user input, text, maximum 50 characters>> |  | <<user input, text, maximum 50 characters>> |  | <<user input, text, maximum 50 characters>> |  |  | <<user input, text (Date), maximum 50 characters>> |  | <<calculated field: if manometer Calibration Date in B05 is within 12 months of the date of the diagnostic test A. 8, then display message: Manometer Calibration is valid"; else display message: "WARNING - Manometer Calibration is expired. A manometer with current calibration is required in order to comply with this Enclosure Air Leakage Diagnostic test">> |
| 07 | Number of Fans Used to Pressurize Home |  |  |  | <<user input, integer>> For entries >1, duplicate lines B. 8-11 |  |  |  |  |
| 08 |  |  | 09 |  | 10 |  |  | 11 |  |
| Fan Make |  |  | Fan Model |  | Fan Serial Number |  |  | Fan Configuration (rings) |  |
| <<user input, text, maximum 50 characters>> |  |  | <<user input, text, maximum 50 characters>> |  | <<user input, text, maximum 50 characters>> |  |  | <<user input, text, maximum 50 characters>> |  |

ENV20b - Single Point Air Tightness Test With Automatic Meter

| C. Enclosure Air Leakage Diagnostic Test |  |  |
| --- | --- | --- |
| 01 | Time Average Period of Meter (seconds) | <<user enter integer ≥ 10>> |
| 02 | Test Methodology | <<user input, user pick one of the following 2 text values: **Pressurization; **Depressurization;>> |
| 03 | Pre-Test Baseline Enclosure Pressure (Pa) (May be positive or negative) | <<user enter numeric xx.x: -40 ≤value≥ 40>> |
| 04 | Induced Enclosure Pressure from Manometer (Pa) Goal = 50 ± 3 (Pressurization is positive; Depressurization is negative) | <<user enter numeric xx.x: -75.0 ≥ value ≤ 75>> |
| 05 | Induced Enclosure Pressure Check | <<calculated value, if absolute value (C04) ≥ 15 Pa, display text: “Induced pressure within range for single point test; else display text: “Induced pressure too low for single point test - Do Not Proceed”>> |
| 06 | Nominal CFM50 | <<user enter integer>> (Resolution of 1 CFM) |

| D. Altitude and Temperature Correction |  |  |
| --- | --- | --- |
| a1 | Outside Dynamic Viscosity of Air Correction **(this row is not visible to user) | <<if C02 = Depressurization, then value=2.629*10-3*[(A04+460)0.5]/[1+(198.7/(A05+460))]; else report “NA”>> |
| a2 | Indoor Dynamic Viscosity of Air Correction **(this row is not visible to user) | << if C02 = Pressurization, then value=2.629*10-3*[(A03+460)0.5]/[1+(198.7/A04+460)]; else report “NA”>> |
| a3 | Outdoor Air Density Correction **(this row is not visible to user) | <<if C02 = Depressurization, then value=0.07517*(1-0.0035666*A06/528)5.2553*(528/{A04+460}); else if C02 = Pressurization, then report “NA”>> |
| a4 | Indoor Air Density Correction **(this row is not visible to user) | <<if C01 = Pressurization, then value=0.07517*(1-0.0035666*A06/528)5.2553*(528/{A03+460}); else report “NA”>> |
| 01 | Altitude and Temperature Correction Factor | <<if C02 = Depressurization, then value= [{(Da1)/0.044}2*(0.65)-1] *[{(Da3)/0.07517}1-0.65]; Else if CO2 = Pressurization, then value = [{(Da2)/0.044}2*(0.65)-1] *[{(Da4)/0.07517}1-0.65]; |
| 02 | Corrected CFM50 | <<else value = C06*D01>> |

| E. Accuracy Adjustment |  |  |
| --- | --- | --- |
| 01 | Adjusted CFM50 (measured air leakage rate) | <<value = D02 * 1.1>> |

| F. Compliance Statement |  |
| --- | --- |
| 01 | << if calibration date in B05 is more than 12 months from the date of the diagnostic test in A07, then display text: “Manometer Calibration is expired, Fails Enclosure Air Leakage Test"; elseif A01 = required, and E01 ≤ A02, then display text: " Passes Enclosure Air Leakage Test"; else display text: “Fails Enclosure Air Leakage Test”>> |

| G. Additional Requirements for Compliance |  |  |
| --- | --- | --- |
| 01 | The procedure for preparing the enclosure for testing is detailed in RESNET 380-2019 Section 3.2. |  |
| 02 | The procedure for installation of the test apparatus, and preparations for measurement shall conform to RESNET 380-2019 Section 3.3 |  |
| 03 | The procedure for the conduct of the enclosure air leakage test shall conform to the One-Point Airtightness Test specified in RESNET 380-2019 Section 3.4.1 |  |
| 04 | Verification Status: | <<user pick from list: *** Pass - all applicable requirements are met; or *** Fail - one or more applicable requirements are not met. Enter reason for failure in corrections notes field below; or *** All n/a - This entire table is not applicable |
| 05 | Correction Notes: | <<if Verification Status= Fail, then text entry in this Corrections Notes field is required; user input text>> |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met unless otherwise noted in the Verification Status and the Corrections Notes in this table. |  |  |

| H. Determination of HERS Verification Compliance All applicable sections of this document shall indicate compliance with the specified verification protocol requirements in order for this Certificate of Verification as a whole to be determined to be in compliance. |  |
| --- | --- |
| 01 | <<if B06 = Manometer Calibration is valid; and C05 = Induced pressure within range for single point test; and F01 = Building Passes Enclosure Air Leakage Test; and G04 = Pass or All n/a; then display: Complies: All specified verification protocol requirements on this document are met; else display: Does not comply: One or more specified verification protocol requirements on this document are not met>> |