CERTIFICATE OF INSTALLATION

Note: This table completed by HERS Registry.

| Project Name: | Enforcement Agency: |
| --- | --- |
| Dwelling Address: | Permit Number: |
| City and Zip Code: | Permit Application Date: |

| A. General Information |  |  |
| --- | --- | --- |
| 01 | Building Name |  |

| B. Design Central Water Heating Systems Information (other than CHPWH) This table reports features of the water heating system other than CHPWH system that were specified on the registered LMCC compliance document for this project. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value |

| B2. Design CHPWH System Information This table reports the water heating systems specified on the registered LMCC compliance document for this project. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Modeled Equipment Make and Model | # of Water Heaters/ Compressors | Primary Tank Location | Primary Tank Volume | Primary Tank Total Insulation | Loop Tank Location | Loop Tank Volume | Loop Tank Total Insulation | Loop Pipe Insulation Thickness | Loop Tank Type | Simulated Equipment Make and Model |

| C. Installed Central Water Heating Systems Information This table reports features of the water heating system other than CHPWH system that were specified on the registered LMCC compliance document for this project. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value |

| C2. Installed CHPWH System Information This table reports the water heating system features that were specified on the registered LMCC compliance document for this project. |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 |
| Water Heating System ID or Name | Modeled Equipment Make and Model | # of Water Heaters/ Compressors | Primary Tank Location | Primary Tank Volume | Primary Tank Insulation | Loop Tank Location | Loop Tank Volume | Loop Tank Insulation | Loop Pipe Insulation Thickness | Loop Tank Type |

| D. Design Central Water Heating Distribution Systems Information This table reports the water heating distribution types specified on the registered LMCC compliance document for this project. |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |

| E. Installed Central Water Heating Distribution Systems Information This table reports the water heating distribution types specified on the registered LMCC compliance document for this project. |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |

| F. Installed Water Heater Manufacturer Information |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Manufacturer | Model Number |

| G. Mandatory Requirements for All Central Domestic Hot Water Systems |  |
| --- | --- |
| 01 | On systems that have a total capacity greater than 167,000 Btu/hr, outlets that require higher than service water temperatures as listed in the ASHRAE Handbook have separate remote heaters, heat exchangers, or boosters to supply the outlet with the higher temperature. (Section 110.3 (c)1) |
| 02 | Systems with circulating pumps or with electrical heat trace systems shall be capable of automatically turning off the system. (Section 110.3(c)2). |
| 03 | Unfired storage tanks are insulated with an external R-3.5 or combination of R-16 internal and external Insulation. (Section 110.3(c)4). |
| 04 | Recirculation loops shall meet the following requirements: - The recirculation pump is mounted on a vertical section of the return line, OR an automatic air release valve is installed on a riser at least 12 inches in length, on the inlet side of the recirculation pump, no more than 4 feet from the pump. (Section 110.3(c)4A). - A check valve is located between the recirculation pump and the water heater. (Section 110.3(c)4B). - A hose bib is installed between the pump and the water heating equipment with an isolation valve between the hose bib and the water heating equipment. (Section 110.3(c)4C). - Isolation valves shall be installed on both sides of the pump, of which the valve required in 110.3(c)4C can be one. (Section 110.3(c)4D). - The cold water piping and the recirculation loop piping shall not be connected to the hot water storage tank drain port. (Section 110.3(c)4E). - A check valve shall be installed on the cold water supply line between the hot water system and the next closest tee on the cold water supply line. (Section 110.3(c)4F). |
| 05 | Instantaneous water heaters with an input greater than 6.8 kBtu/hr. (2kW) shall have isolation valves on both the cold water supply and the hot water line. (Section 110.3 (c)6). |
| 06 | - All domestic hot water piping shall be insulated as specified in Section 609.11 of the California Plumbing Code. Insulation buried below grade must be installed in a waterproof and non-crushable casing or sleeve. - Piping that penetrates framing members shall not be required to have pipe insulation for the distance of the framing penetration. Piping that penetrates metal framing shall use grommets, plugs, wrapping or other insulating material to assure that no contact is made with the metal framing. Insulation shall butt securely against all framing members. - Piping installed in interior or exterior walls that is surrounded on all sides by at least 1 inch (2.5 cm) of insulation. - Piping installed in crawlspace with a minimum of 1 inches (2.5 cm) of crawlspace insulation above and below. - Piping installed in attics with a minimum of 4 inches (10 cm) of attic insulation on top. - Pipe insulation shall fit tightly and all elbows and tees shall be fully insulated. |
| The responsible person’s signature on this compliance document affirms that all applicable requirements in this table have been met. |  |

| Documentation Author's Declaration Statement |  |  |  |
| --- | --- | --- | --- |
| - I certify that this Certificate of Installation documentation is accurate and complete. |  |  |  |
| Documentation Author Name: |  | Documentation Author Signature: |  |
| Documentation Author Company Name: |  | Date Signed: |  |
| Address: |  | CEA/HERS Certification Identification (If applicable): |  |
| City/State/Zip: |  | Phone: |  |
| Responsible Person's Declaration statement |  |  |  |
| ### I certify the following under penalty of perjury, under the laws of the State of California: - The information provided on this Certificate of Installation is true and correct. - I am either: a) a responsible person eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction, or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Installation, and attest to the declarations in this statement, or b) I am an authorized representative of the responsible person and attest to the declarations in this statement on the responsible person’s behalf. - The constructed or installed features, materials, components or manufactured devices (the installation) identified on this Certificate of Installation conforms to all applicable codes and regulations and the installation conforms to the requirements given on the Certificate of Compliance, plans, and specifications approved by the enforcement agency. - I understand that a registered copy of this Certificate of Installation shall be posted or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections, and I will take the necessary steps to ensure this requirement is accomplished. - I understand that a registered copy of this Certificate of Installation is required to be included with the documentation the builder provides to the building owner at occupancy, and I will take the necessary steps to ensure this requirement is accomplished. |  |  |  |
| Responsible Builder/Installer Name: | Responsible Builder/Installer Signature: |  |  |
| Company Name: (Installing Subcontractor or General Contractor or Builder/Owner) | Position With Company (Title): |  |  |
| Address: | CSLB License: |  |  |
| City/State/Zip: | Phone: |  | Date Signed: |

LMCI-PLB-01-E User Instructions

A. General Information

This table reports the building location as specified on the Registered LMCC.

B. Design Central Water Heating Systems Information

This table reports features of the water heating system other than CHPWH system that were specified on the registered LMCC compliance document for this project. This section is for information/verification purposes only and requires no user input.

B2. Design CHPWH System Information

This table reports the water heating systems specified on the registered LMCC compliance document for this project. This section is for information/verification purposes only and requires no user input.

C. Installed Central Water Heating Systems Information

This table reports the water heating system information that is being installed.  Require one line for each  installed water heater.

- Water Heating System ID or Name – Reference information from LMCC.

- Water Heating System Type – Reference information from LMCC. The different kinds of water heating system type are DHW or Combined Hydronic.

- Water Heater Type – Information from LMCC. The different kinds of water heaters are Large/Commercial Storage, Small/Consumer Storage, Residential-Duty Commercial Storage, Heat Pump, Boiler, Large/Commercial Instantaneous, Small/Consumer Instantaneous, Residential-Duty Commercial Instantaneous or Indirect.

- # of Water Heaters in System – Reference information from LMCC.

- Water Heater Storage Volume (gal) – User input. Value may be N/A if water heater type is instantaneous with zero storage.

- Fuel Type – Reference information from LMCC. The different kinds of fuel types are natural gas, propane, oil, or electricity.

- Rated Input Type – Reference information from LMCC. For natural gas, propane and oil fuel type the input type is Btu/hr. For electric the input type is kW.

- Rated Input Value – User input. Numerical value of the rated input. Must be equal to or less than value indicated on the LMCC.

- Heating Efficiency Type – Reference information from LMCC. Different efficiency types are Energy Factor, AFUE, UEF and Thermal Efficiency.

- Heating Efficiency Value – User input. Numerical value of the Heating Efficiency. Must be equal to or higher efficiency than value indicated on the LMCC.

- Standby Loss – User input. Must be equal to or less than value indicated on the LMCC. Value may be N/A if LMCC value is N/A.

- Exterior Insulation. R-Value – User input. Must be equal to or higher than value indicated on the LMCC. Value may be N/A if LMCC value is N/A.

C2. Installed CHPWH System Information

This table reports the water heating system information that is being installed. Require one line for each installed water heater.  Require one line for each installed water heater.

- Water Heating System ID or Name – Reference information from Table B2.

- Modeled Equipment Make and Model – User input must be equal to the value indicated on Table B2 as default and allow user to override with an equivalent system based on the simulated equipment in Table B2.

- Number of Water Heaters/ Compressors – User input, must be equal to the value indicated on table B2.

- Primary Tank Location – Reference information from Table B2.

- Primary Tank Volume – User input, must be equal to or higher than the value indicated on table B2.

- Primary Tank Insulation – User input, must be equal to or higher than value indicated on table B2.

- Loop Tank Location – Reference information from Table B2.

- Loop Tank Volume – User input, must be equal to or higher than the value indicated on table B2.

- Loop Tank Insulation – User input, must be equal to or higher than value indicated on table B2.

- Loop Pipe Insulation Thickness – User input, must be equal to or higher than the value indicated on table B2.

- Loop Tank – Reference information from Table B2.

D. Design Central Water Heating Distribution Systems Information

This table reports the water heating distribution types specified on the registered LMCC compliance document for this project.

E. Installed Central Water Heating Distribution Systems Information

- Water Heating System ID or Name – Reference information from LMCC.

- Central DHW System Distribution Type = Reference information from LMCC.

- Dwelling Unit DHW System Distribution Type = Reference information from LMCC.

F. Installed Water Heater Manufacturer Information

This table reports the manufacturer information of the installed water heater(s). Require one line for each installed water heater

- Water Heating System ID or Name – Reference information from LMCC.

- Manufacturer – User input. Enter the name of the water heater manufacturer.

- Model Number – User input. Enter the model number of the water heater.

G. Mandatory Requirements for All Central Domestic Hot Water Recirculation Systems

This table lists the requirements for all central recirculation systems.  Installer must ensure all the requirements in this table are met.

| A. General Information |  |  |
| --- | --- | --- |
| 01 | Building Name | <<User input>> |

| B. Design Central Water Heating Systems Information <<Static Text - see the top>><<If LMCC only has CHPWH, display the "section does not apply" message>> <<require one row of data for each water heater identified on the LMCC-PRF>> |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value |
| <<Reference values from LMCC >> | <<If Performance, then reference values from LMCC-PRF-01, allowed values: DHW, Hydronic or Combined Hydronic; elseif Prescriptive, then NA >> | <<reference values from LMCC. Allowed values = , Boiler, Indirect, Consumer Instantaneous, Commercial Instantaneous, Consumer Storage, Commercial Storage, Residential-Duty Commercial Storage, or Residential-Duty Commercial Instantaneous >> | <<Reference values from LMCC>> | <<Reference values from LMCC, NA is allowed only if B03 = Consumer Instantaneous, Commercial Instantaneous, or Residential-Duty Commercial Instantaneous >> | << Reference values from LMCC. Allowed values: Natural Gas, Propane, Electric Resistance, or Heat Pump >> | <<if B06 = Heat Pump, then result = NA; If B06 = Natural Gas or Propane, then value = Btu/Hr; Else if B06= Electric Resistance, then value = kW>> | <<if B03 = Heat Pump, then result = NA; If performance, reference value from LMCC-PRF; Else if prescriptive B08 = NA>> B08 >> | <<If Performance, reference values from LMCC-PRF-01, allowed values: *Energy Factor, *AFUE *Thermal Efficiency *Uniform Energy Factor; Else value = NA>> | <<If Performance, reference value from LMCC-PRF-01; Else value = NA>> | <<If Performance, reference Value from LMCC-PRF-01; Else value = NA>> | <<If Performance, reference Value from LMCC-PRF-01; Else value= NA>> |

| B2. Design CHPWH System Information <<Static Text - see the top>> <<If LMCC has CHPWH, then require table, else display the "section does not apply" message>> <<require one row of data for each water heater identified on the LMCC>> |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Modeled Equipment Make and Model | # of Water Heaters/ Compressors | Primary Tank Location | Primary Tank Volume | Primary Tank Total Insulation | Loop Tank Location | Loop Tank Volume | Loop Tank Total Insulation | Loop Pipe Insulation Thickness | Loop Tank Type | Simulated Equipment Make and Model |
| <<Reference values from LMCC >> | <<Reference values from LMCC-PRF-01; else if prescriptive, report default value = Sanden>> | <<Reference values from LMCC>> | <<Reference value from LMCC>> | << Reference value from LMCC>> | << Reference value from LMCC>> | << Reference value from LMCC>> | << Reference value from LMCC>> | << Reference value from LMCC>> | << Reference value from LMCC>> | << Reference value from LMCC>> | <<if performance, hide column from user, needed for equivalency lookup; Reference value from XML; Elseif prescriptive, do not require field>> |

| C. Installed Central Water Heating Systems Information <<Static Text - see the top>> <<If Table B does apply, then require table, else display the "section does not apply" message>> <<require one row of data for each water heater identified in Table B>> |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 |
| Water Heating System ID or Name | Water Heating System Type | Water Heater Type | # of Water Heaters in System | Water Heater Storage Volume (gal) | Fuel Type | Rated Input Type | Rated Input Value | Heating Efficiency Type | Heating Efficiency Value | Standby Loss (%) | Exterior Insul. R-Value |
| <<Reference value from B01 >> | <<Reference value from B02 >> | <<Reference value from B03 >> | <<Reference value from B04>> | << Reference value from B05>> | <<Reference value from B06 >> | <<Reference value from B07>> | <<User input value which must pass the following range tests: If C06 = Heat Pump, then C08 = NA; If C06 = Natural Gas or Propane, then If C03 = Commercial Storage, then value must be > 75,000 Btu/hr; If C03 = Consumer Storage, then value must be ≤ 75,000 Btu/hr; If C03 = Commercial Instant, then value must be > 200,000 Btu/hr; If C03 = Consumer Instant, then value must be ≤ 200,000 Btu/hr; Else if C03 = Residential-Duty Commercial Storage, then value must be ≤ 105,000 Btu/hr; Else if C06 = Electric Resistance, then If C03 = Commercial Storage or Commercial Instant, then value must be > 12 kW; If C03 = Consumer Storage or Consumer Instant, then value must be ≤ 12 kW; Else if C03 = Residential-Duty Commercial Instantaneous, then value must be ≤ 58.6 kW; End If If the value passes range test, it is stored in WaterHeaterElectricFiredRatedInput, if C06 = Electric Resistance. Otherwise the value is stored in WaterHeaterGasFiredRatedInput; Elseif C03 = Boiler or Indirect, no limit on input value >> | << Reference value from B09; elseif prescriptive, then user select from AFUE, Thermal Efficiency, Uniform Energy Factor, and Energy Factor >> | << User Input must be ≥ B10, Value may only be NA if B10 = NA >> | << User Input must ≤ B11, Value may only be NA if B11 = NA >> | << User Input must ≥ B12, Value may only be NA if B12 = NA>> |

| C2. Installed CHPWH System Information <<Static Text - see the top>> <<If Table B2 does apply, then require table, else display the "section does not apply" message>> <<require one row of data for each water heater identified in Table B2>> |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 |
| Water Heating System ID or Name | Modeled Equipment Make and Model | # of Water Heaters/ Compressors | Primary Tank Location | Primary Tank Volume | Primary Tank Insulation | Loop Tank Location | Loop Tank Volume | Loop Tank Insulation | Loop Pipe Insulation Thickness | Loop Tank Type |
| <<reference values from B2-01>> | << If performance, user input is equal to B2-02 as default, and allow user to override with an equivalent system based on the simulated equipment in B2-12; elseif prescriptive, value = Sanden>> | << User Input must equal reference values from B2-03 reference values from LMCC>> | << Reference values from B2-04>> | <<User input, must be ≥ value from B2-05>> | << User input, must be ≥ value from B2-06>> | << Reference values from D07>> | <<User input, must be ≥ value from B2-08>> | << User input, must be ≥ value from B2-09>> | << User input, must be ≥ value from B2-10>> | <<Reference value from B2-11>> |

| D. Design Water Heating Distribution Systems Information <<Static Text - see the top>><<require one row of data for each water heating system identified on the LMCC-PRF>> |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |
| <<reference values from LMCC (see rule in header)>> | <<If performance, reference value from LMCC-PRF-01. Allowed values are: * Multi-family: Recirculation *Multifamily: Non-recirculation Else if Prescriptive, value = *Multi-family: Recirculating demand control>> | <<If Performance, reference value from LMCC-PRF-01. Allowed values are *Standard Distribution System * HERS-Verified Pipe Insulation Else if Prescriptive, value = *Standard Distribution System>> |

| E. Installed Water Heating Distribution Systems Information <<Static Text - see the top>><<require one row of data for each water heating system identified on the LMCC-PRF>> |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Central DHW System Distribution Type | Dwelling Unit DHW System Distribution Type |
| <<reference values from D01>> | <<Reference value from D02>> | << Reference value from D03>> |

| F. Installed Water Heater Manufacturer Information << require one row of data for each water heater identified in Section C, elseif no Section C, then display the "section does not apply" message.>> |  |  |
| --- | --- | --- |
| 01 | 02 | 03 |
| Water Heating System ID or Name | Manufacturer | Model Number |
| <<reference values from C01>> | <<User input>> | <<User input>> |

G. Mandatory Requirements for All Central Domestic Hot Water Systems <<Static Text - see the top>>