## Modified Date
Date | Table | Description of Change | Color
2024-05-14 |  | Changed the CMC section referenced for Duct Leakage Testing from 603.10.1 to 603.9.2. | RED
2024-10-28 | Header/Footer | Update code cycle year in header and footer | yellow with red text
2024-10-28 | Table B | Change OSHPD to HCAI in Table B | yellow with red text
2024-11-11 | Table M | Updated Table M to accommodate the new cooling tower min achievable cycles calculation and added blowdown requirement as footnote | yellow with red text
2024-11-11 | Table F | Updated Min efficiency values based on Tables 110.2 changes - For tables that have been removed or values that have been specified as "federal minimum", we will change the tool and reporting to show "federal minimum" instead of a value. This change has not yet been incorporated to the mock-up due to time intensive formating, but we will be making this change. | yellow with red text
2024-11-11 | Table J | Added "Evaporative Cooler" exception to J07 | yellow with red text
2024-12-13 | Table J | Add/modify minmum ventilation, exhaust and occupancy types | yellow with red text
2024-12-13 | Table J | Incorporate modified fixed seating requirements to J12 | yellow with red text
2024-12-13 | Table J | Add air classification footnote to Table J to accommodate 120.1(g) | yellow with red text
2024-12-13 | Table F | Separate Addition from new enumeration in Space conditiong System Information | yellow with red text
2024-12-13 | Table F | Remove Heat recovery exeption for system type requirements | yellow with red text
2024-12-13 | Table F | Add multizone space type requirements to Dry system table - note if multizone requirements apply, we will be asking the user which pacakge they want to use and then directing them to the correct tables. This is spelled out in the tables, but may be hard to folllow. | yellow with red text
2024-12-13 | Table F | Changed "Chiller Efficiency and Controls" table to "Chiller & Air To Water Heat Pump Efficiency and Controls" to accommodate the AWHP for MZ space type requirements | yellow with red text
2024-12-13 | Table F | Updated min efficiency values for heat pump and heat recovery chillers from Tables 110.2I and J | yellow with red text
2024-12-13 | Table F | Added "Serving" field to Chiler & AWHP table to be used to indicate if the sysstem is serving a FPFC or VAV for MZ space type options 2 and 3. | yellow with red text
2024-12-13 | Table F | Added "Refrigerant loop heat recovery" field to Dry System Table for Multizone option 1 requirements | yellow with red text
2024-12-13 | Table F | Added HVAC Hot Water Supply Temp fild in boiler table for §120.2(I) | yellow with red text
2024-12-13 | Table F | Added Supplemental electric resistance exemption for 140.4(a)3C | yellow with red text
2024-12-13 | Table F | Added new mechanical heat recovery table to accommodate new MHR requirements | yellow with red text
2024-12-13 | Table H | Now all HVAC system names automatically get transferred to Table H as the Fan System Name. Also, if MZ option 1 is selected, a fan system is automatically added to represent the required DOAS system. | yellow with red text
2024-12-13 | Table H | If MZ option 1 or 2 is selected, the fan system for that system uses the 0.35 allowance | yellow with red text
2024-12-13 | Table H | Added new DOAS >1.0 kw to better accommodate and track DOAS and the applicable fan power requirements | yellow with red text
2024-12-13 | Table H | Added footnote to accommodate power draw requriements of 140.4(a)3D | yellow with red text
2024-12-13 | Table H | Added economizer exception for systems complying with MZ requirements package 1 or 2 | yellow with red text
2024-12-13 | Table H | Enforce Exhaust air heat recovery requirements for systems complying with MZ package 1 or 2 | yellow with red text
2024-12-13 | Table I | Incorporate Guideline 26 to the DDC enumeration | yellow with red text
Change trigger to DOAS in Fan table and remove DX-DOAS trigger from table F.
CEC
2025-01-15 | Table F | See Ronald's note on 03-Rating Condition Dropdown
2025-01-16 | Table J(NRCC) | See Ronald's notes on Column 09- Occupancy Type Dropdown
2025-01-16 | Table J(LMCC) | See Ronald's notes on Column 09- Occupancy Type Dropdown

## Table Sequence
Label | Table Title | Trigger within:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | HVAC System Summary (Dry & Wet Systems) | Table B
Table G | Pumps | Table B
Table H | Fan Systems and Air Economizers | Table B
Table I | System Controls | Table B
Table J | Ventilation | Table B
Table K | Terminal Box Controls | Table B
Table L | Distribution (Ductwork & Piping) | Table B
Table M | Cooling Towers | Table B
Table N | Declaration of Required Certificates of Installation | ALWAYS
Table O | Declaration of Required Certificates of Acceptance | ALWAYS
Table P | Declaration of Required Certificates of Verification | ALWAYS
Table Q | Mandatory Measures Documentation Location | ALWAYS
| Signature Page | ALWAYS
Note on C17: 2019 Update: Added new NRCV table
Note on A18: 219 Update: Changed Table letter to Q.

## Hyperlinks
Section
110.1
110.12
110.2
120.1
120.2
120.3
120.4
120.9
140.4
140.4(e)
110.2(a)
110.2(b)
110.2(d)
110.2(e)1
110.2(e)2
110.2(e)3
110.2(e)4
110.2(e)5
120.1(b)2
120.1(c)
120.1(c)2
120.1(d)3
120.1(d)5
120.2(e)
120.2(e)3
120.2(e)3B
120.2(g)
120.3(b)
120.3(c)2
120.4(a)-(f)
140.3(a)1B
140.4(a&b)
140.4(a)
140.4(b)
140.4(c)
140.4(d)
140.4(e)
140.4(f)
140.4(f) and (n)
140.4(h)2
140.4(h)3
140.4(h)5
140.4(i)
140.4(k)
140.4(l)
140.4(m)
140.4(n)
141.0(b)2
141.0(b)2E
Reference Nonresidential Appendix 2 (NA2)
Table 110.2
Table 110.2-E
Table 140.4-B
Tbale 110.2-G
Title 20
Table 120.3-A
130.1(c)

## NRCC Headers
| User input |  | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Mechanical Systems
NRCC-MCH-E (Created XX/XX) |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-MCH-E
This document is used to demonstrate compliance for mechanical systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.4, 140.0, 170.2, §180.1 and §180.2 .
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  |  | Date Prepared:
The project name and date prepared is a user input on the first page, but will populate the heading on all other pages.
STATE OF CALIFORNIA
Mechanical Systems
NRCC-MCH-E (Created XX/XX) |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-MCH-E
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  | Remove this field on all but first & last page header |  |  | Date Prepared:
First & Last Page Heading
Heading for all other pages
Note on A6: 2019 Update: Updated to remove "Table Instructions"
Note on C8: 2/17/23 This cell grays out on all pages other than Page 1 and the last page.

## LMCC Headers
| User input |  | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Mechanical Systems
LMCC-MCH-E |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-MCH-E
This document is used to demonstrate compliance for mechanical systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.0, §140.4, §170.2, §180.1 and §180.2 .
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  |  | Date Prepared:
The project name and date prepared is a user input on the first page, but will populate the heading on all other pages.
STATE OF CALIFORNIA
Mechanical Systems
NRCC-MCH-E (Created XX/XX) |  |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE | [5 empty] | NRCC-MCH-E
Project Name: |  |  |  |  | Report Page: | Page 1 of ??
Project Address: |  | Remove this field on all but first & last page header |  |  | Date Prepared:
First & Last Page Heading
Heading for all other pages
Note on A6: 2019 Update: Updated to remove "Table Instructions"

## NRCC Footers
| User input | auto calculated |  | From another Table |  | From look up table
Footer for every page:
|  |  | Registration Date/Time: |  | Registration Provider:
|  |  | Report Version: |  | Compliance ID:
|  |  | Schema Version: |  | Report Generated:
CA Building Energy Efficiency Standards - 2025 Nonresidential & Multifamily Compliance: https://www.energy.ca.gov/programs-and-topics/programs/building-energy-efficiency-standards/2025-building-energy-efficiency

## LMCC Footers
| User input | auto calculated |  | From another Table |  | From look up table
Footer for every page:
Registration Number: |  |  | Registration Date/Time: |  | Registration Provider:
|  |  | Report Version: |  | Compliance ID:
|  |  | Schema Version: |  | Report Generated:
CA Building Energy Efficiency Standards - 2025 Nonresidential & Multifamily Compliance: https://www.energy.ca.gov/programs-and-topics/programs/building-energy-efficiency-standards/2025-building-energy-efficiency

## A. General Info (NRCC)
| User input | auto calculated |  |  | From another table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  | 04 | Total Conditioned Floor Area
02 | Climate Zone |  | Dropdown |  | 05 | Total Unconditioned Floor Area
03 | Occupancy Types Within Project: |  |  |  | 06 | # of Stories (Habitable Above Grade)
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on A8: 10/28/24 Occupancy types that have been selected show up here

## A. General Info (LMCC)
| User input | auto calculated |  |  | From another table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  | 04 | Total Conditioned Floor Area
02 | Climate Zone |  | Dropdown |  | 05 | Total Unconditioned Floor Area
03 | Occupancy Types Within Project: |  |  |  | 06 | # of Stories (Habitable Above Grade)
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on A8: 10/28/24 Occupancy types that have been selected show up here

## B. Project Scope
|  | User input |  |  | auto calculated |  | From another Table | From look up table
B. PROJECT SCOPE
[d:OnlyUI] Table Instructions: Include any mechanical systems that are within the scope of the permit application and are demonstrating compliance using the mandatory requirements in §110.2, §120.1, §120.2, §120.4, §120.5, §120.9 and prescriptive path outlined in §140.4, or §141.0(b)2 for alterations. [d:/OnlyUI] [d:OnlyRG] This table includes mechanical systems or components that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.4, 170.2(b) or §141.0(b)2 and 180.2(b)2 for alterations. [d:/OnlyRG]
My project consists of (check all that apply)
01 |  | 02 |  | 03
Air System(s) |  | Wet System Components |  | Dry System Components
¨ | Heating Air System | ¨ | Water Economizer | ¨ | Air Economizer | <<triggers Table H
¨ | Cooling Air System | ¨ | Pumps | ¨ | Electric Resistance Heat | << triggers "Electric Resistance" Section in Table F
Mechanical Controls |  | ¨ | System Piping | ¨ | Fan Systems | << triggers Table H
|  | ¨ | Cooling Towers | ¨ | Ductwork (existing to remain, altered or new) | << triggers "Ductwork" section in Table L
¨ | Mechanical Controls (existing to remain, altered or new) | ¨ | Chillers | ¨ | Ventilation | << triggers Table J.01-J.03 UNLESS "Healthcare" is the ONLY occupancy type checked in Table A column 03. If this is the case, trigger "ALERT! Healthcare facilities must be" note below
|  | ¨ | Boilers | ¨ | Zonal Systems/ Terminal Boxes | << triggers Table K UNLESS "Healthcare" is the ONLY occupancy type checked in Table A colmn 03.
ALERT! Healthcare facilities must be ventilated in accordance with Chapter 4 of the CMC as amended by HCAI and do not need to show compliance with Title 24, Part 6 ventilation requirements in Table J.
Note on B9: Sally Blair/Gina: Triggers Controls Table I and Table F "Dry System Eq. Sizing"
Note on C9: Sally Blair: Triggers "Heat Rejection Eq." section in Table F.
Note on B10: Gina: Triggers Controls Table I and Table F "Dry System Eq. Sizing"
Note on C10: Sally Blair: Triggers Table G
Note on C11: Sally Blair: Triggers "Piping" Section in Table L
Note on F11: 3.25.22 When Fan Systems is selected, ventilation is automatically selected
Note on C12: Sally Blair: Triggers Table M & "Heat Rejection Eq." section in Table F.
Note on B13: Sally Blair/Gina: Triggers Controls Table I
Note on C13: Sally Blair: Triggers "Chiller Efficiency & Controls" section in Table F.
Note on F13: 3.25.22 When ventilation is selected, fan systems are automatically selected
Note on G13: 2019 Update: Exception for triggering Table J if Healthcare is checked in Table A was added.
Note on C14: Sally Blair: Triggers "Boiler Efficiency & Controls" section in Table F.
Note on G14: 2019 Update: Exception for triggering Table K if Healthcare is checked in Table A was added.
Note on A15: 2020 Clarification: Triggers when "Healthcare Facility" is checked in Table A AND "Ventilation" in Table B

## C. NRCC Compliance
| User input |  |  | auto calculated |  |  |  | From another Table |  |  |  | From look up table
C. COMPLIANCE RESULTS
[d:OnlyUI] Table Instructions: If any cell on this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D. for guidance. [d:/OnlyUI] [d:OnlyRG] Table C will indicate if the project data input into the compliance document is compliant with mechanical requirements. This table is not editable by the user. If this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D., or the table indicated as not compliance for guidance. [d:/OnlyRG]
01 | AND | 02 | AND | 03 | AND | 04 | AND | 05 | AND | 06 | AND | 07 | AND | 08 | 09
System Summary §110.1, §110.2, §140.4, §170.2(c) |  | Pumps §140.4(k), §170.2(c)4I |  | Fans/ Economizers §140.4(c), §140.4(e), §170.2(c) |  | System Controls §110.2, §120.2, §140.4(f), §170.2(c) |  | Ventilation §120.1, §160.2 |  | Terminal Box Controls §140.4(d), §170.2(c)4B |  | Distribution §120.3, §120.4, §160.2, §160.3 |  | Cooling Towers §110.2(e)2 | Compliance Results
(See Table F) |  | (See Table G) |  | (See Table H) |  | (See Table I) |  | (See Table J) |  | (See Table K) |  | (See Table L) |  | (See Table M)
Yes/No | AND | Yes/No | AND | Yes/No | AND | Yes/No | AND | Yes/No | AND | Yes/No | AND | Yes/No | AND | Yes/No | COMPLIES or "COMPLIES WITH EXCEPTIONAL CONDITIONS" or DOES NOT COMPLY
Mandatory Measures Compliance (See Table Q for Details) | [14 empty] | COMPLIES or DOES NOT COMPLY
Tool Tip:
Table C is auto-filled from data found in the rest of the NRCC-MCH, and it may not be directly edited by the form user. Table C compliance results are automatically calculated from data input and calculations in Tables F through N.
Note on A9: 3.29.22 Says "Yes" if: Dry Sys Eq Sizing Table: if this table is triggered, every field that is not grey must be completed. AND Dry Sys Eq Efficiency (not PTAC/PTHP) Table: if triggered, fields are completed if not grey AND 05 < 06 and 08 < 09 (if not grey). AND Dry Sys Eq Efficiency (PTAC/PTHP) Table: if triggered, fields are completed if not grey AND 03 < 04 and 06 < 07 (if not grey). AND Boiler Efficiency & Controls Table: if triggered, fields are completed if not grey AND all instances of System Efficiency > Minimum System Efficiency. AND Chiller Efficiency & Controls Table: if triggered, fields are completed if not grey AND 06 > 07. 06>=07 if unit in column 08 is "EER" or "COP" OR 06>=07 if unit in column 08 is IPLV and column 02 is EITHER Air Cooled: Condenser elec. operated or Air Cooled: w/o condenser elec operated or Absorption Double effect, indirect fired or Absorption Double effect, direct fired or Water Cooled: Gas engine OR 07>=06 if unit in column 08 is kW/ton OR 07>=06 if unit in column 08 is IPLV and column 02 is EITHER Water Cooled: Reciprocating or Water Cooled: Positive displacement or Water Cooled: Centrifugal AND DX-DOAS Efficiency Table: If triggered, all fields are either completed or gray/blank AND 6< 08 for both ISMRE and ISCOP rows AND Dual Fuel Heat Pump Table: If triggered, all fields are either completed or gray/blank AND 07 >06 AND 10 > 09 AND Heat Rejection Equipment Table: if triggered, fields are completed AND 05 > 06. AND Electric Resistance Heating Table: if triggered, fields are completed Otherwise, says "No"
Note on C9: Sally Blair: Says "Yes" if: If triggered, all fields must be completed (if not grey). Otherwise, says "No"
Note on E9: 5.25.23 C.03 = Yes If: Fan Systems & Air Economizers: If triggered, All fields must be completed or blank/gray AND Fan System Allowance >= Fan System Electrical Input Power AND All instances of Fan System Allowance > Fan System Electrical Input Power AND Dwelling Unit Fan Efficacy Table: If triggered, all fields must be completed or blank/gray AND 07<08 AND 10 >11 AND Exhaust Air Heat Recovery Table: if triggered, all fields must be completed or gray/blank AND DOAS Table: If triggered, all fields must be completed or gray/blank AND if column 2 of FEI Table == None Applies, column 3 of FEI table is greater than or equal to 1.0 Else if column 2 of FEI Table == Variable Air Volume, column 3 of FEI table is greater than or equal to 0.95 Else = "No"
Note on G9: 6.20.22 Says "Yes" if: If triggered, all fields must be completed (if not grey). Otherwise, says "No"
Note on I9: 3/29/22 Says "Yes" if: Nonresidential, Hotel/Motel and Multifamily Common Use Ventilation Systems Table: If triggered, Either 01 is selected OR 04 - 16 are completed OR gray/blank AND 18 only says "Yes" AND Multifamily Dwelling Unit Ventilation Systems: If triggered, All fields are completed or gray/blank AND all instances of J28 and J29 = "Yes" or gray/blank. AND Otherwise, says "No
Note on K9: Sally Blair: Says "Yes" if: If triggered, all fields must be completed (if not grey) AND column 12 only says "Yes" Otherwise, says "No"
Note on M9: 11.11.21 Says "Yes" if: Mand. Pipe Insul. Table: If triggered, 01 is checked AND Either 07<= 09 OR 08 < 09 OR selection in column 10 is something other than "no exception taken" AND Duct Leakage Table: if triggered, all dropdowns are completed if not grey. Otherwise, says "No"
Note on O9: Sally Blair: Says "Yes" if: If triggered, EITHER 01 is checked OR 03-12 are completed & column 16 says "Yes" Otherwise, says "No" 2019 Update: column #'s changed because of added column 02.
Note on P9: Sally Blair: 1. Says "COMPLIES" if no other cells in C.01-C.08 say "No" & no exceptional conditions have been triggered in Table D. 2. Says "COMPLIES WITH EXCEPTIONAL CONDITIONS" if no other cells in C.01-C.08 say "No" & an exceptional condition has been triggered in Table D. 3. Says "DOES NOT COMPLY" if one of the cells in C.01-C.08 says "No"
Note on A10: 2019 Update: Changed Table Reference to Q
Note on P10: Sally Blair: Says "COMPLIES" if Table Q columns 01 & 02 are completed OR if column 04 is completed. Otherwise, says "DOES NOT COMPLY".
Note on A12: UI Only: Tool Tips do not apply to the report generator.

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
1. | Selections made in Table O have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination.
2. | Transfer air is being used in at least one zone to meet minimum ventilation requirements. See Table J for detail. Transfer air must be designed per §120.1(g) for air classification and recircultaion limitations and be documented within construction documents.
3. | The permit applicant has indicated on Table M that cooling tower Maximum Cycles of Concentration calculations have been attached or included elsewhere on the plans.
4. | The permit applicant has indicated on Table J that ventilation calculations have been attached or included elsewhere on the plans.
5. | The permit applicant has indicated on Table J that natural ventilation is being utilized to meet ventilation requirements. Additional documentation may be requested by the Authority Having Jurisdiction demonstrating compliance for natural ventilation design.
6. | Table F indicates more than one boiler, however an exception for isolation valve has been indicated that only applies to plants with only one boiler. Please revise Table F. prior to permit application.
7. | Table F indicates a boiler with rated capacity greater than 500kBtu/h, however an exception for temperature reset controls has been indicated that only applies to boilers < 500kBtu/h. Please revise Table F. prior to permit application.
8. | Table F indicates more than one chiller, however an exception for isolation valve has been indicated that only applies to plants with only one chiller. Please revise Table F. prior to permit application.
9. | An exception has been taken to allow electric resistance heating. See Table F. for details.
10. | Table H indicates a Fan Power System Index that exceeds the maximum allowed per §140.4(c). Please revise to demonstrate compliance.
11. | Selections made in Table P have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination.
12. | Table J indicates continuous ventilation is being used as an alternative to a balanced system. However, Table J also indicates both supply and exhaust fans are being used. Please verify the same ventilation type is being used in all dwelling units within the building per 120.1(b)2Aivb
13. | The permit applicant has indicated their multifamily dwelling units does not contain a kitchen or bathroom. See Table J Multifamily Dwelling Unit Ventilation for details.
Note on P9: 2019 Update: Removed these errors as they are no longer relevant.
Note on B12: 12/13/2022: Triggered if the user changes radio button in Table O.
Note on B13: Sally Blair: Triggered by Table J column 05 2019 Update: Updated column # that triggers note in Table J & updated note text.
Note on B14: 12/13/2022: Triggered if the box is checked in Table M.01.
Note on B15: 12/13/2022: Triggered if the box is checked in Table J.01.
Note on B16: 12/13/2022: Triggered if the box is checked in Table J.03.
Note on B17: 12/13/2022: Triggered if "NA" is selected in Table F (Boiler Efficiency and Controls) F.08 AND F.03 Qty is greater than 1.
Note on B18: 12/13/2022: Triggered if "NA: ≤ 500,000 Btu/h" selected in Table F (Boiler Efficiency and Controls) F.08 AND 'Rated Input Capacity' is EITHER >500,000 to 2,500,000 OR > 2,500,000 in F.04.
Note on B19: 12/13/2022: Triggered if "NA" selected in Table F (Chiller Efficiency and Controls) F.09 AND F.03 Qty is greater than 1.
Note on B20: 12/13/2022: Triggered if any Exceptions 1 through 5 are selected in Table F (Electric Resistance Heating) F.04.
Note on J21: 9/11/20 Triggers when: Table H "Total System Design (B)HP:" row > Table H "Maximum System Fan Power (B)HP:" row
Note on B22: 12/13/2022: Triggered if the user changes radio button in Table P.
Note on G22: 2019 Update: New for 2019 since Table P was added.
Note on B23: 9/11/20: New note as of 9/10/20 to support the alternative compliance path for HRR balanced system requirements 12/13/2022: Triggered if the user is using continuous ventilation to meet the HRR ventilation requirements (first checkbox in HRR ventilation table) AND J24 and J24 both have values greater than 0.
Note on B24: 12/13/2022: Triggered if no If neither Bathroom/ Kitchen IAQ or Bathroom/Kitchen IAQ & Vent is selected in J.26 of Table J (Multifamily Dwelling Unit Ventilation Systems).

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## F. HVAC Systems (NRCC)
|  | User input |  |  | auto calculated | [6 empty] | From another Table |  |  | From look up table
F. HVAC SYSTEM SUMMARY (DRY & WET SYSTEMS)
This table is used to demonstrate compliance for mechanical equipment with mandatory requirements found in §110.1 and §110.2(a) and prescriptive requirements found in §140.4 (a), §140.4(b), §170.2(c)1, §170.2(c)3, §140.4(k) or §141.0(b)2 and §180.2(b)2 for alterations.
Space Conditioning System Information
01 | 02 | 03 | 04 | 05 | 06
Name or Item Tag | Quantity | System Serving | System Status | Space Type | Utilizing Recovered Heat
|  | Dropdown | Dropdown | Dropdown | ¨
|  | System Serving Dropdown | Status Dropdown | Space Type Dropdown
|  | Single Zone | New/Addition | Retail
|  | Multi-Zone | Alteratation | Grocery
|  | Multiple Dwelling units | Addition | School
|  | Individual Dwelling Unit |  | Financial Institution
Library
Office Space in Wearhouse
Office
Other
NOTE - The sizing table below is not completed from left to right in the user interface. Sizing information is needed to determine if system type is restricted. This is ok since the form is just a reporting tool, not a user interface
Dry System Equipment Sizing (includes air conditioners, condensers, heat pumps, VRF, furnaces, unit heaters and DOAS systems )
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Name or Item Tag | Equipment Category per Tables 110.2, §140.4(a)2 and 170.2(c)3aii | Equipment Type per Tables 110.2 & Title 20 | Smallest Size Available1 §140.4(a) & 170.2(c)1 | Equipment Sizing per Mechanical Schedule (kBtu/h) §140.4 (a&b), §170.2(c)1 & §170.2(c)2
|  |  |  | Heating Output2,3 |  |  | Cooling Output2,3 |  | Load Calculations3,4
|  |  |  | Per Design (kBtu/h) | Rated (kBtu/h) | Supp. Heating Output (kBtu/h) | Sensible Per Design (kBtu/h) | Rated (kBtu/h) | Total Heating Load (kBtu/h) | Total Sensible Cooling Load (kBtu/h)
auto-populated from table above | Dropdown | Dropdown | Dropdown
1 FOOTNOTES: Equipment shall be the smallest size, within the available options of the desired equipment line, necessary to meet the design heating and cooling loads of the building per §140.4(a) and §170.2(c)1. Healthcare facilities are excepted. | [8 empty] | Add Row | Remove Last
2 It is common practice to show rated output capacity on the equipment schedule. Sensible cooling output comes from specification sheet tables.
3 If equipment is heating only, leave cooling output and load blank. If equipment is cooling only, leave heating output and load blank.
4 Authority Having Jurisdiction may ask for load calculations used for compliance per §140.4(b) and §170.2(c)2. | [21 empty] | Customized Sizing drop downs for column 02 in Dry System Equipment Efficiency (other than Package Terminal Air Conditioners (PTAC) and Package Terminal Heat Pumps (PTHP)) Table
| Equipment Category Dropdown | Eq Type Dropdown | Smallest Size Dropdown | [11 empty] | Dropdown for Column 03Eq Type
| Unitary AC/ Condensers | Ben, see column M. | Yes | [17 empty] | From Table 110.2-A >> | AC, water cooled | AC, evaporatively cooled | Condensing Units, air cooled | Condensing Units, water cooled | Condensing Units, evaporatively cooled
| Unitary AC/ Cond. (no elec. resistance) |  | NA: Standby Equip. | [18 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000 | > 135,000
| Unitary heat pumps |  | NA: Load Controls | [10 empty] | "Unitary AC/ Condensers" | AC, water cooled | << from Table 110.2-A | [5 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
| Unitary heat pumps (no elec. resistance) |  | NA: Altered per §141.0(b)2E & 180.2(b)2 | [18 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000
| PTAC/ PTHP |  | NA: System serves Healthcare | [11 empty] | AC, evaporatively cooled | << from Table 110.2-A | [5 empty] | > 760,000 | > 760,000
| SPVAC/ SPVHP |  | NA: DOAS system | [12 empty] | << from Table 110.2-A |  |  | Last updated Table B-2 on 4.3.2020 from Title 20 Section 1605.1
| Variable Refrigerant Flow | [13 empty] | Condensing units, air cooled | << from Table 110.2-A
| Furnace/ Unit heater | [13 empty] | Condensing units, water cooled | << from Table 110.2-A
| Ceiling Mounted Computer Rm AC | [13 empty] | Condensing units, evaporatively cooled | << from Table 110.2-A
Computer Room AC (not ceiling mounted)
Sm. Commercial AC
| Furnace + AC | [18 empty] | AirCooledSplit1PhaseAC
Room AC/HP
Dual Fuel Heat Pump
Dedicated Outdoor Air System
Dry System Equipment Efficiency (other than Package Terminal Air Conditioners (PTAC), Package Terminal Heat Pumps (PTHP), DX-DOAS and Dual Fuel Heat Pumps) | [14 empty] | AC, air cooled, split (1 phase)
01 | 02 | 03 | 04 | 05 |  | 06 | 07 | 08 | 09 | 10 |  |  |  |  | AC, air cooled, split (3 phase)
Name or Item Tag | Size Category (Btu/h) | Heating Mode | [5 empty] | Cooling Mode | [6 empty] | AC, air cooled, split, space constrained
|  | Rating Condition (oF) | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 |  | Design Efficiency | Refrigerant Loop Heat Recovery | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency |  |  |  |  | AC, air cooled, package (1 phase)
From Eq Table above | Dropdown | Dropdown | Dropdown | Values from Tables 110.2-A, B, C, F, G & T20 Tables |  |  |  | Unit from efficiency tables auto populates here based on size category (col 02) | Values from Tables 110.2-A, B, C, F, G & T20 Tables | [5 empty] | AC, air cooled, package (3 phase) | [5 empty] | From Tables C-3, C-4 or 110.2-A, depending on size category >> | AC, air cooled, split (1 phase) | AC, air cooled, split (3 phase) | AC, air cooled, split, space constrained | AC, air cooled, package (1 phase) | AC, air cooled, package (3 phase) | AC, air cooled, package, space constrained | AC, air cooled, small duct, high velocity
[8 empty] | Unit from efficiency tables auto populates here based on size category (col 02) | Values from Tables 110.2-A, B, C, F, G & T20 Tables | [5 empty] | AC, air cooled, package, space constrained | [6 empty] | < 45,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[15 empty] | AC, air cooled, small duct, high velocity | [6 empty] | >= 45,000 and < 65,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
| Size Category Dropdown | Rating Condition Dropdown | Unit Dropdown |  |  |  |  | Units for auto populating, depends on equipment & size | [5 empty] | Sm. Commercial AC | Air-cooled unitary AC/HP Split Sys (3Ph) | << from Table C-4 to the right | [5 empty] | >= 65,000 and < 135,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
| See tables in column AF of this tab for custom drop downs. Sorry! | See choices in notes in column AF rows 51 & 76 of this tab. | COP |  |  |  |  | EER | [6 empty] | Air-cooled unitary AC/HP Pkg (3Ph) | << from Table C-4 to the right | [5 empty] | >= 135,000 and < 240,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000
|  |  | AFUE |  |  |  |  | IEER | [5 empty] | "Unitary Heat Pumps" | Air cooled, split (1 phase) | [6 empty] | >= 240,000 and < 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000
|  |  | Et |  |  |  |  | SEER | [6 empty] | Air cooled, split (3 phase) | [6 empty] | >= 760,000
|  |  | Ec |  |  |  |  | COP | [6 empty] | Air cooled, split, space constrained
|  |  | HSPF |  |  |  |  | SCOP | [6 empty] | Air cooled, package (1 phase)
Air cooled, package (3 phase)
[15 empty] | Air cooled, package, space constrained | [5 empty] | From Table C-4 to the left >> | Air-cooled unitary AC+HP Split Sys (3Ph) | Air-cooled unitary AC+HP Pkg (3Ph)
[15 empty] | Aircooled, small duct, high velocity | [6 empty] | < 65,000 | < 65,000
[15 empty] | Water source | << from Table 110.2-B |  |  |  |  | From Table 110.2-B >> | Water source | Groundwater source | Ground source | Water source water-to-water | Groundwater source water-to water | Ground source brine-to-water
[15 empty] | Groundwater source | << from Table 110.2-B | [5 empty] | <17,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000
Dry System Equipment Efficiency (Package Terminal Air Conditioners (PTAC) and Package Terminal Heat Pumps (PTHP) only) | [14 empty] | Ground source | << from Table 110.2-B | [5 empty] | =>17,000 and < 135,000
01 | 02 | 03 | 04 | 05 | 06 | 070 | [8 empty] | Water source water-to-water | << from Table 110.2-B | [5 empty] | > 135,000 and < 240,000
Name or Item Tag | Heating Mode |  |  | Cooling Mode | [10 empty] | Groundwater source water-to water | << from Table 110.2-B | [6 empty] | 1 |  | 1 | 1 |  | 1 | 1
| Rated Output Capacity (kBtu/h) | Minimum COP Required per Table 110.2-E | Design COP | Rated Output Capacity (kBtu/h) | Minimum EER Required per Table 110.2-E | Design EER | [8 empty] | Ground source brine-to-water | << from Table 110.2-B |  |  |  |  | From Table C-3, C-4, 110.2-B or 110.2-C depending on size category>> | Air-cooled gas-engine heat pump | Air cooled, split (1 phase) | Air cooled, split (3 phase) | Air cooled, split, space constrained | Air cooled, package (1 phase) | Air cooled, package (3 phase) | Air cooled, package, space constrained | Air cooled, small duct, high velocity
[15 empty] | Air-cooled gas-engine heat pump | << from Table 110.2-C | [5 empty] | Grey out the cell for this selection | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
From Eq Table above | Comes from sizing table column 06 | From Table 110.2-E Title 20 |  | Comes from sizing table column 09 | From Table 110.2-E Title 20 | [17 empty] | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
[23 empty] | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
[14 empty] | "PTAC/PTHP" | PTAC newly constructed or newly conditioned | << from Table 110.2-E | [5 empty] | F03_UnitaryHeatPumps | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000
[15 empty] | PTAC replacements | << from Table 110.2-E
[15 empty] | PTHP newly constructed or newly conditioned | << from Table 110.2-E |  |  |  | ƒ
[15 empty] | PTHP replacements | << from Table 110.2-E
[14 empty] | "SPVAC/ SPVHP" | SPVAC | << from Table 110.2-E
NOTE - This table should act like the fan table with tiered levels. There can be mutiple Boiler systems and multiple boilers within each boiler system | [14 empty] | SPVAC nonweatherized space constrained | << from Table 110.2-E
Boiler Efficiency and Controls | [14 empty] | SPVHP | << from Table 110.2-E |  | Last updated Table C-3 on 4.3.2020 from Title 20 Section 1605.1 |  |  | From Table 110.2-E >> | SPVAC | SPVHP
Boiler System Serving: |  |  | User Input | [11 empty] | SPVHP nonweatherized space constrained | << from Table 110.2-E | [5 empty] | < 65,000 | < 65,000
01 | 02 |  | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Boiler Name or Item Tag | Equipment Type1 |  | Qty | Rated Input Capacity (Btu/h)2, 3 | Rated Efficiency | Minimum Efficiency Required per §110.2 | Efficiency Unit | Boiler Controls per §140.4(k) & §170.2(c)Iiii |  | High Capacity Boiler Exceptions | HVAC Hot Water Supply Temperature §120.2(I)
[8 empty] | Isolation Valve | Temperature Reset
| Dropdown |  |  |  |  | Use table 110.2-J column after 1/10/23 Title 20 Tables | Units listed in Table 110.2-J Title 20 Tables | Dropdown | Dropdown | Dropdown | user input
System Efficiency |  |  | User Input 05: Minimum System Efficiency for High Capacity Boilers per 140.4(k)8A; User Input 08: 90%
1 FOOTNOTES: Use NRCC-PLB to document compliance with domestic hot water and service water heating systems | [20 empty] | From Table 110.2-G >> | VRF air conditioners, air cooled
2 Maximum capacity- maximum ratings per the certified unit capacity |  |  | User Input 08: Isolation Dropdown; User Input 09: Temperature Reset Dropdown; User Input 10: HCB Exceptions Dropdown | [10 empty] | < 65,000
3 Includes oil-fired (residual) |  |  | User Input 08: Yes; User Input 09: Yes; User Input 10: >=25% space heating provided by on-site renewable |  |  | "VRF" | VRF air conditioners, air cooled | << from Table 110.2-G | [5 empty] | > 65,000 and < 135,000
|  |  | User Input 08: NA: only 1 boiler in plant; User Input 09: NA: < 500,000 Btu/h; User Input 10: >=25% space heating provided by site recovered energy |  |  |  | VRF heat pump, air cooled | << from Table 110.2-H | [5 empty] | > 135,000 and < 240,000
| Equipment Type Dropdown |  | User Input 09: NA: Variable Flow Controls; User Input 10: >=25% space heating provided heat recovery chillers |  |  |  | VRF water source | << from Table 110.2-H | [5 empty] | > 240,000
| Hot water: Gas-Fired |  | User Input 09: NA: System serves Healthcare; User Input 10: Installed in individual dwelling unit |  |  |  | VRF groundwater source | << from Table 110.2-H
| Hot water: Oil-Fired |  | User Input 10: >=50% heating served by perimeter convective/radiant ceiling panels |  |  |  | VRF ground source | << from Table 110.2-H |  |  |  |  | From Table 110.2-H >> | VRF heat pump, air cooled | VRF water source | VRF groundwater source | VRF ground source
| Steam: Gas-Fired, not natural draft |  | User Input 10: Serving Multifamily Occupancy |  |  | "Furnace/ Unit Heater" | Warm-air central furnace, gas-fired | << from Table 110.2-I | [5 empty] | < 65,000 | < 65,000 | < 135,000 | < 135,000
| Steam: Gas-Fired, natural draft |  | User Input 10: No Exceptions Apply |  |  | "Furnace/ Unit Heater" | Warm-air duct furnace, gas-fired | << from Table 110.2-I | [5 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000
| Steam: Oil-Fired | [13 empty] | Warm-air unit heaters, gas-fired | << from Table 110.2-I | [5 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
[14 empty] | "Furnace/ Unit Heater" | Weatherized gas central furnace w single phase supply | << from Table 4-1 to the right | [5 empty] | > 240,000 | >=240,000
[15 empty] | Non-weatherized gas central furnace w single phase supply | << from Table 4-1 to the right |  | Last updated Table C-4 on 4.3.2020 from Title 20 Section 1605.1.. Larger size HP are covered in T24 110.2 Tables.
[14 empty] | "Furnace/ Unit Heater" | Wall furnace, fan | << from Table 4-2 to the right |  |  |  |  | From Table 110.2-I >> | Warm-air central furnace, gas-fired | Warm-air duct furnace, gas-fired | Warm-air unit heaters, gas-fired
[15 empty] | Wall furnace, gravity | << from Table 4-2 to the right | [5 empty] | < 225,000 | Grey out the cell for this selection | Grey out the cell for this selection
[15 empty] | Floor furnace | << from Table 4-2 to the right | [5 empty] | > 225,000
[15 empty] | Room Heater | << from Table 4-2 to the right
[14 empty] | "Computer Rm AC (not ceiling mounted) | CRAC, air-cooled, downflow | << from Table C-7 to the right |  |  |  |  | From Title 20 Table E-6 to the left >> | Weatherized gas central furnace w single phase supply | Non-weatherized gas central furnace w single phase supply
[15 empty] | CRAC, air-cooled, upflow | << from Table C-7 to the right | [5 empty] | < 225,000 | < 225,000
[15 empty] | CRAC, water-cooled, downflow | << from Table C-7 to the right
[15 empty] | CRAC, water-cooled, upflow | << from Table C-7 to the right |  |  |  |  | From Table E-2 to the left >> | Wall furnace, fan | Wall furnace, gravity | Floor furnace | Room Heater
[15 empty] | CRAC, water-cooled w econ, downflow | << from Table C-7 to the right | [5 empty] | < 42,000 | < 27,000 | < 37,000 | < 20,000
[15 empty] | CRAC, water-cooled w econ,upflow | << from Table C-7 to the right | [5 empty] | > 42,000 | > 27,000 and < 46,000 | > 37,000 | > 20,000 and < 27,000
[15 empty] | CRAC, Glycol-cooled, downflow | << from Table C-7 to the right | [6 empty] | > 46,000 |  | > 27,000 and < 46,000
[15 empty] | CRAC, Glycol-cooled, upflow | << from Table C-7 to the right | [8 empty] | > 46,000
[15 empty] | CRAC, Glycol-cooled w econ, downflow | << from Table C-7 to the right | Last updated Table C-7 on 4.3.2020 from Title 20 Section 1605.1
[15 empty] | CRAC, Glycol-cooled w econ, upflow | << from Table C-7 to the right |  |  |  |  | From Table C-7 to the left >> | CRAC, air-cooled, downflow | CRAC, air-cooled, upflow | CRAC, water-cooled, downflow | CRAC, water-cooled, upflow | CRAC, water-cooled w econ, downflow | CRAC, water-cooled w econ, upflow | CRAC, Glycol-cooled, downflow | CRAC, Glycol-cooled, upflow | CRAC, Glycol-cooled w econ, downflow | CRAC, Glycol-cooled w econ, upflow
[14 empty] | Room AC/HP | Room AC, louvered sides | << from Table B-2 to the right | [5 empty] | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[15 empty] | Room AC, no louvers | << from Table B-2 to the right | [5 empty] | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000
[15 empty] | Room AC, casement only | << from Table B-2 to the right | [5 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000
[15 empty] | Slider Room AC, casement | << from Table B-2 to the right
[15 empty] | Room AC Heat Pump, louvered sides | << from Table B-2 to the right
[15 empty] | Room AC Heat Pump, no louvers | << from Table B-2 to the right
[14 empty] | Furnace + AC | AC, air cooled, split + warm-air central furnace, gas-fired
AC, air cooled, split + weatherized gas central furnace
[15 empty] | AC, air cooled, single pkg + weatherized gas central furnace, 1 phase supply | [5 empty] | From Table 110.2-A & T20 C-3 (cooling) & 110.2-I & Table E-6 to the left (heating) >>> | AC, air cooled, split + Warm-air central furnace, gas-fired | AC, air cooled, split+ weatherized gas central furnace w single phase supply |  | From Table 110.2-A & T20 C-3 (cooling) & 110.2-I & Table E-6 to the left (heating) >>> | AC, air cooled, single package + Weatherized gas central furnace w single phase supply | AC, air cooled, single package + Warm-air central furnace, gas-fired
[15 empty] | AC, air cooled, single pkg + warm-air central furnace, gas-fired | [6 empty] | <45kBtuh cooling/ <225kBtuh heating | <45kBtuh cooling/ <225kBtuh heating
[14 empty] | Unitary AC/ Cond. (no elec. resistance) | AC, water cooled | [6 empty] | <45kBtuh cooling/ >225kBtuh heating | <45kBtuh cooling/ >225kBtuh heating |  |  | <65kBtuh cooling/ <225kBtuh heating | <65kBtuh cooling/ <225kBtuh heating
Chiller & Air To Water Heat Pump Efficiency and Controls | [14 empty] | AC, evaporatively cooled | [6 empty] | >45kBtuh cooling/ <225kBtuh heating | >45kBtuh cooling/ <225kBtuh heating |  |  | <65kBtuh cooling/ >225kBtuh heating | <65kBtuh cooling/ >225kBtuh heating
01 |  | 02 | 03 | 04 | 05 | 06 |  | 07 | 08 | 09 | 10 | 11 | 12
Name or Item Tag |  | Equipment Type | Qty | Size Category1 (Tons) | Leaving Hot Water Temperature | Chiller Efficiency "Path B" Exception per §140.4(i) & §170.2(c)g |  | Rated Efficiencies | Efficiencies Required per §110.22 | Efficiency Unit | Controls per §140.4(k) & §170.2(c)I |  | Serving | [8 empty] | >45kBtuh cooling/ >225kBtuh heating | >45kBtuh cooling/ >225kBtuh heating |  |  | >65kBtuh cooling/ <225kBtuh heating | >65kBtuh cooling/ <225kBtuh heating
|  |  | User Input 11: Isolation Valve | Temperature Reset |  |  | Condensing units, air cooled | [6 empty] | >65kBtuh cooling/ <225kBtuh heating | >65kBtuh cooling/ <225kBtuh heating |  |  | >65kBtuh cooling/ >225kBtuh heating | >65kBtuh cooling/ >225kBtuh heating
|  | Dropdown to match Table 110.2-D |  | Dropdown | Dropdown | Dropdown |  |  | Ben, "Path B" value from Table 110.2-D or 110.2-NI & J | Ben, "Path B" units from Table 110.2-D or 110.2-NI & J | Dropdown | Dropdown |  |  | Condensing units, water cooled | [6 empty] | >65kBtuh cooling/ >225kBtuh heating | >65kBtuh cooling/ >225kBtuh heating |  |  | >135kBtuh cooling/ <225kBtuh heating | >135kBtuh cooling/ <225kBtuh heating
|  |  | User Input 09: Ben, "Path B" value from Table 110.2-D or 110.2-NI & J; User Input 10: Ben, "Path B" units from Table 110.2-D or 110.2-NI & J |  |  |  | Condensing units, evaporatively cooled |  | Last updated Table E-6 on 4.3.2020 from Title 20 Section 1605.1 |  |  |  |  | >135kBtuh cooling/ <225kBtuh heating | >135kBtuh cooling/ <225kBtuh heating |  |  | >135kBtuh cooling/ >225kBtuh heating | >135kBtuh cooling/ >225kBtuh heating
|  |  | User Input 09: Table 110.2-NI & J; User Input 10: Table 110.2-NI & J |  |  |  | AC, air cooled, split (1 phase) | [6 empty] | >135kBtuh cooling/ >225kBtuh heating | >135kBtuh cooling/ >225kBtuh heating |  |  | >240kBtuh cooling/ <225kBtuh heating | >240kBtuh cooling/ <225kBtuh heating
|  |  | User Input 09: Table 110.2-NI & J; User Input 10: Table 110.2-NI & J |  |  |  | AC, air cooled, split (3 phase) | [6 empty] | >240kBtuh cooling/ <225kBtuh heating | >240kBtuh cooling/ <225kBtuh heating |  |  | >240kBtuh cooling/ >225kBtuh heating | >240kBtuh cooling/ >225kBtuh heating
|  |  | User Input 10: Reset; User Input 11: Add Row | Remove Last |  |  | AC, air cooled, split, space constrained | [6 empty] | >240kBtuh cooling/ >225kBtuh heating | >240kBtuh cooling/ >225kBtuh heating |  |  | >760kBtuh cooling/ <225kBtuh heating | >760kBtuh cooling/ <225kBtuh heating
1 FOOTNOTES: Chilled water plants shall not have more than 300 tons provided by air-cooled chillers. Exceptions may apply per §140.4(j). | [14 empty] | AC, air cooled, package (1 phase) | [6 empty] | >760kBtuh cooling/ <225kBtuh heating | >760kBtuh cooling/ <225kBtuh heating |  |  | >760kBtuh cooling/ >225kBtuh heating | >760kBtuh cooling/ >225kBtuh heating
2 Efficiency required is a minimum when "EER" or "COP" is the Efficiency Unit in column 08. It is also a minimum when "IPLV" is the unit for air-cooled, absorption, and water cooled gas engine chillers. Efficiency required is a maximum when "kW/ton" is the Efficiency Unit and when "IPLV" is the unit for water cooled electrically operated chillers. |  |  | User Input 11: Isolation Dropdown | Temp Reset Dropdown |  |  | AC, air cooled, package (3 phase) | [6 empty] | >760kBtuh cooling/ >225kBtuh heating | >760kBtuh cooling/ >225kBtuh heating
|  | Equipment Type Dropdown | User Input 04: Size Category Dropdown; User Input 05: Leaving Hot Water Temperature; User Input 06: Efficiency Exception Dropdown; User Input 11: Yes | Yes |  |  | AC, air cooled, package, space constrained
|  | Air Cooled: Condenser elec. operated | User Input 04: < 75; User Input 05: Low - 105F; User Input 06: No exception taken; User Input 11: NA: only 1 chiller in plant | NA: ≤ 500 kBtu/hr (41.67 tons) |  |  | AC, air cooled, small duct, high velocity
|  | Air Cooled: w/o condenser elec. operated | User Input 04: ≥ 75 and < 150; User Input 05: Medium - 120F; User Input 06: 1. Electrical service > 600V; User Input 11: NA: chillers in series | NA: Variable Flow Controls |  | Unitary heat pumps (no elec. resistance) | Air cooled, split (1 phase)
|  | Water Cooled: Reciprocating | User Input 04: ≥ 150 and < 300; User Input 05: High - 140F; User Input 06: 2. Heat recovery w/ design capacity > 40% of the design chiller cooling capacity | NA: System serves Healthcare |  |  | Air cooled, split (3 phase)
|  | Water Cooled: Positive displacement | User Input 04: ≥ 300 and < 400; User Input 05: Boost - 140F; User Input 06: 3. Charging energy storage systems w/ charging temperature < 40oF |  |  |  | Air cooled, split, space constrained |  | Last updated Table E-2 on 4.3.2020 from Title 20 Section 1605.1 |  |  |  | From Table B-2 >>> | Room AC, louvered sides | Room AC, no louvers | Room AC, casement only | Room AC, slider & casement | Room AC Heat Pump, louvered sides | Room AC Heat Pump, no louvers
|  | Water Cooled: Centrifugal | User Input 04: ≥ 400 and < 600; User Input 06: 4. 4th (or more) chiller in this building |  |  |  | Air cooled, package (1 phase) | [6 empty] | < 8,000 | < 8,000 | Grey out the cell for this selection | Grey out the cell for this selection | < 20,000 | < 14,000
|  | Air Cooled: Absorption, single effect | User Input 04: ≥ 600; User Input 06: Water -Cooled Centrifugal Chilling Package per Exception 1 to §110.2(a) |  |  |  | Air cooled, package (3 phase) | [6 empty] | >= 8,000 and < 14,000 | >= 8,000 and < 11,000 |  |  | >= 20,000 | >= 14,000
|  | Water Cooled: Absorption, single effect | [12 empty] | Air cooled, package, space constrained | [6 empty] | >= 14,000 and < 20,000 | >= 11,000 and < 14,000
|  | Absorption: Double effect, indirect-fired | [12 empty] | Aircooled, small duct, high velocity | [6 empty] | >= 20,000 and < 28,000 | >= 14,000 and < 20,000
|  | Absorption: Double effect, direct-fired | [19 empty] | >= 28,000 | >= 20,000
Water Cooled: Gas engine
Heat Recovery Chiller - Positive Displacement
Heat Recovery Chiller - Centrifugal
Air-To-Water Source Heat Pump
Water source
Groundwater source
Ground source
[15 empty] | Water source water-to-water | [5 empty] | From Table 110.2-A >> | AC, water cooled | AC, evaporatively cooled | Condensing Units, air cooled | Condensing Units, water cooled | Condensing Units, evaporatively cooled
DX-DOAS Efficiency | [14 empty] | Groundwater source water-to water | [6 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000 | > 135,000
01 |  | 02 | 03 | 04 | 05 |  | 06 | 07 | 08 | [5 empty] | Ground source brine-to-water | [6 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
Name or Item Tag |  | Equipment Type | Qty | Energy Recovery | Rating Condition |  | Rated Efficiencies | Efficiency Unit | Minimum Efficiency | [5 empty] | Air-cooled gas-engine heat pump | [6 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000
[14 empty] | DOAS | DOAS | [6 empty] | > 760,000 | > 760,000
From sizing table above |  | Dropdown to match Table 110.2-H | User Input 04: Dropdown; User Input 05: Dropdown; User Input 08: ISMRE |  |  |  | DX-DOAS
|  |  | User Input 08: ISCOP |  |  | Computer Rm AC Ceiling Mounted
[21 empty] | From Tables C-3, C-4 or 110.2-A, depending on size category >> | AC, air cooled, split (1 phase) | AC, air cooled, split (3 phase) | AC, air cooled, split, space constrained | AC, air cooled, package (1 phase) | AC, air cooled, package (3 phase) | AC, air cooled, package, space constrained | AC, air cooled, small duct, high velocity
[22 empty] | < 45,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[22 empty] | >= 45,000 and < 65,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
[22 empty] | >= 65,000 and < 135,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
|  | Equipment Type Dropdown | User Input 04: Energy Recovery Dropdown; User Input 05: Rating Condition Dropdown | [10 empty] | >= 135,000 and < 240,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000
|  | Air Cooled | User Input 04: Yes; User Input 05: Cooling Tower Condenser Water | [10 empty] | >= 240,000 and < 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000
|  | Air Source Heat Pump | User Input 04: No; User Input 05: Chilled Water | [10 empty] | >= 760,000
Water Cooled
|  | Water Source Heat Pump | User Input 05: Rating Condition Dropdown | [10 empty] | Water source | Groundwater source | Ground source | Water source water-to-water | Groundwater source water-to water | Ground source brine-to-water
|  |  | User Input 05: Ground Source Closed & Open Loop | [10 empty] | > 65,000 and < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000
|  |  | User Input 05: Ground Water Source | [10 empty] | > 135,000 and < 240,000
Water Source
[22 empty] | Air-cooled gas-engine heat pump | Air cooled, split (1 phase) | Air cooled, split (3 phase) | Air cooled, split, space constrained | Air cooled, package (1 phase) | Air cooled, package (3 phase) | Air cooled, package, space constrained | Air cooled, small duct, high velocity
[22 empty] | Grey out the cell for this selection | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
Dual Fuel Heat Pump | [22 empty] | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | [12 empty] | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
Name or Item Tag | Equipment Category | Equipment Type | User Input 03: Size Category (Btu/h); User Input 04: Heating Mode; User Input 08: Cooling Mode | [11 empty] | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000
|  |  |  | Rating Condition (oF) | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency
From Eq Table above | Dropdown | Dropdown | Dropdown | Dropdown | Lookup based on heat pump system type selected | Always appropriate HP values |  | Unit from efficiency tables auto populates here based on size category (col 02) | Values from Tables 110.2-A, B, C, E, HG, I, J & T20 Tables | [12 empty] | Air Cooled with free air discharge condenser, ducted | Air Cooled with free air discharge condenser, nonducted | Air Cooled with free air discharge condenser with fluid economizer, ducted | Air Cooled with free air discharge condenser with fluid economizer, nonducted | Air cooled with ducted condenser, ducted | Air cooled with ducted condenser, nonducted | Air cooled with fluid economizer and ducted condenser, ducted | Air cooled with fluid economizer and ducted condenser, nonducted
|  |  | User Input 08: Unit from efficiency tables auto populates here based on size category (col 02); User Input 09: Values from Tables 110.2-A, B, C, E, HG, I, J & T20 Tables | [10 empty] | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h
| Always = Furnace/Unit Heater | Dropdown | Dropdown | Always Blank/Gray | Dropdown | Always appropriate furnace value |  | Always Blank/Gray | Always Blank/Gray | Always Blank/Gray | [11 empty] | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h
[22 empty] | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h
| HP Equipment Category Dropdown | Equipment Type Dropdown | User Input 03: Size Category Dropdown; User Input 04: Rating Condition Dropdown; User Input 05: Unit Dropdown | [10 empty] | Water Cooled, Ducted | Water Cooled, nonducted | Water cooled with fluid economizer, ducted | Water cooled with fluid economizer, nonducted | Glycol cooled, ducted | Glycol cooled, nonducted | Glycol cooled with fluid economizer, ducted | Glycol cooled with fluid economizer, nonducted
| Unitary Heat Pump | Provide the appropriate equipment type dropdowns based on the equipment category chosen in 02. | User Input 03: See tables in column AF of this tab for custom drop downs.; User Input 04: See choices in notes in column AF rows 51 & 76 of this tab.; User Input 05: COP | [10 empty] | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h
| Unitary Heat Pump (no elec resistance) |  | User Input 05: AFUE | [10 empty] | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h
[22 empty] | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | bar: User Input 05
Ec
HSPF
Heat Rejection Equipment (Cooling Towers, Condensers, Waterside Economizers) Efficiency and Controls
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12
Name or Item Tag | Equipment Type1 | Qty | Rating Condition (oF) | Rated Performance | Minimum Required Performance per Table 110.2-E, §140.4(h)5 & §170.2(c)fv | Performance Unit | Fan Speed Control §140.4(h)1 | Tower Flow Turndown §140.4(h)2 | Fan Control in Multiple Cell Equipment §140.4(h)4 | Economizer Controls §140.4(e) | Condenser Water Temp Reset Controls
| Dropdown to match Table 110.2-FE |  | Dropdown |  | Value from table |  | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
1 FOOTNOTES: Centrifugal fan open-circuit towers are not allowed for rated capacities > 900 gpm at 95oF condenser water return, 85oF condenser water supply and 75oF outdoor wet-bulb temperature. Exceptions may apply per §140.4(h)4. | [13 empty] | Link to 2022 Table 110.2-F
| Equipment Type Dropdown |  | User Input 07: Fan Speed Control Dropdown; User Input 08: Tower Flow Turndown Dropdown; User Input 09: Fan Control Dropdown; User Input 10: Economizer Control Dropdown; User Input 11: Cond. Water Temp Reset Controls Dropdown |  |  | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1102mandatoryrequirementsforspaceconditioningequipment.htm#table1102fperformancerequirementsforheatrejectionequipment.htm
| Axial fan open-circuit tower, CW loop in CHW plant >= 900gpm |  | Rating Condition Dropdown |  |  |  | Yes | Yes | Yes | Designed per §140.4(e) | Yes
| Replacement axial fan open-circuit tower, CW loop in CHW plant >= 900gpm |  | User Input 03: 165oF entering gas temp 105oF condensing temp 75oF entering air wb"; User Input 07: NA: Fan motor < 7.5hp (5.6kW); User Input 08: NA: Single condenser water pump; User Input 09: NA: Not multiple cell; User Input 11: No
| Propeller/ axial fan open-circuit cooling tower |  | User Input 03: 140oF entering gas temp 96.3oF condensing temp 75oF entering air wb"; User Input 07: NA: Integral to other equip.; User Input 08: NA: Not open-circuit tower; User Input 09: NA: No variable speed drives
| Propeller/ axial fan closed-circuit cooling tower |  | User Input 07: NA: Cond. fans serving > 1 refrigerant circuits
| Centrifugal fan open-circuit cooling tower |  | User Input 07: NA: Cond. fans serving flooded cond.
| Centrifugal fan closed-circuit cooling tower |  | User Input 07: NA: Mult. fans & lead fans meet req.
Propeller/ axial fan evaporative condensers
Centrifugal fan evaporative condensers
Air cooled condensers
Waterside Economizer
Propeller/ axial fan dry cooler
Electric Resistance Heating
01 | 02 | 03 | User Input 03: 04
Name or Item Tag | Equipment Description | Output Capacity (kW) | User Input 03: Applicable Exception to §140.4(g) Allowing Electric Resistance Heating
| dropdown |  | User Input 03: dropdown
Elec Resistance Dropdown
| Dropdown |  | User Input 03: Exception 1: Supplement to a heating system in which at least 60% of the annual energy requirement is supplied by site-solar or recovered energy.
| Baseboard |  | User Input 03: Exception 2: Supplement to a heat pump heating system and the heating capacity of the heat pump is more than 75% of the design heating load calculated in accordance with §140.4.
| Under-mat |  | User Input 03: Exception 3: Total capacity of electric-resistance heating systems serving the entire building is less than 10% of the total design output capacity of all heating equipment serving the entire building.
| Other |  | User Input 03: Exception 4: Total capacity of electric-resistance heating systems serving the entire building, excluding those allowed under Exception 2, is no more than 3 kW.
Exception 5: Serving an entire building that is not hotel/motel and has a conditioned floor area no greater than 5,000 ft2, has no mechanical cooling and is in an area without natural gas access.
NA: Alteration, replacement of existing electric resistance heating system.
Exempt: Supplemental electric resistance heating systems complying with Section 140.4(a)3C
fasd
Mechanical Heat Recovery | bar: User Input 03 to User Input 09
01 | 02 | 03 | User Input 03: 04; User Input 04: 05; User Input 05: 06; User Input 06: 07
Name or Item Tag | Coincident Peak Cooling Load of All High Load Spaces | Design Capacity of All Mechanical Cooling Systems2 | User Input 03: Design Capacity of All Service Water Heating Systems1; User Input 04: Design Capacity for all space heating systems; User Input 05: Simultaneous Mechanical Heat Recovery; User Input 06: Heat Recovery Systems Shall: - Transferring the lesser of the following from spaces in cooling to spaces in heating: - 25% of thje peak heat rejection of the cooling system - 25% of design capacity of all service water heating systems + design capacity of all space heating systems - Heat or preheat the service water heating to the smaller of: - 30% of the peak heat rejection of the cooling system; or - 30% of design capacity of all service water heating systems
| user input | user input | User Input 03: user input; User Input 04: user input
Footnote 1: Excluding systems expected to operate less than 5 hours per week | bar: User Input 03 to User Input 05
Footnote 2: If the design includes capacity for future cooling systems, then assume 20% of future systems serve high load spaces | bar: User Input 03 to User Input 05
Note on F11: 12/9/24 If selected, ignore the custom dropdown options for Equipment Category 02 and Equipment Type 03
Note on C15: 3.3.22 If Multi-zone or Dwelling unit is selected, 03-06 are gray/blank
Note on D15: 3.3.22 If Alteration is selected, 04-07 blank/grayed out
Note on E21: Ben Lalor: If other is selected 06 blank/grayed out
Note on E32: 2020 Update: F.05, F.06, and F.07 should Trigger when: F.02 = - Sm. Commercal AC - Unitary Heat Pump - Furnace/Unit Heater - Furnace + AC OR F.03 = - PTHP newly constructed or newly conditioned - PTHP replacements - SPVHP - SPVHP nonweatherized space constrained - VRF heat pump, air cooled - VRF water source - VRF groundwater source - VRF ground source OTHERWISE F.05, F.06, F.07 should be grayed out
Note on H32: 2020 UPDATE: F.08 and F.09 should trigger when: F.02 = - Unitary AC/Condenser - Heatpump + AC - Unitary Heat Pump - Computer Room AC - Room AC/HP - Furnace + AC - PTAC/PTHP - SPVAC/SPVHP - VRF OTHERWISE F.08 and F.09 should be grayed out
Note on B34: 11/12/24 If 03 above == Multi-zone, 04 == alteration or addition or 06 has been selected, If 04 == alteration or addition user has the options to select any of the equipment categories F.03 Else If F.03 SCSI == "Individual Dwelling unit(s)" AND A.02 = 2-15 Equipment Category 02 limited to - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else If F.03 SCSI == ""Individual Dwelling unit(s)" AND A.02 = 1 OR 16 Equipment Type 03 limited to - Unitary Heat Pump - DUAL FUEL HEAT PUMP Else If F.03 SCSI == Single Zone AND A.02 = 2-15 AND space type = retail OR grocery AND rated cooling capacity 09 <=240 Then equipment type 03 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else If F.03 SCSI == Single Zone AND A.02 = 1 OR 16 AND space type = retail OR grocery AND rated cooling capacity 09 <=65 Then equipment type 03 limited to the following options: - Furnace + AC Else If F.03 SCSI == Single Zone AND A.02 = 1 OR 16 AND space type = retail OR grocery AND rated cooling capacity 09 >65 AND <240 Then equipment type 03 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP Else If F.03 SCSI == Single Zone AND climate zone = 2-15 AND space type = school AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else If F.03 SCSI == Single Zone AND climate zone = 1 OR 16 AND space type = school AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP Else If F.03 SCSI == Single Zone AND climate zone = 1-15 AND space type = office OR financial institution OR library AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else If F.03 SCSI == Single Zone AND climate zone = 16 AND space type = office OR financial institution OR library AND rated cooling capacity 09 <=65 Then equipment type 02 limited to the following options: - Furnace + AC Else If F.03 SCSI == Single Zone AND climate zone = 16 AND space type = office OR financial institution OR library AND rated cooling capacity 09 > 65 AND <=225 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP Else If F.03 SCSI == Single Zone AND space type = office spaces in warehouses AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else if F.03 SCSI == multizone AND F.05 FSCI == office OR (F.05 == school And A.02 = And F.04 == New And A.04 + A.05 <= 150,000 And A.06 < 6 Equipment type in 02 limited to the following options (NOTE - options listed below are non-reported fields in the user interface for the VCA. The reported value is listed in the options and is one of the enumerations listed shown in the mock-up dropdown) Option 1 - VRF with refrigerant loop heat recovery and DOAS - Reported values: - Variable Refrigerant Flow (must select HP option in F.03 Equipment Type, VRF AC not allowed) AND - Dedicated Outdoor Air System Option 2 - Air to water heat pump with Four pipe fan coil and DOAS - Reported Values: - Air To Water Heat Pump in Chiller & AWHP Table AND - Dedicated Outdoor Air System Option 3 (not an option for school buildings in climate zones 1, 3, 5, 6, 7) - VAV with heating provided by air to water heat pump - Reported Value: - Air To Water Heat Pump in Chiller and AWHP Table Option 4 - Dual Fan Dual Duct - reported value is any of the following: - Unitary Heat Pump - Unitary Heat Pump (no elec resistance) PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP ELSE choose from the full list of equipment categories
Note on AI41: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.1" in the upper row & "13.9" in the lower row
Note on AJ41: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.1" in the upper row & "12.3" in the lower row
Note on AK41: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.5" in the upper row & "11.8" in the lower row
Note on AL41: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AM41: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AI42: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.5" in the upper row & "13.9" in the lower row
Note on AJ42: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.0" in the upper row & "12.2" in the lower row
Note on AI43: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.4" in the upper row & "13.6" in the lower row
Note on AJ43: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "12.1" in the lower row
Note on AI44: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.2" in the upper row & "13.5" in the lower row
Note on AJ44: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.7" in the upper row & "11.9" in the lower row
Note on B53: 3.14.22 When DFHP is selected, gray equipment type 03 and transfer system to DFHP efficiency table. They still need to complete 04-11
Note on A57: Sally Blair: This table only shows up if any of the equip. categories OTHER THAN "PTAC/PTHP" is selected in Eq Sizing Table above. Otherwise, user shouldn't see this at all (including title).
Note on D58: October 2019 Update: Trigger F.04/5/6 if F.05 >=1, otherwise they are gray
Note on I58: Trigger F.07/8/9 if F.05 >=1 , otherwise they are gray
Note on A61: 6.3.22 Anything designated as one of the follwing does not transfer to this table. Everything else does. PTAC/PTHP DX-DOAS Dual Fuel Heat Pump
Note on C61: Sally Blair: This is only a dropdown if column 03 in Dry System Equipment Sizing table is any of the following: - "VRF heat pump, air cooled" - "Air cooled, split" - "Air cooled, split, space constrained" - "Air cooled, packaged" - "Air cooled, packaged, space constrained" Otherwise this cell greys out.
Note on E61: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on G61: Sally Blair: If nothing is entered in Column 10 above in the Sizing Table, columns 03-06 here grey out.
Note on H61: 12/9/24 = "Required" if multizone option 1 is selected in F.02, otherwise = BlankGrayedOut
Note on K61: Sally Blair: If nothing is entered in Column 11 above in the Sizing Table, columns 07-09 here grey out.
Note on AI62: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "FEDERAL MINIMUM14.0" in the upper row & "12.2" in the lower row. From Table C-3
Note on AJ62: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AK62: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AL62: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.0" in the lower row. From Table C-3
Note on AM62: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AN62: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AO62: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AI63: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.7" in the lower row. From Table C-3
Note on AJ63: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AK63: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AL63: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AM63: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AN63: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on D64: Sally Blair: This needs to be a custom dropdown which only includes the unit relevant to the equipment type chosen. There's only one instance where they get to choose- Warm Air Central Furnace, Gas fired.
Note on AI64: 12/12/24 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "FEDERAL MINIMUM14.8" in the lower row.
Note on AJ64: 12/12/24 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "FEDERAL MINIMUM14.8" in the lower row.
Note on AK64: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AL64: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AM64: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AN64: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on C65: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These references are old
Note on AI65: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AJ65: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AK65: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AL65: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AM65: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AN65: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AI66: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AJ66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AK66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AL66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AM66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AN66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AI67: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AI72: Column 07 upper should be SEER & Column 08 upper should be "14.0" & column 04 should be HSPF & column 05 should be "8.2" From Table C-4
Note on AJ72: Column 07 upper should be SEER & Column 08 upper should be "14.0" & column 04 should be HSPF & column 05 should be "8.0" From Table C-4
Note on AI75: Cooling Mode Efficiency = 12.2 EER Heating Mode Efficiency = 4.3 COP
Note on AJ75: Sally Blair: this would result in the Cooling Mode eff. Of 18.0 EER & the heating mode eff. Of 3.7 COP.
Note on AK75: Sally Blair: this would result in the Cooling Mode eff. Of 14.1 EER & the heating mode eff. Of 3.2 COP.
Note on AL75: Sally Blair: this would result in the Cooling Mode eff. Of 10.6 EER & the heating mode eff. Of 3.7 COP.
Note on AM75: Sally Blair: this would result in the Cooling Mode eff. Of 16.3 EER & the heating mode eff. Of 3.1 COP.
Note on AN75: Sally Blair: this would result in the Cooling Mode eff. Of 12.1 EER & the heating mode eff. Of 2.5 COP.
Note on A76: Sally Blair: This table only shows up if "PTAC/PTHP" is selected in Eq Sizing Table above. Otherwise, user shouldn't see this at all (including title).
Note on AI76: In Table 110.2-B, this would result in the Cooling Mode eff. Of 13.0 EER & the heating mode eff. Of 4.3 COP.
Note on AI77: Table 110.2-B, this would result in NO Cooling Mode eff. (ie, so grey that column out) & the heating mode eff. Of 2.90 COP.
Note on AG80: 2019 Update: For heating mode only, the dropdown choices in light purple would trigger two choices in the drop down for rating condition in column 03 of the Dry System Equipment Efficiency (other than PTAC and PTHP) subtable: - 47oFdb/43oFwb OSA - 17oFdb/15oFwb OSA Otherwise, column 03 stays grey & blank
Note on AI80: 2019 Update: For all sizes, if selected column 04 dropdown is "COP" and column 05 is "0.72" and column 07 is "COP" in the upper row and blank in the lower row & column 08 is "0.60" in the upper row & blank in the lower row.
Note on AJ80: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Tabe C-3.
Note on AK80: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AL80: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AM80: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-3
Note on AN80: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AO80: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AP80: NEEDS TO BE UPDATED IN FORM & SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "7.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. Table C-3
Note on A81: Sally Blair: Anything designated as "PTAC/PTHP" transfers to this table. Everything else does not.
Note on C81: October 2019 Updates: Calculated field: PTHP: Newly constructed or newly conditioned- if column 02 < 7 = 3.3 if column 02 >=7 and <= 15 = 3.7 - (0.052 x column02) if column 02 > 15 = 2.9 PTHP: replacement- if column 02 < 7 = 2.7 if column 02 >=7 and <= 15 = 2.9 - (0.026 x column02) if column 02 > 15 = 2.5
Note on D81: Sally Blair: If nothing is entered in Column 10 above in the Sizing Table, columns 02-04 here grey out.
Note on F81: Ocotber 2019 Updates: Calculated field: PTHP: Newly constructed or newly conditioned- if column 05 < 7 = 11.9 if column 05 >=7 and <= 15 = 14 - (0.3 x column05) if column 05 > 15 = 9.5 PTHP: replacement- if column 05 < 7 = 9.3 if column 05 >=7 and <= 15 = 10.8 - (0.213 x column05) if column 05 > 15 = 7.6 PTAC: Newly constructed or newly conditioned- if column 05 < 7 = 11.9 if column 05 >=7 and <= 15 = 14 - (0.3 x column05) if column 05 > 15 = 9.5 PTAC: replacement- if column 05 < 7 = 9.4 if column 05 >=7 and <= 15 = 10.9 - (0.213 x column05) if column 05 > 15 = 7.7
Note on G81: Sally Blair: If nothing is entered in Column 11 above in the Sizing Table, columns 05-07 here grey out.
Note on AJ81: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AK81: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AL81: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AM81: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AN81: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AO81: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AJ82: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AK82: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AL82: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AM82: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AN82: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AO82: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AJ83: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AK83: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AL83: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AM83: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AN83: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AO83: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AI92: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.0"
Note on AJ92: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.0" & column 04 should be COP & column 05 should be "3.3"
Note on K96: 6.8.22 = 90% if sum of rated input capacity >=1,000,000 excluding individual boilers < 300,000 Else gray/blank
Note on D97: 11/18/22 if sum of rated input capacity >=1,000,000 excluding individual boilers < 100,000 System Efficiency = (sum (Rated Efficiency x input capacity))/ total input capacity of boilers > between 1million and 10 million btu/h else = gray/blank
Note on I97: 6.3.22 Always = 90% if not grayed out
Note on AI99: 11/11/24 Column 07 upper should be SEER & Column 08 upper should be "13.4"
Note on AI100: 11/11/24: Column 07 upper should be EER & Column 08 upper should be "10.5" Column 07 lower should be IEER & Column 08 lower should be "15.5"
Note on I101: Sally Blair: If NA selected AND Col 03 Qty is greater than 1, Table D needs to return Item #6 "Table F indicates more than one boiler" error on the Table D tab.
Note on J101: Sally Blair: If "NA: ≤ 500,000 Btu/h" selected AND rated capacity is EITHER >500,000 to 2,500,000 OR > 2,500,000 in Col 04, Table D needs to return item #7 "Table F indicates a boiler with" error on the Table D tab.
Note on AI101: 11/11/24: Column 07 upper should be EER & Column 08 upper should be "10.3" Column 07 lower should be IEER & Column 08 lower should be "14.9"
Note on AI102: 11/11/24: Column 07 upper should be EER & Column 08 upper should be "9.5" Column 07 lower should be IEER & Column 08 lower should be "13.9"
Note on AI104: Sally Blair: For heating mode only, the 3 selections highlighted in pink would trigger two choices in the drop down for rating condition: - 47oFdb/43oFwb OSA - 17oFdb/15oFwb OSA
Note on AI105: 11/11/24: If chosen, column 07 upper is "SEER" and column 07 lower is blank. Column 08 upper is "13.4" and column 08 lower is blank. AND column 04 is "HSPF" dropdown choice and column 05 is "7.5"
Note on AJ105: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "12.0" and column 08 lower is "16.0". AND column 04 is "COP" dropdown choice and column 05 is "4.3"
Note on AK105: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "16.2" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.6"
Note on AL105: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "13.4" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.1"
Note on AI106: 11/11/24: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.3" and column 08 lower is "14.6". AND column 04 is "COP" dropdown choice and column 05 is: "3.3" if column 02 is "47oFdb/43oFwb OSA" "2.25" if column 02 is "17oFdb/15oFwb OSA"
Note on AJ106: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "12.0" and column 08 lower is "16.0". AND column 04 is "COP" dropdown choice and column 05 is "4.3"
Note on AK106: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "13.8" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.3"
Note on AL106: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "11.0" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "2.8"
Note on AI107: 11/11/24: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "9.9" and column 08 lower is "13.9". AND column 04 is "COP" dropdown choice and column 05 is: "3.2" if column 02 is "47oFdb/43oFwb OSA" "2.05" if column 02 is "17oFdb/15oFwb OSA"
Note on AJ107: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.0" and column 08 lower is "14.0". AND column 04 is "COP" dropdown choice and column 05 is "4.0"
Note on O108: 2019 Update: Remove these two dropdown choices from "Furnace + AC" & only use with "Furnace/ Unit heater"
Note on AI108: 11/11/24: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "9.1" and column 08 lower is "12.7". AND column 04 is "COP" dropdown choice and column 05 is: "3.2" if column 02 is "47oFdb/43oFwb OSA" "2.05" if column 02 is "17oFdb/15oFwb OSA"
Note on AJ108: 2019 Update: New size category for 2019. If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.0" and column 08 lower is "12.0". AND column column 04 is "COP" dropdown choice and column 05 is "3.9"
Note on AI111: 6.29.21 This is the only instance where the "Efficiency Unit" under heating mode needs to be a dropdown. The two choices are: - AFUE - Et If "AFUE" chosen, column 05 is "0.78" If "Et" chosen, column 05 is "0.81"
Note on AJ111: Sally Blair: If chosen, column 04 is "Ec" dropdown choice and column 05 is "0.80"
Note on AK111: Sally Blair: If chosen, column 04 is "Ec" dropdown choice and column 05 is "0.80"
Note on AI112: 6.29.21 If chosen, column 04 is "Et" dropdown choice and column 05 is "0.82"
Note on AI115: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.81"
Note on AJ115: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.80"
Note on AI118: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.75"
Note on AJ118: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.65"
Note on AK118: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.57"
Note on AL118: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.61"
Note on AI119: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.76"
Note on AJ119: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.66"
Note on AK119: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.58"
Note on AL119: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.66"
Note on AJ120: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.67"
Note on AL120: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.67"
Note on AL121: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.68"
Note on AI123: 2019 Update: Divided all of these choices into "downflow" and "upflow"
Note on AI124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.2" in the upper row & blank in the lower row.
Note on AJ124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.09" in the upper row & blank in the lower row.
Note on AK124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.6" in the upper row & blank in the lower row.
Note on AL124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.49" in the upper row & blank in the lower row.
Note on AM124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.55" in the upper row & blank in the lower row.
Note on AN124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.44" in the upper row & blank in the lower row.
Note on AO124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.5" in the upper row & blank in the lower row.
Note on AP124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.39" in the upper row & blank in the lower row.
Note on AQ124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.45" in the upper row & blank in the lower row.
Note on AR124: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.34" in the upper row & blank in the lower row.
Note on AI125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.1" in the upper row & blank in the lower row.
Note on AJ125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AK125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.5" in the upper row & blank in the lower row.
Note on AL125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.39" in the upper row & blank in the lower row.
Note on AM125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.45" in the upper row & blank in the lower row.
Note on AN125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.34" in the upper row & blank in the lower row.
Note on AO125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.15" in the upper row & blank in the lower row.
Note on AP125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.04" in the upper row & blank in the lower row.
Note on AQ125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.10" in the upper row & blank in the lower row.
Note on AR125: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AI126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.9" in the upper row & blank in the lower row.
Note on AJ126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.79" in the upper row & blank in the lower row.
Note on AK126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.4" in the upper row & blank in the lower row.
Note on AL126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.29" in the upper row & blank in the lower row.
Note on AM126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.35" in the upper row & blank in the lower row.
Note on AN126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.24" in the upper row & blank in the lower row.
Note on AO126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.10" in the upper row & blank in the lower row.
Note on AP126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AQ126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.05" in the upper row & blank in the lower row.
Note on AR126: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.94" in the upper row & blank in the lower row.
Note on AI132: 2019 Update: Taking "/single package" out of this choice
Note on AJ132: 01.09.20 Update: Completely new set of dropdowns and efficiencies.
Note on AN132: 2019 Update: Taking out "split/" in both of these choices.
Note on AI133: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AJ133: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AI134: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AJ134: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AM134: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AN134: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AI135: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AJ135: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AM135: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AN135: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on G137: 7/5/23 If 02 == air source heat pump or heat recovery chiller, this field is BlankGrayedOut
Note on AI137: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AJ137: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AN137: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI138: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AJ138: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AN138: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11.2" F.08 Lower Row = "14.8"
Note on F139: 6/22/23 Blank/gray unless 02 == Heat Recovery Chiller or Air Source Heat Pump
Note on J139: 11/11/24 Ben, if Path B says "NA", then lets use Path A values to document MM. They restructured the Heat Pump and Heat Recovery Chiller Table in 110.2. The restructure isn't in it self supposed to be substantive, but the values have also changed in addition to the restructure
Note on K139: 11/11/24: Ben, if Path B says "NA", then lets use Path A values to document MM. Units have changed for 2025
Note on N139: 12/11/24 = "Four Pipe Fan Coil" If F02 = AWHP in connection with system that selected option 2 = "VAV" if F02 = AWHP in connection with system that selected option 3 else BlankGrayedOut
Note on AI139: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AJ139: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AM139: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AN139: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on I140: Sally Blair: If there is only one value required by Table 110.2-D (ex. COP), then these three cells in 06/07/08 grey out.
Note on J140: 11/11/24 Ben, if Path B says "NA", then lets use Path A values to document MM. They restructured the Heat Pump and Heat Recovery Chiller Table in 110.2. The restructure isn't in it self supposed to be substantive, but the values have also changed in addition to the restructure
Note on K140: 11/11/24: Ben, if Path B says "NA", then lets use Path A values to document MM. Units have changed for 2025
Note on AI140: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AJ140: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AM140: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11" F.08 Lower Row = "14.2"
Note on AN140: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11" F.08 Lower Row = "14.2"
Note on AI141: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AJ141: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AM141: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AN141: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI142: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AJ142: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AM142: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "10" F.08 Lower Row = "13.2"
Note on AN142: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "10" F.08 Lower Row = "13.2"
Note on AI143: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AJ143: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AM143: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AN143: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI144: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AJ144: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AM144: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "9.7" F.08 Lower Row = "12.5"
Note on AI145: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AJ145: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on L147: Sally Blair: If NA selected AND Col 03 Qty is greater than 1, Table D needs to return the item #8 "Table F indicates more than one chiller" error on the Table D tab.
Note on M149: 2019 Update: Added new NA choice for new exception for Healthcare facilities.
Note on AI150: 2019 Update: These are new categories.
Note on AI151: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "11.0" in the upper row & blank in the lower row.
Note on AJ151: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.0" in the upper row & blank in the lower row.
Note on AK151: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.5" in the upper row & blank in the lower row.
Note on AL151: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.4" in the upper row & blank in the lower row.
Note on AM151: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.8" in the upper row & blank in the lower row.
Note on AN151: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AI152: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.9" in the upper row & blank in the lower row.
Note on AJ152: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.6" in the upper row & blank in the lower row.
Note on AM152: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AN152: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "8.7" in the upper row & blank in the lower row.
Note on AI153: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.7" in the upper row & blank in the lower row.
Note on AJ153: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.5" in the upper row & blank in the lower row.
Note on AI154: 2019 UPdate: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.4" in the upper row & blank in the lower row.
Note on AJ154: 2019 UPdate: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AI155: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.0" in the upper row & blank in the lower row.
Note on AJ155: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.4" in the upper row & blank in the lower row.
Note on AI164: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "13.7" in the lower row
Note on AJ164: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "12.1" in the lower row
Note on AK164: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.5" in the upper row & "11.8" in the lower row
Note on AL164: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AM164: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AI165: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.3" in the upper row & "13.7" in the lower row
Note on AJ165: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.8" in the upper row & "12.0" in the lower row
Note on AI166: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.2" in the upper row & "13.4" in the lower row
Note on AJ166: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.7" in the upper row & "11.9" in the lower row
Note on P167: 3.24.22 If DOAS is selectedd 04-11 gray out and no efficiency table is triggered.
Note on AI167: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.0" in the upper row & "13.3" in the lower row
Note on AJ167: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.5" in the upper row & "11.7" in the lower row
Note on F168: 9.20.22 = gray/blank when: 02 = air cooled or air source heat pump Otherwise see custom dropdown scenarios below.
Note on J168: 11/11/24 Lookup based on Table 110.2-H 2025 code updated the values in 110.2-H
Note on P168: 3.24.22 If DX-DOAS is selected the DX-DOAS table is triggered
Note on H169: 6.1.22: col 06 & 08 ISCOP row grey out when "Air cooled" OR "Water cooled" selected in col02.
Note on AI170: 2019 Update: These are all new categories for "Unitary AC/ Condensers" so these sizing dropdowns need to be added.
Note on AI171: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "12.2" in the lower row. From Table C-3
Note on AJ171: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AK171: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AL171: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.0" in the lower row. From Table C-3
Note on AM171: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AN171: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AO171: NEEDS TO BE UPDATED IN FORM AND SCHEMA If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AI172: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.7" in the lower row. From Table C-3
Note on AJ172: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AK172: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AL172: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AM172: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AN172: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AI173: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AJ173: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AK173: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AL173: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AM173: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AN173: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on F174: 11/11/24 Custom Dropdown when 02=Water Cooled Chilled Water category was removed from Table 110.2-H so this dropdown is no longer needed
Note on AI174: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AJ174: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AK174: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AL174: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AM174: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AN174: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AI175: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AJ175: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AK175: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AL175: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AM175: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AN175: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AI176: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on F178: 3.14.22 Custom Dropdown when 02=Water Source Heat Pump
Note on AI179: Added 6/15/20: Ben, in Table 110.2-B, this would result in the Cooling Mode eff. Of 12.8 EER & the heating mode eff. Of 4.3 COP.
Note on AJ179: Sally Blair: this would result in the Cooling Mode eff. Of 17.8 EER & the heating mode eff. Of 3.7 COP.
Note on AK179: Added 6/15/20: this would result in the Cooling Mode eff. Of 13.9 EER & the heating mode eff. Of 3.2 COP.
Note on AL179: Added 6/15/20: this would result in the Cooling Mode eff. Of 10.4 EER & the heating mode eff. Of 3.7 COP.
Note on AM179: Added 6/15/20: this would result in the Cooling Mode eff. Of 16.1 EER & the heating mode eff. Of 3.1 COP.
Note on AN179: Added 6/15/20: this would result in the Cooling Mode eff. Of 11.9 EER & the heating mode eff. Of 2.5 COP.
Note on AI180: Sally Blair: Ben, in Table 110.2-B, this would result in NO Cooling Mode eff. (ie, so grey that column out) & the heating mode eff. Of 2.90 COP.
Note on AI184: 2019 Update: For all sizes, if selected column 04 dropdown is "COP" and column 05 is "0.72" and column 07 is "COP" in the upper row and blank in the lower row & column 08 is "0.60" in the upper row & blank in the lower row.
Note on AJ184: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Tabe C-3.
Note on AK184: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AL184: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AM184: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-3
Note on AN184: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AO184: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AP184: NEEDS TO BE UPDATED IN FORM & SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "7.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. Table C-3
Note on A185: 3.14.22 This table is triggered when Dual Fuel Heat Pump is selected in System Sizing Table above
Note on AJ185: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AK185: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AL185: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AM185: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AN185: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AO185: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AJ186: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AK186: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AL186: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AM186: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AN186: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AO186: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AJ187: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AK187: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AL187: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AM187: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AN187: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AO187: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on A189: 3.14.22 Bring in system name for DFHP systems
Note on E189: Sally Blair: This is only a dropdown if column 03 in Dry System Equipment Sizing table is any of the following: - "VRF heat pump, air cooled" - "Air cooled, split" - "Air cooled, split, space constrained" - "Air cooled, packaged" - "Air cooled, packaged, space constrained" Otherwise this cell greys out.
Note on G189: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on AI190: 6.3.22 Blank/Gray
Note on AJ190: 6.3.22 2.08 COP
Note on AK190: 6.3.22 2.01 COP
Note on AL190: 6.3.22 2.04 COP
Note on AM190: 6.3.22 1.86 COP
Note on AN190: 6.3.22 1.89 COP
Note on AO190: 6.3.22 1.82 COP
Note on AP190: 6.3.22 1.85 COP
Note on G191: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on AI191: 6.3.22 2.02 COP
Note on AJ191: 6.3.22 2.05 COP
Note on AK191: 6.3.22 1.97 COP
Note on AL191: 6.3.22 2.00 COP
Note on AM191: 6.3.22 1.83 COP
Note on AN191: 6.3.22 1.86 COP
Note on AO191: 6.3.22 1.78 COP
Note on AP191: 6.3.22 1.81 COP
Note on AI192: 6.3.22 1.92 COP
Note on AJ192: 6.3.22 1.94 COP
Note on AK192: 6.3.22 1.87 COP
Note on AL192: 6.3.22 1.89 COP
Note on AM192: 6.3.22 1.73 COP
Note on AN192: 6.3.22 1.75 COP
Note on AO192: 6.3.22 1.68 COP
Note on AP192: 6.3.22 1.70 COP
Note on F194: Sally Blair: This needs to be a custom dropdown which only includes the unit relevant to the equipment type chosen. There's only one instance where they get to choose- Warm Air Central Furnace, Gas fired.
Note on AI195: 6.3.22 2.38 COP
Note on AJ195: 6.3.22 2.41 COP
Note on AK195: 6.3.22 2.33 COP
Note on AL195: 6.3.22 2.36 COP
Note on AM195: 6.3.22 1.97 COP
Note on AN195: 6.3.22 2.00 COP
Note on AO195: 6.3.22 1.92 COP
Note on AP195: 6.3.22 1.95 COP
Note on AI196: 6.3.22 2.38 COP
Note on AJ196: 6.3.22 2.31 COP
Note on AK196: 6.3.22 2.23 COP
Note on AL196: 6.3.22 2.26 COP
Note on AM196: 6.3.22 1.93 COP
Note on AN196: 6.3.22 1.98 COP
Note on AO196: 6.3.22 1.88 COP
Note on AP196: 6.3.22 1.93 COP
Note on AI197: 6.3.22 2.18 COP
Note on AJ197: 6.3.22 2.20 COP
Note on AK197: 6.3.22 2.13 COP
Note on AL197: 6.3.22 2.16 COP
Note on AM197: 6.3.22 1.78 COP
Note on AN197: 6.3.22 1.81 COP
Note on AO197: 6.3.22 1.73 COP
Note on AP197: 6.3.22 1.76 COP
Note on F217: 6.1.22: Need to add new value for >=4.5 gpm/hp for Propeller/axial fan dry cooler in col 02.
Note on D219: Sally Blair: Only open for user selection if one of the (2) evaporative condenser options are selected in 02. Otherwise, grey this column out.
Note on F219: 12/11/24 For user selection of "Axial fan open-circuit tower, CW loop in CHW plant >= 900gpm" in F02 & 2-15 in A02, this = 42.1 in CZ1, 70 in CZ2, 4, 5, 12, 60 in CZ3, 11, 14, 60 in CZ6-10, 13, 15 For user selection of "Axial fan open-circuit tower, CW loop in CHW plant >= 900gpm" in 02 & 1 or 16 in A02, this = "42.1". For user selection of "Replacement axial fan open-circuit tower, CW loop in CHW plant >= 900gpm" this needs to be "42.1"
Note on I219: Sally Blair: Grey out if anything other than open-circuit towers is selected in 02.
Note on K219: Sally Blair: Grey out if anything other than Waterside Economizer selected in 02.
Note on L219: Sally Blair: grey out if "Air cooled condenser" is selected in column 02
Note on B231: Updated 9.29.20: If Waterside Economizer chosen, grey and blank columns 03-10.
Note on B232: 6.1.22: New equipment type for 2022.
Note on D236: Sally Blair: If any choice is selected, Table D needs to return item #9 "An exception has…" error on the Table D tab.
Note on A250: 12/11/24 Always shows up when Table F is in scope and indicates if HR is required or not in the table.
Note on G252: 12/11/24 If F06 = required and F04>= 500kbtu then this text shows up Else if F06 = required and F04 < 500kbtu, then this text shows up without the heat or preheat service water heating part else if F06 - not required, this field in BlankGrayedOut
Note on F253: 12/11/24 = "Required" if: A.02 != 15 And F04 >= 600 kbtuh AND F02 + 0.1 * (F03 - F02) >= 2400 kbtu AND F04 + F05 >= 2200 kbtu OR F03 >= 3600 kbtu AND F04 + 0.1 * F05 >= 700 kBtu Else = "Not Required"

## F. HVAC Systems (LMCC)
|  | User input |  |  | auto calculated | [6 empty] | From another Table |  |  | From look up table
F. HVAC SYSTEM SUMMARY (DRY & WET SYSTEMS)
[d:OnlyUI] Table Instructions: Complete the following equipment schedules to show compliance with mandatory requirements found in §110.1 and §110.2(a) and prescriptive requirements found in §140.4 (a), §140.4(b) and §140.4(k), §170.2(c)1, §170.2(c)3 or §141.0(b)2 and §180.2(b)2 for alterations. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance for mechanical equipment with mandatory requirements found in §110.1 and §110.2(a) and prescriptive requirements found in §140.4 (a), §140.4(b), §170.2(c)1, §170.2(c)3, §140.4(k) or §141.0(b)2 and §180.2(b)2 for alterations. [d:/OnlyRG]
Space Conditioning System Information
01 | 02 | 03 | 04 | 05 | 06 | 07
Name or Item Tag | Quantity | System Serving | System Status | Space Type | Utilizing Recovered Heat | Distrubution System Type
|  | Dropdown | Dropdown | Dropdown | ¨ | Dropdown
|  | System Serving Dropdown | Status Dropdown | Space Type Dropdown |  | Distrubution System Type Dropdown
|  | Single Zone | New/Addition | Retail |  | Ducted
|  | Multi-Zone | Alteratation | Grocery |  | Ductless
|  | Multiple Dwelling units | Addition | School |  | Piping
|  | Individual Dwelling Unit |  | Financial Institution |  | Radiant
Library
Office Space in Wearhouse
Office
Other
Residential Space Conditioning (SC) Systems – Heating/Cooling/Ducts (Section 150.1(c)7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 |  | 14
Name or Item Tag | Dwelling Unit Type | SC Type | Heating System Type | Heating Efficiency Type | Proposed Heating Efficiency | Cooling System Type | Cooling Efficiency Type | Proposed Cooling Efficiency SEER/SEER2 | Proposed Cooling Efficiency EER/EER2/CEER | Distribution System Type | Duct Location | Duct R-value |  | Thermostat Type
auto-populated from table above | User input | Select From List | Select From List | Select From List | User input | Select From List | Select From List | User input | User input | Select From List | Select From List | Select From List |  | Select From List
NOTE - The sizing table below is not completed from left to right in the user interface. Sizing information is needed to determine if system type is restricted. This is ok since the form is just a reporting tool, not a user interface
Dry System Equipment Sizing (includes air conditioners, condensers, heat pumps, VRF, furnaces, unit heaters and DOAS systems )
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Name or Item Tag | Equipment Category per Tables 110.2, §140.4(a)2 and 170.2(c)3ai | Equipment Type per Tables 110.2 & Title 20 | Smallest Size Available1 §140.4(a) & 170.2(c)1 | Equipment Sizing per Mechanical Schedule (kBtu/h) §140.4 (a&b), §170.2(c)1 & §170.2(c)2
|  |  |  | Heating Output2,3 |  |  | Cooling Output2,3 |  | Load Calculations3,4
|  |  |  | Per Design (kBtu/h) | Rated (kBtu/h) | Supp. Heating Output (kBtu/h) | Sensible Per Design (kBtu/h) | Rated (kBtu/h) | Total Heating Load (kBtu/h) | Total Sensible Cooling Load (kBtu/h)
auto-populated from table above | Dropdown | Dropdown | Dropdown
1 FOOTNOTES: Equipment shall be the smallest size, within the available options of the desired equipment line, necessary to meet the design heating and cooling loads of the building per §140.4(a) and §170.2(c)1. Healthcare facilities are excepted. | [9 empty] | Reset | Add Row | Remove Last
2 It is common practice to show rated output capacity on the equipment schedule. Sensible cooling output comes from specification sheet tables.
3 If equipment is heating only, leave cooling output and load blank. If equipment is cooling only, leave heating output and load blank.
4 Authority Having Jurisdiction may ask for load calculations used for compliance per §140.4(b) and §170.2(c)2. | [22 empty] | Customized Sizing drop downs for column 02 in Dry System Equipment Efficiency (other than Package Terminal Air Conditioners (PTAC) and Package Terminal Heat Pumps (PTHP)) Table
| Equipment Category Dropdown | Eq Type Dropdown | Smallest Size Dropdown | [11 empty] | Dropdown for Column 03 Eq Type
| Unitary AC/ Condensers | Ben, see column M. | Yes | [18 empty] | From Table 110.2-A >> | AC, water cooled | AC, evaporatively cooled | Condensing Units, air cooled | Condensing Units, water cooled | Condensing Units, evaporatively cooled
| Unitary AC/ Cond. (no elec. resistance) |  | NA: Standby Equip. | [19 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000 | > 135,000
| Unitary heat pumps |  | NA: Load Controls | [10 empty] | "Unitary AC/ Condensers" | AC, water cooled | << from Table 110.2-A | [6 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
| Unitary heat pumps (no elec. resistance) |  | NA: Altered per §141.0(b)2E & 180.2(b)2 | [19 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000
| PTAC/ PTHP |  | NA: System serves Healthcare | [11 empty] | AC, evaporatively cooled | << from Table 110.2-A | [6 empty] | > 760,000 | > 760,000
| SPVAC/ SPVHP |  | NA: DOAS system | [12 empty] | << from Table 110.2-A |  |  | Last updated Table B-2 on 4.3.2020 from Title 20 Section 1605.1
| Variable Refrigerant Flow | [13 empty] | Condensing units, air cooled | << from Table 110.2-A
| Furnace/ Unit heater | [13 empty] | Condensing units, water cooled | << from Table 110.2-A
| Ceiling Mounted Computer Rm AC | [13 empty] | Condensing units, evaporatively cooled | << from Table 110.2-A
Computer Room AC (not ceiling mounted)
Sm. Commercial AC
Furnace + AC
Room AC/HP
Dual Fuel Heat Pump
Dedicated Outdoor Air System
Dry System Equipment Efficiency (other than Package Terminal Air Conditioners (PTAC), Package Terminal Heat Pumps (PTHP), DX-DOAS and Dual Fuel Heat Pumps) | [14 empty] | AC, air cooled, split (1 phase)
01 | 02 | 03 | 04 | 05 |  | 06 | 07 | 08 | 09 | 10 |  |  |  |  | AC, air cooled, split (3 phase)
Name or Item Tag | Size Category (Btu/h) | Heating Mode | [5 empty] | Cooling Mode | [6 empty] | AC, air cooled, split, space constrained |  |  |  |  | BEN - PURPLE MEANS YOU NEED TO COME BACK AND TAKE A LOOK. MOST IF NOT ALL ARE TITLE 20 ISSUE. NEED TO MAKE SURE THOSE TABLES DIDN'T CHANGE ALSO.
|  | Rating Condition (oF) | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 |  | Design Efficiency | Refrigerant Loop Heat Recovery | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency |  |  |  |  | AC, air cooled, package (1 phase)
From Eq Table above | Dropdown | Dropdown | Dropdown | Values from Tables 110.2-A, B, C, F, G & T20 Tables |  |  |  | Unit from efficiency tables auto populates here based on size category (col 02) | Values from Tables 110.2-A, B, C, F, G & T20 Tables | [5 empty] | AC, air cooled, package (3 phase) | [6 empty] | From Tables C-3, C-4 or 110.2-A, depending on size category >> | AC, air cooled, split (1 phase) | AC, air cooled, split (3 phase) | AC, air cooled, split, space constrained | AC, air cooled, package (1 phase) | AC, air cooled, package (3 phase) | AC, air cooled, package, space constrained | AC, air cooled, small duct, high velocity
[8 empty] | Unit from efficiency tables auto populates here based on size category (col 02) | Values from Tables 110.2-A, B, C, F, G & T20 Tables | [5 empty] | AC, air cooled, package, space constrained | [7 empty] | < 45,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[15 empty] | AC, air cooled, small duct, high velocity | [7 empty] | >= 45,000 and < 65,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
| Size Category Dropdown | Rating Condition Dropdown | Unit Dropdown |  |  |  | Units for auto populating, depends on equipment & size | [6 empty] | Sm. Commercial AC | Air-cooled unitary AC/HP Split Sys (3Ph) | << from Table C-4 to the right | [6 empty] | >= 65,000 and < 135,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
| Ben, see tables in column AF of this tab for custom drop downs. Sorry! | See choices in notes in column AF rows 51 & 76 of this tab. | COP |  |  |  | EER | [7 empty] | Air-cooled unitary AC/HP Pkg (3Ph) | << from Table C-4 to the right | [6 empty] | >= 135,000 and < 240,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000
|  |  | AFUE |  |  |  | IEER | [6 empty] | "Unitary Heat Pumps" | Air cooled, split (1 phase) | [7 empty] | >= 240,000 and < 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000
|  |  | Et |  |  |  | SEER | [7 empty] | Air cooled, split (3 phase) | [7 empty] | >= 760,000
|  |  | Ec |  |  |  | COP | [7 empty] | Air cooled, split, space constrained
|  |  | HSPF |  |  |  | SCOP | [7 empty] | Air cooled, package (1 phase)
Air cooled, package (3 phase)
[15 empty] | Air cooled, package, space constrained | [6 empty] | From Table C-4 to the left >> | Air-cooled unitary AC+HP Split Sys (3Ph) | Air-cooled unitary AC+HP Pkg (3Ph)
[15 empty] | Aircooled, small duct, high velocity | [7 empty] | < 65,000 | < 65,000
[15 empty] | Water source | << from Table 110.2-B | [5 empty] | From Table 110.2-B >> | Water source | Groundwater source | Ground source | Water source water-to-water | Groundwater source water-to water | Ground source brine-to-water
[15 empty] | Groundwater source | << from Table 110.2-B | [6 empty] | <17,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000
Dry System Equipment Efficiency (Package Terminal Air Conditioners (PTAC) and Package Terminal Heat Pumps (PTHP) only) | [14 empty] | Ground source | << from Table 110.2-B | [6 empty] | =>17,000 and < 135,000
01 | 02 | 03 | 04 | 05 | 06 | 070 | [8 empty] | Water source water-to-water | << from Table 110.2-B | [6 empty] | > 135,000 and < 240,000
Name or Item Tag | Heating Mode |  |  | Cooling Mode | [10 empty] | Groundwater source water-to water | << from Table 110.2-B
| Rated Output Capacity (kBtu/h) | Minimum COP Required per Table 110.2-E | Design COP | Rated Output Capacity (kBtu/h) | Minimum EER Required per Table 110.2-E | Design EER | [8 empty] | Ground source brine-to-water | << from Table 110.2-B | [5 empty] | From Table C-3, C-4, 110.2-B or 110.2-C depending on size category>> | Air-cooled gas-engine heat pump | Air cooled, split (1 phase) | Air cooled, split (3 phase) | Air cooled, split, space constrained | Air cooled, package (1 phase) | Air cooled, package (3 phase) | Air cooled, package, space constrained | Air cooled, small duct, high velocity
[15 empty] | Air-cooled gas-engine heat pump | << from Table 110.2-C | [6 empty] | Grey out the cell for this selection | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
From Eq Table above | Comes from sizing table column 06 | From Table 110.2-E Title 20 |  | Comes from sizing table column 09 | From Table 110.2-E Title 20 | [18 empty] | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
[24 empty] | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
[14 empty] | "PTAC/PTHP" | PTAC newly constructed or newly conditioned | << from Table 110.2-E | [7 empty] | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000
[15 empty] | PTAC replacements | << from Table 110.2-E
[15 empty] | PTHP newly constructed or newly conditioned | << from Table 110.2-E
[15 empty] | PTHP replacements | << from Table 110.2-E
[14 empty] | "SPVAC/ SPVHP" | SPVAC | << from Table 110.2-E
NOTE - This table should act like the fan table with tiered levels. There can be mutiple Boiler systems and multiple boilers within each boiler system | [14 empty] | SPVAC nonweatherized space constrained | << from Table 110.2-E
Boiler Efficiency and Controls | [14 empty] | SPVHP | << from Table 110.2-E |  | Last updated Table C-3 on 4.3.2020 from Title 20 Section 1605.1 |  |  |  | From Table 110.2-E >> | SPVAC | SPVHP
Boiler System Serving: |  |  | User Input | [11 empty] | SPVHP nonweatherized space constrained | << from Table 110.2-E | [6 empty] | < 65,000 | < 65,000
01 | 02 |  | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | [11 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000
Boiler Name or Item Tag | Equipment Type1 |  | Qty | Rated Input Capacity (Btu/h)2, 3 | Rated Efficiency | Minimum Efficiency Required per §110.2 | Efficiency Unit | Boiler Controls per §140.4(k) & §170.2(c)Iiii |  | High Capacity Boiler Exceptions | HVAC Hot Water Supply Temperature §120.2(I) | [11 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
[8 empty] | Isolation Valve | Temperature Reset
| Dropdown |  |  |  |  | Use table 110.2-J column after 1/10/23 Title 20 Tables | Units listed in Table 110.2-J Title 20 Tables | Dropdown | Dropdown | Dropdown | user input
System Efficiency |  |  | User Input 05: Minimum System Efficiency for High Capacity Boilers per 140.4(k)8A; User Input 08: 90%
1 FOOTNOTES: Use NRCC-PLB to document compliance with domestic hot water and service water heating systems
2 Maximum capacity- maximum ratings per the certified unit capacity |  |  | User Input 08: Isolation Dropdown; User Input 09: Temperature Reset Dropdown; User Input 10: HCB Exceptions Dropdown
3 Includes oil-fired (residual) |  |  | User Input 08: Yes; User Input 09: Yes; User Input 10: >=25% space heating provided by on-site renewable | [10 empty] | From Table 110.2-G >> | VRF air conditioners, air cooled
|  |  | User Input 08: NA: only 1 boiler in plant; User Input 09: NA: < 500,000 Btu/h; User Input 10: >=25% space heating provided by site recovered energy | [11 empty] | < 65,000
| Equipment Type Dropdown |  | User Input 09: NA: Variable Flow Controls; User Input 10: >=25% space heating provided heat recovery chillers |  |  | "VRF" | VRF air conditioners, air cooled | << from Table 110.2-G | [6 empty] | > 65,000 and < 135,000
| Hot water: Gas-Fired |  | User Input 09: NA: System serves Healthcare; User Input 10: Installed in individual dwelling unit |  |  |  | VRF heat pump, air cooled | << from Table 110.2-H | [6 empty] | > 135,000 and < 240,000
| Hot water: Oil-Fired |  | User Input 10: >=50% heating served by perimeter convective/radiant ceiling panels |  |  |  | VRF water source | << from Table 110.2-H | [6 empty] | > 240,000
| Steam: Gas-Fired, not natural draft |  | User Input 10: Serving Multifamily Occupancy |  |  |  | VRF groundwater source | << from Table 110.2-H
| Steam: Gas-Fired, natural draft |  | User Input 10: No Exceptions Apply |  |  |  | VRF ground source | << from Table 110.2-H | [5 empty] | From Table 110.2-H >> | VRF heat pump, air cooled | VRF water source | VRF groundwater source | VRF ground source
| Steam: Oil-Fired | [12 empty] | "Furnace/ Unit Heater" | Warm-air central furnace, gas-fired | << from Table 110.2-I | [6 empty] | < 65,000 | < 65,000 | < 135,000 | < 135,000
[14 empty] | "Furnace/ Unit Heater" | Warm-air duct furnace, gas-fired | << from Table 110.2-I | [6 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000
[15 empty] | Warm-air unit heaters, gas-fired | << from Table 110.2-I | [6 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
[14 empty] | "Furnace/ Unit Heater" | Weatherized gas central furnace w single phase supply | << from Table 4-1 to the right | [6 empty] | > 240,000 | >=240,000
[15 empty] | Non-weatherized gas central furnace w single phase supply | << from Table 4-1 to the right |  | Last updated Table C-4 on 4.3.2020 from Title 20 Section 1605.1.. Larger size HP are covered in T24 110.2 Tables.
[14 empty] | "Furnace/ Unit Heater" | Wall furnace, fan | << from Table 4-2 to the right | [5 empty] | From Table 110.2-I >> | Warm-air central furnace, gas-fired | Warm-air duct furnace, gas-fired | Warm-air unit heaters, gas-fired
[15 empty] | Wall furnace, gravity | << from Table 4-2 to the right | [6 empty] | < 225,000 | Grey out the cell for this selection | Grey out the cell for this selection
[15 empty] | Floor furnace | << from Table 4-2 to the right | [6 empty] | > 225,000
[15 empty] | Room Heater | << from Table 4-2 to the right
[14 empty] | "Computer Rm AC (not ceiling mounted) | CRAC, air-cooled, downflow | << from Table C-7 to the right | [5 empty] | From Title 20 Table E-6 to the left >> | Weatherized gas central furnace w single phase supply | Non-weatherized gas central furnace w single phase supply
[15 empty] | CRAC, air-cooled, upflow | << from Table C-7 to the right | [6 empty] | < 225,000 | < 225,000
[15 empty] | CRAC, water-cooled, downflow | << from Table C-7 to the right
[15 empty] | CRAC, water-cooled, upflow | << from Table C-7 to the right | [5 empty] | From Table E-2 to the left >> | Wall furnace, fan | Wall furnace, gravity | Floor furnace | Room Heater
[15 empty] | CRAC, water-cooled w econ, downflow | << from Table C-7 to the right | [6 empty] | < 42,000 | < 27,000 | < 37,000 | < 20,000
[15 empty] | CRAC, water-cooled w econ,upflow | << from Table C-7 to the right | [6 empty] | > 42,000 | > 27,000 and < 46,000 | > 37,000 | > 20,000 and < 27,000
[15 empty] | CRAC, Glycol-cooled, downflow | << from Table C-7 to the right | [7 empty] | > 46,000 |  | > 27,000 and < 46,000
[15 empty] | CRAC, Glycol-cooled, upflow | << from Table C-7 to the right | [9 empty] | > 46,000
[15 empty] | CRAC, Glycol-cooled w econ, downflow | << from Table C-7 to the right | Last updated Table C-7 on 4.3.2020 from Title 20 Section 1605.1
[15 empty] | CRAC, Glycol-cooled w econ, upflow | << from Table C-7 to the right | [5 empty] | From Table C-7 to the left >> | CRAC, air-cooled, downflow | CRAC, air-cooled, upflow | CRAC, water-cooled, downflow | CRAC, water-cooled, upflow | CRAC, water-cooled w econ, downflow | CRAC, water-cooled w econ, upflow | CRAC, Glycol-cooled, downflow | CRAC, Glycol-cooled, upflow | CRAC, Glycol-cooled w econ, downflow | CRAC, Glycol-cooled w econ, upflow
[14 empty] | Room AC/HP | Room AC, louvered sides | << from Table B-2 to the right | [6 empty] | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[15 empty] | Room AC, no louvers | << from Table B-2 to the right | [6 empty] | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000 | > 65,000 and < 240,000
[15 empty] | Room AC, casement only | << from Table B-2 to the right | [6 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000 | > 240,000 and < 760,000
[15 empty] | Slider Room AC, casement | << from Table B-2 to the right
[15 empty] | Room AC Heat Pump, louvered sides | << from Table B-2 to the right
[15 empty] | Room AC Heat Pump, no louvers | << from Table B-2 to the right
[14 empty] | Furnace + AC | AC, air cooled, split + warm-air central furnace, gas-fired
AC, air cooled, split + weatherized gas central furnace
[15 empty] | AC, air cooled, single pkg + weatherized gas central furnace, 1 phase supply | [6 empty] | From Table 110.2-A & T20 C-3 (cooling) & 110.2-I & Table E-6 to the left (heating) >>> | AC, air cooled, split + Warm-air central furnace, gas-fired | AC, air cooled, split+ weatherized gas central furnace w single phase supply |  | From Table 110.2-A & T20 C-3 (cooling) & 110.2-I & Table E-6 to the left (heating) >>> | AC, air cooled, single package + Weatherized gas central furnace w single phase supply | AC, air cooled, single package + Warm-air central furnace, gas-fired
[15 empty] | AC, air cooled, single pkg + warm-air central furnace, gas-fired | [7 empty] | <45kBtuh cooling/ <225kBtuh heating | <45kBtuh cooling/ <225kBtuh heating
[14 empty] | Unitary AC/ Cond. (no elec. resistance) | AC, water cooled | [7 empty] | <45kBtuh cooling/ >225kBtuh heating | <45kBtuh cooling/ >225kBtuh heating |  |  | <65kBtuh cooling/ <225kBtuh heating | <65kBtuh cooling/ <225kBtuh heating
Chiller & Air To Water Heat Pump Efficiency and Controls | [14 empty] | AC, evaporatively cooled | [7 empty] | >45kBtuh cooling/ <225kBtuh heating | >45kBtuh cooling/ <225kBtuh heating |  |  | <65kBtuh cooling/ >225kBtuh heating | <65kBtuh cooling/ >225kBtuh heating
01 |  | 02 | 03 | 04 | 05 | 06 |  | 07 | 08 | 09 | 10 | 11 | 12
Name or Item Tag |  | Equipment Type | Qty | Size Category1 (Tons) | Leaving Hot Water Temperature | Chiller Efficiency "Path B" Exception per §140.4(i) & §170.2(c)g |  | Rated Efficiencies | Efficiencies Required per §110.22 | Efficiency Unit | Controls per §140.4(k) & §170.2(c)I |  | Serving | [9 empty] | >45kBtuh cooling/ >225kBtuh heating | >45kBtuh cooling/ >225kBtuh heating |  |  | >65kBtuh cooling/ <225kBtuh heating | >65kBtuh cooling/ <225kBtuh heating
|  |  | User Input 11: Isolation Valve | Temperature Reset |  |  | Condensing units, air cooled | [7 empty] | >65kBtuh cooling/ <225kBtuh heating | >65kBtuh cooling/ <225kBtuh heating |  |  | >65kBtuh cooling/ >225kBtuh heating | >65kBtuh cooling/ >225kBtuh heating
|  | Dropdown to match Table 110.2-D |  | Dropdown | Dropdown | Dropdown |  |  | Ben, "Path B" value from Table 110.2-D or 110.2-NI & J | Ben, "Path B" units from Table 110.2-D or 110.2-NI & J | Dropdown | Dropdown |  |  | Condensing units, water cooled | [5 empty] | EVEN THE YELLOW ONES NEED TO BE REVISITED AGAIN. THEY HAVE ONLY BE UPDATED FOR COOLING EFFICIENCY |  | >65kBtuh cooling/ >225kBtuh heating | >65kBtuh cooling/ >225kBtuh heating |  |  | >135kBtuh cooling/ <225kBtuh heating | >135kBtuh cooling/ <225kBtuh heating
[9 empty] | Ben, "Path B" value from Table 110.2-D or 110.2-NI & J | Ben, "Path B" units from Table 110.2-D or 110.2-NI & J
[9 empty] | Table 110.2-NI & J | Table 110.2-NI & J
|  |  | User Input 09: Table 110.2-NI & J; User Input 10: Table 110.2-NI & J |  |  |  | Condensing units, evaporatively cooled |  | Last updated Table E-6 on 4.3.2020 from Title 20 Section 1605.1 | [5 empty] | >135kBtuh cooling/ <225kBtuh heating | >135kBtuh cooling/ <225kBtuh heating |  |  | >135kBtuh cooling/ >225kBtuh heating | >135kBtuh cooling/ >225kBtuh heating
|  |  | User Input 10: Reset; User Input 11: Add Row | Remove Last |  |  | AC, air cooled, split (1 phase) | [7 empty] | >135kBtuh cooling/ >225kBtuh heating | >135kBtuh cooling/ >225kBtuh heating |  |  | >240kBtuh cooling/ <225kBtuh heating | >240kBtuh cooling/ <225kBtuh heating
1 FOOTNOTES: Chilled water plants shall not have more than 300 tons provided by air-cooled chillers. Exceptions may apply per §140.4(j). | [14 empty] | AC, air cooled, split (3 phase) | [7 empty] | >240kBtuh cooling/ <225kBtuh heating | >240kBtuh cooling/ <225kBtuh heating |  |  | >240kBtuh cooling/ >225kBtuh heating | >240kBtuh cooling/ >225kBtuh heating
2 Efficiency required is a minimum when "EER" or "COP" is the Efficiency Unit in column 08. It is also a minimum when "IPLV" is the unit for air-cooled, absorption, and water cooled gas engine chillers. Efficiency required is a maximum when "kW/ton" is the Efficiency Unit and when "IPLV" is the unit for water cooled electrically operated chillers. |  |  | User Input 11: Isolation Dropdown | Temp Reset Dropdown |  |  | AC, air cooled, split, space constrained | [7 empty] | >240kBtuh cooling/ >225kBtuh heating | >240kBtuh cooling/ >225kBtuh heating |  |  | >760kBtuh cooling/ <225kBtuh heating | >760kBtuh cooling/ <225kBtuh heating
|  | Equipment Type Dropdown | User Input 04: Size Category Dropdown; User Input 05: Leaving Hot Water Temperature; User Input 06: Efficiency Exception Dropdown; User Input 11: Yes | Yes |  |  | AC, air cooled, package (1 phase) | [7 empty] | >760kBtuh cooling/ <225kBtuh heating | >760kBtuh cooling/ <225kBtuh heating |  |  | >760kBtuh cooling/ >225kBtuh heating | >760kBtuh cooling/ >225kBtuh heating
|  | Air Cooled: Condenser elec. operated | User Input 04: < 75; User Input 05: Low - 105F; User Input 06: No exception taken; User Input 11: NA: only 1 chiller in plant | NA: ≤ 500 kBtu/hr (41.67 tons) |  |  | AC, air cooled, package (3 phase) | [7 empty] | >760kBtuh cooling/ >225kBtuh heating | >760kBtuh cooling/ >225kBtuh heating
|  | Air Cooled: w/o condenser elec. operated | User Input 04: ≥ 75 and < 150; User Input 05: Medium - 120F; User Input 06: 1. Electrical service > 600V; User Input 11: NA: chillers in series | NA: Variable Flow Controls |  |  | AC, air cooled, package, space constrained
|  | Water Cooled: Reciprocating | User Input 04: ≥ 150 and < 300; User Input 05: High - 140F; User Input 06: 2. Heat recovery w/ design capacity > 40% of the design chiller cooling capacity | NA: System serves Healthcare |  |  | AC, air cooled, small duct, high velocity
|  | Water Cooled: Positive displacement | User Input 04: ≥ 300 and < 400; User Input 05: Boost - 140F; User Input 06: 3. Charging energy storage systems w/ charging temperature < 40oF |  |  | Unitary heat pumps (no elec. resistance) | Air cooled, split (1 phase)
|  | Water Cooled: Centrifugal | User Input 04: ≥ 400 and < 600; User Input 06: 4. 4th (or more) chiller in this building |  |  |  | Air cooled, split (3 phase)
|  | Air Cooled: Absorption, single effect | User Input 04: ≥ 600; User Input 06: Water -Cooled Centrifugal Chilling Package per Exception 1 to §110.2(a) |  |  |  | Air cooled, split, space constrained |  | Last updated Table E-2 on 4.3.2020 from Title 20 Section 1605.1 |  |  |  |  | From Table B-2 >>> | Room AC, louvered sides | Room AC, no louvers | Room AC, casement only | Room AC, slider & casement | Room AC Heat Pump, louvered sides | Room AC Heat Pump, no louvers
|  | Water Cooled: Absorption, single effect | [12 empty] | Air cooled, package (1 phase) | [7 empty] | < 8,000 | < 8,000 | Grey out the cell for this selection | Grey out the cell for this selection | < 20,000 | < 14,000
|  | Absorption: Double effect, indirect-fired | [12 empty] | Air cooled, package (3 phase) | [7 empty] | >= 8,000 and < 14,000 | >= 8,000 and < 11,000 |  |  | >= 20,000 | >= 14,000
|  | Absorption: Double effect, direct-fired | [12 empty] | Air cooled, package, space constrained | [7 empty] | >= 14,000 and < 20,000 | >= 11,000 and < 14,000
|  | Water Cooled: Gas engine | [12 empty] | Aircooled, small duct, high velocity | [7 empty] | >= 20,000 and < 28,000 | >= 14,000 and < 20,000
|  | Heat Recovery Chiller - Positive Displacement | [12 empty] | Water source | [7 empty] | >= 28,000 | >= 20,000
Heat Recovery Chiller - Positive Centrifugal
Air Source Heat Pump
Groundwater source
This table is brand new in 2022 | [14 empty] | Ground source
[15 empty] | Water source water-to-water | [6 empty] | From Table 110.2-A >> | AC, water cooled | AC, evaporatively cooled | Condensing Units, air cooled | Condensing Units, water cooled | Condensing Units, evaporatively cooled
DX-DOAS Efficiency | [14 empty] | Groundwater source water-to water | [7 empty] | > 65,000 and < 135,000 | > 65,000 and < 135,000 | > 135,000 | > 135,000 | > 135,000
01 |  | 02 | 03 | 04 | 05 |  | 06 | 07 | 08 | [5 empty] | Ground source brine-to-water | [7 empty] | > 135,000 and < 240,000 | > 135,000 and < 240,000
Name or Item Tag |  | Equipment Type | Qty | Energy Recovery | Rating Condition |  | Rated Efficiencies | Efficiency Unit | Minimum Efficiency | [5 empty] | Air-cooled gas-engine heat pump | [7 empty] | > 240,000 and < 760,000 | > 240,000 and < 760,000
[14 empty] | DOAS | DOAS | [7 empty] | > 760,000 | > 760,000
From sizing table above |  | Dropdown to match Table 110.2-H | User Input 04: Dropdown; User Input 05: Dropdown; User Input 08: ISMRE |  |  |  | DX-DOAS
|  |  | User Input 08: ISCOP |  |  | Computer Rm AC Ceiling Mounted
[22 empty] | From Tables C-3, C-4 or 110.2-A, depending on size category >> | AC, air cooled, split (1 phase) | AC, air cooled, split (3 phase) | AC, air cooled, split, space constrained | AC, air cooled, package (1 phase) | AC, air cooled, package (3 phase) | AC, air cooled, package, space constrained | AC, air cooled, small duct, high velocity
[23 empty] | < 45,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
[23 empty] | >= 45,000 and < 65,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
[23 empty] | >= 65,000 and < 135,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
|  | Equipment Type Dropdown | User Input 04: Energy Recovery Dropdown; User Input 05: Rating Condition Dropdown | [11 empty] | >= 135,000 and < 240,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000 | >= 240,000 and < 760,000
|  | Air Cooled | User Input 04: Yes; User Input 05: Cooling Tower Condenser Water | [11 empty] | >= 240,000 and < 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000 | >= 760,000
|  | Air Source Heat Pump | User Input 04: No; User Input 05: Chilled Water | [11 empty] | >= 760,000
Water Cooled
|  | Water Source Heat Pump | User Input 05: Rating Condition Dropdown | [11 empty] | Water source | Groundwater source | Ground source | Water source water-to-water | Groundwater source water-to water | Ground source brine-to-water
|  |  | User Input 05: Ground Source Closed & Open Loop | [11 empty] | > 65,000 and < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000 | < 135,000
|  |  | User Input 05: Ground Water Source | [11 empty] | > 135,000 and < 240,000
Water Source
This table is brand new in 2022
[23 empty] | Air-cooled gas-engine heat pump | Air cooled, split (1 phase) | Air cooled, split (3 phase) | Air cooled, split, space constrained | Air cooled, package (1 phase) | Air cooled, package (3 phase) | Air cooled, package, space constrained | Air cooled, small duct, high velocity
[23 empty] | Grey out the cell for this selection | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000 | < 65,000
Dual Fuel Heat Pump | [23 empty] | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000 | >= 65,000 and < 135,000
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | [13 empty] | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000 | >= 135,000 and < 240,000
Name or Item Tag | Equipment Category | Equipment Type | User Input 03: Size Category (Btu/h); User Input 04: Heating Mode; User Input 08: Cooling Mode | [12 empty] | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000 | >= 240,000
|  |  |  | Rating Condition (oF) | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency | Efficiency Unit | Minimum Efficiency Required per Tables 110.2/ Title 20 | Design Efficiency
From Eq Table above | Dropdown | Dropdown | Dropdown | Dropdown | Lookup based on heat pump system type selected | Always appropriate HP values |  | Unit from efficiency tables auto populates here based on size category (col 02) | Values from Tables 110.2-A, B, C, E, HG, I, J & T20 Tables | [13 empty] | Air Cooled with free air discharge condenser, ducted | Air Cooled with free air discharge condenser, nonducted | Air Cooled with free air discharge condenser with fluid economizer, ducted | Air Cooled with free air discharge condenser with fluid economizer, nonducted | Air cooled with ducted condenser, ducted | Air cooled with ducted condenser, nonducted | Air cooled with fluid economizer and ducted condenser, ducted | Air cooled with fluid economizer and ducted condenser, nonducted
|  |  | User Input 08: Unit from efficiency tables auto populates here based on size category (col 02); User Input 09: Values from Tables 110.2-A, B, C, E, HG, I, J & T20 Tables | [11 empty] | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h
| Always = Furnace/Unit Heater | Dropdown | Dropdown | Always Blank/Gray | Dropdown | Always appropriate furnace value |  | Always Blank/Gray | Always Blank/Gray | Always Blank/Gray | [12 empty] | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h
[23 empty] | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h
| HP Equipment Category Dropdown | Equipment Type Dropdown | User Input 03: Size Category Dropdown; User Input 04: Rating Condition Dropdown; User Input 05: Unit Dropdown | [11 empty] | Water Cooled, Ducted | Water Cooled, nonducted | Water cooled with fluid economizer, ducted | Water cooled with fluid economizer, nonducted | Glycol cooled, ducted | Glycol cooled, nonducted | Glycol cooled with fluid economizer, ducted | Glycol cooled with fluid economizer, nonducted
| Unitary Heat Pump | Provide the appropriate equipment type dropdowns based on the equipment category chosen in 02. | User Input 03: See tables in column AF of this tab for custom drop downs.; User Input 04: See choices in notes in column AF rows 51 & 76 of this tab.; User Input 05: COP | [11 empty] | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h | <29,000 Btu/h
| Unitary Heat Pump (no elec resistance) |  | User Input 05: AFUE | [11 empty] | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h | >29,000 Btu/h and < 65,000 Btu/h
[23 empty] | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | > 65,000 Btu/h | bar: User Input 05
Ec
HSPF
Heat Rejection Equipment (Cooling Towers, Condensers, Waterside Economizers) Efficiency and Controls
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12
Name or Item Tag | Equipment Type1 | Qty | Rating Condition (oF) | Rated Performance | Minimum Required Performance per Table 110.2-E, §140.4(h)5 & §170.2(c)fv | Performance Unit | Fan Speed Control §140.4(h)1 | Tower Flow Turndown §140.4(h)2 | Fan Control in Multiple Cell Equipment §140.4(h)4 | Economizer Controls §140.4(e) | Condenser Water Temp Reset Controls
| Dropdown to match Table 110.2-FE |  | Dropdown |  | Value from table |  | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
1 FOOTNOTES: Centrifugal fan open-circuit towers are not allowed for rated capacities > 900 gpm at 95oF condenser water return, 85oF condenser water supply and 75oF outdoor wet-bulb temperature. Exceptions may apply per §140.4(h)4. | [13 empty] | Link to 2022 Table 110.2-F
| Equipment Type Dropdown |  | User Input 07: Fan Speed Control Dropdown; User Input 08: Tower Flow Turndown Dropdown; User Input 09: Fan Control Dropdown; User Input 10: Economizer Control Dropdown; User Input 11: Cond. Water Temp Reset Controls Dropdown |  |  | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1102mandatoryrequirementsforspaceconditioningequipment.htm#table1102fperformancerequirementsforheatrejectionequipment.htm
| Axial fan open-circuit tower, CW loop in CHW plant >= 900gpm |  | Rating Condition Dropdown |  |  |  | Yes | Yes | Yes | Designed per §140.4(e) | Yes
| Replacement axial fan open-circuit tower, CW loop in CHW plant >= 900gpm |  | User Input 03: 165oF entering gas temp 105oF condensing temp 75oF entering air wb"; User Input 07: NA: Fan motor < 7.5hp (5.6kW); User Input 08: NA: Single condenser water pump; User Input 09: NA: Not multiple cell; User Input 11: No
| Propeller/ axial fan open-circuit cooling tower |  | User Input 03: 140oF entering gas temp 96.3oF condensing temp 75oF entering air wb"; User Input 07: NA: Integral to other equip.; User Input 08: NA: Not open-circuit tower; User Input 09: NA: No variable speed drives
| Propeller/ axial fan closed-circuit cooling tower |  | User Input 07: NA: Cond. fans serving > 1 refrigerant circuits
| Centrifugal fan open-circuit cooling tower |  | User Input 07: NA: Cond. fans serving flooded cond.
| Centrifugal fan closed-circuit cooling tower |  | User Input 07: NA: Mult. fans & lead fans meet req.
Propeller/ axial fan evaporative condensers
Centrifugal fan evaporative condensers
Air cooled condensers
Waterside Economizer
Electric Resistance Heating
01 |  | 02 | User Input 03: 03; User Input 04: 04
Name or Item Tag |  | Equipment Description | User Input 03: Output Capacity (kW); User Input 04: Applicable Exception to §140.4(g) Allowing Electric Resistance Heating
|  | dropdown | User Input 04: dropdown
Elec Resistance Dropdown
|  | Dropdown | User Input 04: Exception 1: Supplement to a heating system in which at least 60% of the annual energy requirement is supplied by site-solar or recovered energy.
|  | Baseboard | User Input 04: Exception 2: Supplement to a heat pump heating system and the heating capacity of the heat pump is more than 75% of the design heating load calculated in accordance with §140.4.
|  | Under-mat | User Input 04: Exception 3: Total capacity of electric-resistance heating systems serving the entire building is less than 10% of the total design output capacity of all heating equipment serving the entire building.
|  | Other | User Input 04: Exception 4: Total capacity of electric-resistance heating systems serving the entire building, excluding those allowed under Exception 2, is no more than 3 kW.
NA: Alteration, replacement of existing electric resistance heating system.
Exempt: Supplemental electric resistance heating systems complying with Section 140.4(a)3C
Mechanical Heat Recovery | bar: User Input 03 to User Input 09
01 | 02 | 03 | User Input 03: 04; User Input 04: 05; User Input 05: 06; User Input 06: 07
Name or Item Tag | Coincident Peak Cooling Load of All High Load Spaces | Design Capacity of All Mechanical Cooling Systems2 | User Input 03: Design Capacity of All Service Water Heating Systems1; User Input 04: Design Capacity for all space heating systems; User Input 05: Simultaneous Mechanical Heat Recovery; User Input 06: Heat Recovery Systems Shall: - Transferring the lesser of the following from spaces in cooling to spaces in heating: - 25% of thje peak heat rejection of the cooling system - 25% of design capacity of all service water heating systems + design capacity of all space heating systems - Heat or preheat the service water heating to the smaller of: - 30% of the peak heat rejection of the cooling system; or - 30% of design capacity of all service water heating systems
| user input | user input | User Input 03: user input; User Input 04: user input
Footnote 1: Excluding systems expected to operate less than 5 hours per week | bar: User Input 03 to User Input 05
Footnote 2: If the design includes capacity for future cooling systems, then assume 20% of future systems serve high load spaces | bar: User Input 03 to User Input 05
Note on F11: 12/9/24 If selected, ignore the custom dropdown options for Equipment Category 02 and Equipment Type 03
Note on G13: 7.5.22 This is needed for downstream CF2Rs, this does not trigger other fields or affect compliance logic.
Note on C15: 3.3.22 If Multi-zone or Dwelling unit is selected, 03-06 are gray/blank
Note on D15: 3.3.22 If Alteration is selected, 04-07 blank/grayed out
Note on E21: Ben Lalor: If other is selected 06 blank/grayed out
Note on E35: 2020 Update: F.05, F.06, and F.07 should Trigger when: F.02 = - Sm. Commercal AC - Unitary Heat Pump - Furnace/Unit Heater - Furnace + AC OR F.03 = - PTHP newly constructed or newly conditioned - PTHP replacements - SPVHP - SPVHP nonweatherized space constrained - VRF heat pump, air cooled - VRF water source - VRF groundwater source - VRF ground source OTHERWISE F.05, F.06, F.07 should be grayed out
Note on H35: 2020 UPDATE: F.08 and F.09 should trigger when: F.02 = - Unitary AC/Condenser - Heatpump + AC - Unitary Heat Pump - Computer Room AC - Room AC/HP - Furnace + AC - PTAC/PTHP - SPVAC/SPVHP - VRF OTHERWISE F.08 and F.09 should be grayed out
Note on J36: October 2019 Updates Added units to F.10 and F.11
Note on B37: 11/12/24 If 03 above == Multi-zone, 04 == alteration or addition or 06 has been selected, If 04 == alteration or addition user has the options to select any of the equipment categories F.03 Else If F.03 SCSI == "Individual Dwelling unit(s)" AND A.02 = 2-15 Equipment Category 02 limited to - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else If F.03 SCSI == ""Individual Dwelling unit(s)" AND A.02 = 1 OR 16 Equipment Type 03 limited to - Unitary Heat Pump - DUAL FUEL HEAT PUMP Else If F.03 SCSI == Single Zone AND A.02 = 2-15 AND space type = retail OR grocery AND rated cooling capacity 09 <=240 Then equipment type 03 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else If F.03 SCSI == Single Zone AND A.02 = 1 OR 16 AND space type = retail OR grocery AND rated cooling capacity 09 <=65 Then equipment type 03 limited to the following options: - Furnace + AC Else If F.03 SCSI == Single Zone AND A.02 = 1 OR 16 AND space type = retail OR grocery AND rated cooling capacity 09 >65 AND <240 Then equipment type 03 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP Else If F.03 SCSI == Single Zone AND climate zone = 2-15 AND space type = school AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else If F.03 SCSI == Single Zone AND climate zone = 1 OR 16 AND space type = school AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP Else If F.03 SCSI == Single Zone AND climate zone = 1-15 AND space type = office OR financial institution OR library AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else If F.03 SCSI == Single Zone AND climate zone = 16 AND space type = office OR financial institution OR library AND rated cooling capacity 09 <=65 Then equipment type 02 limited to the following options: - Furnace + AC Else If F.03 SCSI == Single Zone AND climate zone = 16 AND space type = office OR financial institution OR library AND rated cooling capacity 09 > 65 AND <=225 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - DUAL FUEL HEAT PUMP Else If F.03 SCSI == Single Zone AND space type = office spaces in warehouses AND rated cooling capacity 09 <=240 Then equipment type 02 limited to the following options: - Unitary Heat Pumps - Unitary Heat Pumps (no elec resistance) - Unitary AC/Condensers - Unitary AC/Condensers (no elec resistance) - PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP - Dedicated Outdoor Air System Else if F.03 SCSI == multizone AND F.05 FSCI == office OR (F.05 == school And A.02 = And F.04 == New And A.04 + A.05 <= 150,000 And A.06 < 6 Equipment type in 02 limited to the following options (NOTE - options listed below are non-reported fields in the user interface for the VCA. The reported value is listed in the options and is one of the enumerations listed shown in the mock-up dropdown) Option 1 - VRF with refrigerant loop heat recovery and DOAS - Reported values: - Variable Refrigerant Flow (must select HP option in F.03 Equipment Type, VRF AC not allowed) AND - Dedicated Outdoor Air System Option 2 - Air to water heat pump with Four pipe fan coil and DOAS - Reported Values: - Air To Water Heat Pump in Chiller & AWHP Table AND - Dedicated Outdoor Air System Option 3 (not an option for school buildings in climate zones 1, 3, 5, 6, 7) - VAV with heating provided by air to water heat pump - Reported Value: - Air To Water Heat Pump in Chiller and AWHP Table Option 4 - Dual Fan Dual Duct - reported value is any of the following: - Unitary Heat Pump - Unitary Heat Pump (no elec resistance) PTAC/PTHP - SPVAC/SPCHP - Variable Refrigerant Flow - Ceiling Mounted Computer Room AC - Computer Room AC (not ceilling mounted) - Sm. Commercial AC - Room AC/HP ELSE choose from the full list of equipment categories
Note on E37: 2019 Update: If this value is > 1.43x column10, Table D needs to return the Row 9 error on the Table D tab.
Note on H37: 2019 Update: If this value is > 1.21x column11, Table D needs to return the Row 10 error on the Table D tab.
Note on C43: 2019 Update: Changes were made to these custom dropdowns for 2019
Note on B44: 6.10.20: Added category
Note on AI44: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.1" in the upper row & "13.9" in the lower row
Note on AJ44: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.1" in the upper row & "12.3" in the lower row
Note on AK44: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.5" in the upper row & "11.8" in the lower row
Note on AL44: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AM44: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AI45: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.5" in the upper row & "13.9" in the lower row
Note on AJ45: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.0" in the upper row & "12.2" in the lower row
Note on B46: 6.10.20: Added category
Note on D46: Sally Blair: Greys out columns 05, 07, 08 2019 Update: This should no longer gray out 05, 06, or 08
Note on AI46: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.4" in the upper row & "13.6" in the lower row
Note on AJ46: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "12.1" in the lower row
Note on D47: 2019 Update: Added new NA choice for new exception for Healthcare facilities.
Note on AI47: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.2" in the upper row & "13.5" in the lower row
Note on AJ47: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.7" in the upper row & "11.9" in the lower row
Note on B53: THIS NEEDS TO BE UPDATED IN FORM AND SCHEMA Rename this "Sm. Commercial AC"
Note on B54: 2020 Update: Remove "Split" from this dropdown choice.
Note on B56: 3.14.22 When DFHP is selected, gray equipment type 03 and transfer system to DFHP efficiency table. They still need to complete 04-11
Note on A60: Sally Blair: This table only shows up if any of the equip. categories OTHER THAN "PTAC/PTHP" is selected in Eq Sizing Table above. Otherwise, user shouldn't see this at all (including title).
Note on D61: October 2019 Update: Trigger F.04/5/6 if F.05 >=1, otherwise they are gray
Note on I61: Trigger F.07/8/9 if F.05 >=1 , otherwise they are gray
Note on A64: 6.3.22 Anything designated as one of the follwing does not transfer to this table. Everything else does. PTAC/PTHP DX-DOAS Dual Fuel Heat Pump
Note on C64: Sally Blair: This is only a dropdown if column 03 in Dry System Equipment Sizing table is any of the following: - "VRF heat pump, air cooled" - "Air cooled, split" - "Air cooled, split, space constrained" - "Air cooled, packaged" - "Air cooled, packaged, space constrained" Otherwise this cell greys out.
Note on E64: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on G64: Sally Blair: If nothing is entered in Column 10 above in the Sizing Table, columns 03-06 here grey out.
Note on H64: 12/9/24 = "Required" if multizone option 1 is selected in F.02, otherwise = BlankGrayedOut
Note on K64: Sally Blair: If nothing is entered in Column 11 above in the Sizing Table, columns 07-09 here grey out.
Note on AI65: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "12.2" in the lower row. From Table C-3
Note on AJ65: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AK65: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AL65: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.0" in the lower row. From Table C-3
Note on AM65: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AN65: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AO65: NEEDS TO BE UPDATED IN FORM AND SCHEMA If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AI66: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.7" in the lower row. From Table C-3
Note on AJ66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AK66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AL66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AM66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AN66: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on D67: Sally Blair: This needs to be a custom dropdown which only includes the unit relevant to the equipment type chosen. There's only one instance where they get to choose- Warm Air Central Furnace, Gas fired.
Note on AI67: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row.
Note on AJ67: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AK67: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AL67: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AM67: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AN67: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on B68: 2019 Update: Changes were made to these sizing dropdowns for 2019.
Note on AI68: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row.
Note on AJ68: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AK68: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AL68: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AM68: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AN68: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AI69: 6.24.21: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row.
Note on AJ69: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AK69: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AL69: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AM69: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AN69: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on AI70: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row.
Note on H72: 2019 Update: Added new unit to dropdown for CRACs
Note on AI75: NEED TO UPDATE IN FORM AND SCHEMA Column 07 upper should be SEER & Column 08 upper should be "14.0" & column 04 should be HSPF & column 05 should be "8.2" From Table C-4
Note on AJ75: NEED TO UPDATE IN FORM AND SCHEMA Column 07 upper should be SEER & Column 08 upper should be "14.0" & column 04 should be HSPF & column 05 should be "8.0" From Table C-4
Note on AI78: 7/30/20 - New Size Category Cooling Mode Efficiency = 12.2 EER Heating Mode Efficiency = 4.3 COP
Note on AJ78: Sally Blair: this would result in the Cooling Mode eff. Of 18.0 EER & the heating mode eff. Of 3.7 COP.
Note on AK78: Sally Blair: this would result in the Cooling Mode eff. Of 14.1 EER & the heating mode eff. Of 3.2 COP.
Note on AL78: Sally Blair: this would result in the Cooling Mode eff. Of 10.6 EER & the heating mode eff. Of 3.7 COP.
Note on AM78: Sally Blair: this would result in the Cooling Mode eff. Of 16.3 EER & the heating mode eff. Of 3.1 COP.
Note on AN78: Sally Blair: this would result in the Cooling Mode eff. Of 12.1 EER & the heating mode eff. Of 2.5 COP.
Note on A79: Sally Blair: This table only shows up if "PTAC/PTHP" is selected in Eq Sizing Table above. Otherwise, user shouldn't see this at all (including title).
Note on AI79: 7/30/20: SIZE RANGE CHANGE ON 7/30 Ben, in Table 110.2-B, this would result in the Cooling Mode eff. Of 13.0 EER & the heating mode eff. Of 4.3 COP.
Note on AI80: Sally Blair: Ben, in Table 110.2-B, this would result in NO Cooling Mode eff. (ie, so grey that column out) & the heating mode eff. Of 2.90 COP.
Note on AG83: 2019 Update: For heating mode only, the dropdown choices in light purple would trigger two choices in the drop down for rating condition in column 03 of the Dry System Equipment Efficiency (other than PTAC and PTHP) subtable: - 47oFdb/43oFwb OSA - 17oFdb/15oFwb OSA Otherwise, column 03 stays grey & blank
Note on AI83: 2019 Update: For all sizes, if selected column 04 dropdown is "COP" and column 05 is "0.72" and column 07 is "COP" in the upper row and blank in the lower row & column 08 is "0.60" in the upper row & blank in the lower row.
Note on AJ83: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Tabe C-3.
Note on AK83: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AL83: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AM83: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-3
Note on AN83: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AO83: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AP83: NEEDS TO BE UPDATED IN FORM & SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "7.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. Table C-3
Note on A84: Sally Blair: Anything designated as "PTAC/PTHP" transfers to this table. Everything else does not.
Note on C84: October 2019 Updates: Calculated field: PTHP: Newly constructed or newly conditioned- if column 02 < 7 = 3.3 if column 02 >=7 and <= 15 = 3.7 - (0.052 x column02) if column 02 > 15 = 2.9 PTHP: replacement- if column 02 < 7 = 2.7 if column 02 >=7 and <= 15 = 2.9 - (0.026 x column02) if column 02 > 15 = 2.5
Note on D84: Sally Blair: If nothing is entered in Column 10 above in the Sizing Table, columns 02-04 here grey out.
Note on F84: Ocotber 2019 Updates: Calculated field: PTHP: Newly constructed or newly conditioned- if column 05 < 7 = 11.9 if column 05 >=7 and <= 15 = 14 - (0.3 x column05) if column 05 > 15 = 9.5 PTHP: replacement- if column 05 < 7 = 9.3 if column 05 >=7 and <= 15 = 10.8 - (0.213 x column05) if column 05 > 15 = 7.6 PTAC: Newly constructed or newly conditioned- if column 05 < 7 = 11.9 if column 05 >=7 and <= 15 = 14 - (0.3 x column05) if column 05 > 15 = 9.5 PTAC: replacement- if column 05 < 7 = 9.4 if column 05 >=7 and <= 15 = 10.9 - (0.213 x column05) if column 05 > 15 = 7.7
Note on G84: Sally Blair: If nothing is entered in Column 11 above in the Sizing Table, columns 05-07 here grey out.
Note on AJ84: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AK84: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AL84: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AM84: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AN84: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AO84: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.4" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.1" in the lower row.
Note on AJ85: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AK85: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AL85: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AM85: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AN85: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AO85: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.6" in the upper row & "13.5" in the lower row.
Note on AJ86: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AK86: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AL86: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AM86: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AN86: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AO86: 6.29.21 If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.5" in the lower row.
Note on AI95: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.0"
Note on AJ95: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.0" & column 04 should be COP & column 05 should be "3.3"
Note on AI96: Sally Blair: Column 07 upper should be EER & Column 08 upper should be "10.0"
Note on AJ96: Sally Blair: Column 07 upper should be EER & Column 08 upper should be "10.0" & column 04 should be COP & column 05 should be "3.0"
Note on AI97: Sally Blair: Column 07 upper should be EER & Column 08 upper should be "10.0"
Note on AJ97: Sally Blair: Column 07 upper should be EER & Column 08 upper should be "10.0" & column 04 should be COP & column 05 should be "3.0"
Note on K99: 6.8.22 = 90% if sum of rated input capacity >=1,000,000 excluding individual boilers < 300,000 Else gray/blank
Note on D100: 11/18/22 if sum of rated input capacity >=1,000,000 excluding individual boilers < 100,000 System Efficiency = (sum (Rated Efficiency x input capacity))/ total input capacity of boilers > between 1million and 10 million btu/h else = gray/blank
Note on I100: 6.3.22 Always = 90% if not grayed out
Note on I104: Sally Blair: If NA selected AND Col 03 Qty is greater than 1, Table D needs to return Item #6 "Table F indicates more than one boiler" error on the Table D tab.
Note on J104: Sally Blair: If "NA: ≤ 500,000 Btu/h" selected AND rated capacity is EITHER >500,000 to 2,500,000 OR > 2,500,000 in Col 04, Table D needs to return the Item #7 "Table F indicates a boiler with" error on the Table D tab.
Note on AI104: Sally Blair: Column 07 upper should be SEER & Column 08 upper should be "13.0"
Note on AI105: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.2" Column 07 lower should be IEER & Column 08 lower should be "15.5"
Note on AI106: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "11.0" Column 07 lower should be IEER & Column 08 lower should be "14.9"
Note on AI107: 2019 Update: Column 07 upper should be EER & Column 08 upper should be "10.0" Column 07 lower should be IEER & Column 08 lower should be "13.9"
Note on AI109: Sally Blair: For heating mode only, the 3 selections highlighted in pink would trigger two choices in the drop down for rating condition: - 47oFdb/43oFwb OSA - 17oFdb/15oFwb OSA
Note on AI110: Sally Blair: If chosen, column 07 upper is "SEER" and column 07 lower is blank. Column 08 upper is "13.0" and column 08 lower is blank. AND column 04 is "HSPF" dropdown choice and column 05 is "7.7"
Note on AJ110: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "12.0" and column 08 lower is "16.0". AND column 04 is "COP" dropdown choice and column 05 is "4.3"
Note on AK110: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "16.2" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.6"
Note on AL110: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "13.4" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.1"
Note on AI111: 2019 Update: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "11.0" and column 08 lower is "14.6". AND column 04 is "COP" dropdown choice and column 05 is: "3.3" if column 02 is "47oFdb/43oFwb OSA" "2.25" if column 02 is "17oFdb/15oFwb OSA"
Note on AJ111: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "12.0" and column 08 lower is "16.0". AND column 04 is "COP" dropdown choice and column 05 is "4.3"
Note on AK111: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "13.8" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "3.3"
Note on AL111: Sally Blair: If chosen, column 07 upper is "EER" and column 07 lower is blank. Column 08 upper is "11.0" and column 08 lower is blank. AND column 04 is "COP" dropdown choice and column 05 is "2.8"
Note on AI112: 2019 Update: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.6" and column 08 lower is "13.9". AND column 04 is "COP" dropdown choice and column 05 is: "3.2" if column 02 is "47oFdb/43oFwb OSA" "2.05" if column 02 is "17oFdb/15oFwb OSA"
Note on AJ112: 6.29.21 If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.0" and column 08 lower is "14.0". AND column 04 is "COP" dropdown choice and column 05 is "4.0"
Note on O113: 2019 Update: Remove these two dropdown choices from "Furnace + AC" & only use with "Furnace/ Unit heater"
Note on AI113: 2019 Update: If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "9.5" and column 08 lower is "12.7". AND column 04 is "COP" dropdown choice and column 05 is: "3.2" if column 02 is "47oFdb/43oFwb OSA" "2.05" if column 02 is "17oFdb/15oFwb OSA"
Note on AJ113: 2019 Update: New size category for 2019. If chosen, column 07 upper is "EER" and column 07 lower is "IEER". Column 08 upper is "10.0" and column 08 lower is "12.0". AND column column 04 is "COP" dropdown choice and column 05 is "3.9"
Note on AI116: 6.29.21 This is the only instance where the "Efficiency Unit" under heating mode needs to be a dropdown. The two choices are: - AFUE - Et If "AFUE" chosen, column 05 is "0.78" If "Et" chosen, column 05 is "0.81"
Note on AJ116: Sally Blair: If chosen, column 04 is "Ec" dropdown choice and column 05 is "0.80"
Note on AK116: Sally Blair: If chosen, column 04 is "Ec" dropdown choice and column 05 is "0.80"
Note on AI117: 6.29.21 If chosen, column 04 is "Et" dropdown choice and column 05 is "0.82"
Note on AI120: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.81"
Note on AJ120: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.80"
Note on AI123: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.75"
Note on AJ123: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.65"
Note on AK123: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.57"
Note on AL123: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.61"
Note on AI124: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.76"
Note on AJ124: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.66"
Note on AK124: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.58"
Note on AL124: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.66"
Note on AJ125: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.67"
Note on AL125: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.67"
Note on AL126: Sally Blair: If chosen, column 04 is "AFUE" and column 05 is "0.68"
Note on AI128: 2019 Update: Divided all of these choices into "downflow" and "upflow"
Note on AI129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.2" in the upper row & blank in the lower row.
Note on AJ129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.09" in the upper row & blank in the lower row.
Note on AK129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.6" in the upper row & blank in the lower row.
Note on AL129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.49" in the upper row & blank in the lower row.
Note on AM129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.55" in the upper row & blank in the lower row.
Note on AN129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.44" in the upper row & blank in the lower row.
Note on AO129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.5" in the upper row & blank in the lower row.
Note on AP129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.39" in the upper row & blank in the lower row.
Note on AQ129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.45" in the upper row & blank in the lower row.
Note on AR129: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.34" in the upper row & blank in the lower row.
Note on AI130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.1" in the upper row & blank in the lower row.
Note on AJ130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AK130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.5" in the upper row & blank in the lower row.
Note on AL130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.39" in the upper row & blank in the lower row.
Note on AM130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.45" in the upper row & blank in the lower row.
Note on AN130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.34" in the upper row & blank in the lower row.
Note on AO130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.15" in the upper row & blank in the lower row.
Note on AP130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.04" in the upper row & blank in the lower row.
Note on AQ130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.10" in the upper row & blank in the lower row.
Note on AR130: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AI131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.9" in the upper row & blank in the lower row.
Note on AJ131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.79" in the upper row & blank in the lower row.
Note on AK131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.4" in the upper row & blank in the lower row.
Note on AL131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.29" in the upper row & blank in the lower row.
Note on AM131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.35" in the upper row & blank in the lower row.
Note on AN131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.24" in the upper row & blank in the lower row.
Note on AO131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.10" in the upper row & blank in the lower row.
Note on AP131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.99" in the upper row & blank in the lower row.
Note on AQ131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "2.05" in the upper row & blank in the lower row.
Note on AR131: Sally Blair: If selected column 07 is "SCOP" in the upper row and blank in the lower row & column 08 is "1.94" in the upper row & blank in the lower row.
Note on AI137: 2019 Update: Taking "/single package" out of this choice
Note on AJ137: 01.09.20 Update: Completely new set of dropdowns and efficiencies.
Note on AN137: 2019 Update: Taking out "split/" in both of these choices.
Note on AI138: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AJ138: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AI139: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AJ139: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "12.2" F.08 Lower Row = "14"
Note on AM139: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AN139: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AI140: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AJ140: 01.09.20 Update Heating Efficiency = ".81" Efficiency Unit = "AFUE" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AM140: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on AN140: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11" F.08 Lower Row = "14"
Note on G142: 7/5/23 If 02 == air source heat pump or heat recovery chiller, this field is BlankGrayedOut
Note on AI142: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AJ142: 01.09.20 Update Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "SEER" F.08 Upper Row = "11.7" F.08 Lower Row = "14"
Note on AN142: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI143: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AJ143: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AN143: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11.2" F.08 Lower Row = "14.8"
Note on F144: 6/22/23 Blank/gray unless 02 == Heat Recovery Chiller or Air Source Heat Pump
Note on J144: 11/11/24 Ben, if Path B says "NA", then lets use Path A values to document MM. They restructured the Heat Pump and Heat Recovery Chiller Table in 110.2. The restructure isn't in it self supposed to be substantive, but the values have also changed in addition to the restructure
Note on K144: 11/11/24: Ben, if Path B says "NA", then lets use Path A values to document MM. Units have changed for 2025
Note on N144: 12/11/24 = "Four Pipe Fan Coil" If F02 = AWHP in connection with system that selected option 2 = "VAV" if F02 = AWHP in connection with system that selected option 3 else BlankGrayedOut
Note on AI144: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AJ144: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.2" in the upper row & "14.8" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AM144: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AN144: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on I145: Sally Blair: If there is only one value required by Table 110.2-D (ex. COP), then these three cells in 06/07/08 grey out.
Note on J145: 11/11/24 Ben, if Path B says "NA", then lets use Path A values to document MM. They restructured the Heat Pump and Heat Recovery Chiller Table in 110.2. The restructure isn't in it self supposed to be substantive, but the values have also changed in addition to the restructure
Note on K145: 11/11/24: Ben, if Path B says "NA", then lets use Path A values to document MM. Units have changed for 2025
Note on AI147: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AJ147: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AM147: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11" F.08 Lower Row = "14.2"
Note on AN147: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "11" F.08 Lower Row = "14.2"
Note on AI148: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AJ148: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AM148: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AN148: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI149: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AJ149: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AM149: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "10" F.08 Lower Row = "13.2"
Note on AN149: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "10" F.08 Lower Row = "13.2"
Note on AI150: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AJ150: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.0" in the upper row & "13.2" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AM150: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "AFUE" dropdown choice and column 05 is "0.81"
Note on AN150: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AI151: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".80" Efficiency Unit = "AFUE"
Note on AJ151: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. Heating Efficiency = ".81" Efficiency Unit = "AFUE"
Note on AM151: 6.24.21 Heating Efficiency = ".80" Efficiency Unit = "Et" Cooling Efficiency: F.07 Upper Row = "EER" F.07 Lower Row = "IEER" F.08 Upper Row = "9.7" F.08 Lower Row = "12.5"
Note on L152: Sally Blair: If NA selected AND Col 03 Qty is greater than 1, Table D needs to return the Row 19 error on the Table D tab.
Note on AI152: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on AJ152: 6.24.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.7" in the upper row & "12.5" in the lower row. If chosen, column 04 is "Et" dropdown choice and column 05 is "0.80"
Note on M154: 2019 Update: Added new NA choice for new exception for Healthcare facilities.
Note on AI157: 2019 Update: These are new categories.
Note on AI158: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "11.0" in the upper row & blank in the lower row.
Note on AJ158: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.0" in the upper row & blank in the lower row.
Note on AK158: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.5" in the upper row & blank in the lower row.
Note on AL158: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.4" in the upper row & blank in the lower row.
Note on AM158: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.8" in the upper row & blank in the lower row.
Note on AN158: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AI159: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.9" in the upper row & blank in the lower row.
Note on AJ159: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.6" in the upper row & blank in the lower row.
Note on AM159: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AN159: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "8.7" in the upper row & blank in the lower row.
Note on AI160: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "10.7" in the upper row & blank in the lower row.
Note on AJ160: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.5" in the upper row & blank in the lower row.
Note on AI161: 2019 UPdate: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.4" in the upper row & blank in the lower row.
Note on AJ161: 2019 UPdate: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.3" in the upper row & blank in the lower row.
Note on AI162: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.0" in the upper row & blank in the lower row.
Note on AJ162: 2019 Update: If selected column 07 is "EER" in the upper row and blank in the lower row & column 08 is "9.4" in the upper row & blank in the lower row.
Note on AI171: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "13.7" in the lower row
Note on AJ171: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.9" in the upper row & "12.1" in the lower row
Note on AK171: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.5" in the upper row & "11.8" in the lower row
Note on AL171: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AM171: Sally Blair: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "13.5" in the upper row & "14.0" in the lower row
Note on AI172: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.3" in the upper row & "13.7" in the lower row
Note on AJ172: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.8" in the upper row & "12.0" in the lower row
Note on AI173: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.2" in the upper row & "13.4" in the lower row
Note on AJ173: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.7" in the upper row & "11.9" in the lower row
Note on P174: 3.24.22 If DOAS is selectedd 04-11 gray out and no efficiency table is triggered.
Note on AI174: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "12.0" in the upper row & "13.3" in the lower row
Note on AJ174: 6/15/20 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.5" in the upper row & "11.7" in the lower row
Note on F175: 9.20.22 = gray/blank when: 02 = air cooled or air source heat pump Otherwise see custom dropdown scenarios below.
Note on J175: 11/11/24 Lookup based on Table 110.2-H 2025 code updated the values in 110.2-H
Note on P175: 3.24.22 If DX-DOAS is selected the DX-DOAS table is triggered
Note on H176: 6.1.22: col 06 & 08 ISCOP row grey out when "Air cooled" OR "Water cooled" selected in col02.
Note on AI177: 2019 Update: These are all new categories for "Unitary AC/ Condensers" so these sizing dropdowns need to be added.
Note on AI178: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "12.2" in the lower row. From Table C-3
Note on AJ178: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AK178: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AL178: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.0" in the lower row. From Table C-3
Note on AM178: 01/09/2020 Update: Column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "13.0" in the upper row & blank in the lower row.
Note on AN178: 2019 update: If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AO178: NEEDS TO BE UPDATED IN FORM AND SCHEMA If selected column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AI179: 2019 Update: If selected column 07 is "SEER" in the upper row and "EER" in the lower row & column 08 is "14.0" in the upper row & "11.7" in the lower row. From Table C-3
Note on AJ179: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AK179: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AL179: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AM179: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AN179: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AI180: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "11.0" in the upper row & "14.6" in the lower row.
Note on AJ180: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AK180: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AL180: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AM180: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AN180: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on F181: 11/11/24 Custom Dropdown when 02=Water Cooled Chilled Water category was removed from Table 110.2-H so this dropdown is no longer needed
Note on AI181: 6.29.21 If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "14.0" in the lower row.
Note on AJ181: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AK181: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AL181: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AM181: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AN181: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AI182: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.8" in the upper row & "13.0" in the lower row.
Note on AJ182: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AK182: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AL182: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AM182: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AN182: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on AI183: 6/15/20: If selected column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.5" in the upper row & "12.3" in the lower row.
Note on F185: 3.14.22 Custom Dropdown when 02=Water Source Heat Pump
Note on AI186: Added 6/15/20: Ben, in Table 110.2-B, this would result in the Cooling Mode eff. Of 12.8 EER & the heating mode eff. Of 4.3 COP.
Note on AJ186: Sally Blair: this would result in the Cooling Mode eff. Of 17.8 EER & the heating mode eff. Of 3.7 COP.
Note on AK186: Added 6/15/20: this would result in the Cooling Mode eff. Of 13.9 EER & the heating mode eff. Of 3.2 COP.
Note on AL186: Added 6/15/20: this would result in the Cooling Mode eff. Of 10.4 EER & the heating mode eff. Of 3.7 COP.
Note on AM186: Added 6/15/20: this would result in the Cooling Mode eff. Of 16.1 EER & the heating mode eff. Of 3.1 COP.
Note on AN186: Added 6/15/20: this would result in the Cooling Mode eff. Of 11.9 EER & the heating mode eff. Of 2.5 COP.
Note on AI187: Sally Blair: Ben, in Table 110.2-B, this would result in NO Cooling Mode eff. (ie, so grey that column out) & the heating mode eff. Of 2.90 COP.
Note on AI191: 2019 Update: For all sizes, if selected column 04 dropdown is "COP" and column 05 is "0.72" and column 07 is "COP" in the upper row and blank in the lower row & column 08 is "0.60" in the upper row & blank in the lower row.
Note on AJ191: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Tabe C-3.
Note on AK191: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AL191: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AM191: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-3
Note on AN191: NEED TO UPDATE FORM AND SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "8.0" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "14.0" in the upper row & blank in the lower row. From Table C-4
Note on AO191: 2019 Update: If selected column 04 dropdown is "HSPF" and column 05 is "7.4" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. From Table C-3
Note on AP191: NEEDS TO BE UPDATED IN FORM & SCHEMA If selected column 04 dropdown is "HSPF" and column 05 is "7.2" and column 07 is "SEER" in the upper row and blank in the lower row & column 08 is "12.0" in the upper row & blank in the lower row. Table C-3
Note on A192: 3.14.22 This table is triggered when Dual Fuel Heat Pump is selected in System Sizing Table above
Note on AJ192: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AK192: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AL192: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AM192: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AN192: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AO192: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.3" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.25" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.8" in the upper row & "12.0" in the lower row.
Note on AJ193: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AK193: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AL193: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AM193: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AN193: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AO193: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "10.4" in the upper row & "11.4" in the lower row.
Note on AJ194: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AK194: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AL194: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AM194: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AN194: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on AO194: Added 6/15/20: If selected column 04 dropdown is "COP" and column 05 is "3.2" if "47oFdb/43oFwb OSA" is selected in column 03, or "2.05" if "17oFdb/15oFwb OSA" is selected in column 03. Column 07 is "EER" in the upper row and "IEER" in the lower row & column 08 is "9.3" in the upper row & "10.4" in the lower row.
Note on A196: 3.14.22 Bring in system name for DFHP systems
Note on E196: Sally Blair: This is only a dropdown if column 03 in Dry System Equipment Sizing table is any of the following: - "VRF heat pump, air cooled" - "Air cooled, split" - "Air cooled, split, space constrained" - "Air cooled, packaged" - "Air cooled, packaged, space constrained" Otherwise this cell greys out.
Note on G196: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on AI197: 6.3.22 Blank/Gray
Note on AJ197: 6.3.22 2.08 COP
Note on AK197: 6.3.22 2.01 COP
Note on AL197: 6.3.22 2.04 COP
Note on AM197: 6.3.22 1.86 COP
Note on AN197: 6.3.22 1.89 COP
Note on AO197: 6.3.22 1.82 COP
Note on AP197: 6.3.22 1.85 COP
Note on G198: 6/24/2022 There are changes to the minimum values. See 110.2 Tables
Note on AI198: 6.3.22 2.02 COP
Note on AJ198: 6.3.22 2.05 COP
Note on AK198: 6.3.22 1.97 COP
Note on AL198: 6.3.22 2.00 COP
Note on AM198: 6.3.22 1.83 COP
Note on AN198: 6.3.22 1.86 COP
Note on AO198: 6.3.22 1.78 COP
Note on AP198: 6.3.22 1.81 COP
Note on AI199: 6.3.22 1.92 COP
Note on AJ199: 6.3.22 1.94 COP
Note on AK199: 6.3.22 1.87 COP
Note on AL199: 6.3.22 1.89 COP
Note on AM199: 6.3.22 1.73 COP
Note on AN199: 6.3.22 1.75 COP
Note on AO199: 6.3.22 1.68 COP
Note on AP199: 6.3.22 1.70 COP
Note on F201: Sally Blair: This needs to be a custom dropdown which only includes the unit relevant to the equipment type chosen. There's only one instance where they get to choose- Warm Air Central Furnace, Gas fired.
Note on AI202: 6.3.22 2.38 COP
Note on AJ202: 6.3.22 2.41 COP
Note on AK202: 6.3.22 2.33 COP
Note on AL202: 6.3.22 2.36 COP
Note on AM202: 6.3.22 1.97 COP
Note on AN202: 6.3.22 2.00 COP
Note on AO202: 6.3.22 1.92 COP
Note on AP202: 6.3.22 1.95 COP
Note on AI203: 6.3.22 2.38 COP
Note on AJ203: 6.3.22 2.31 COP
Note on AK203: 6.3.22 2.23 COP
Note on AL203: 6.3.22 2.26 COP
Note on AM203: 6.3.22 1.93 COP
Note on AN203: 6.3.22 1.98 COP
Note on AO203: 6.3.22 1.88 COP
Note on AP203: 6.3.22 1.93 COP
Note on AI204: 6.3.22 2.18 COP
Note on AJ204: 6.3.22 2.20 COP
Note on AK204: 6.3.22 2.13 COP
Note on AL204: 6.3.22 2.16 COP
Note on AM204: 6.3.22 1.78 COP
Note on AN204: 6.3.22 1.81 COP
Note on AO204: 6.3.22 1.73 COP
Note on AP204: 6.3.22 1.76 COP
Note on F224: 6.1.22: Need to add new value for >=4.5 gpm/hp for Propeller/axial fan dry cooler in col 02.
Note on H224: Update 9.29.20: Updated code reference numbers for 08-10
Note on F226: 12/11/24 For user selection of "Axial fan open-circuit tower, CW loop in CHW plant >= 900gpm" in F02 & 2-15 in A02, this = 42.1 in CZ1, 70 in CZ2, 4, 5, 12, 60 in CZ3, 11, 14, 60 in CZ6-10, 13, 15 For user selection of "Axial fan open-circuit tower, CW loop in CHW plant >= 900gpm" in 02 & 1 or 16 in A02, this = "42.1". For user selection of "Replacement axial fan open-circuit tower, CW loop in CHW plant >= 900gpm" this needs to be "42.1"
Note on I226: Sally Blair: Grey out if anything other than open-circuit towers is selected in 02.
Note on K226: Sally Blair: Grey out if anything other than open-circuit towers is selected in 02.
Note on L226: Sally Blair: grey out if "Air cooled condenser" is selected in column 02
Note on B229: 2019 Update: two new options added for 2019
Note on B238: Updated 9.29.20: If Waterside Economizer chosen, grey and blank columns 03-10.
Note on E243: Sally Blair: If any choice is selected, Table D needs to return the Row 20 error on the Table D tab.
Note on A255: Balneg, Ronald@Energy: Unsure if this is needed. This was intended for hospitals, large offices, schools. Don't think any MF will trigger this for this code cycle.
Note on A256: 12/11/24 Always shows up when Table F is in scope and indicates if HR is required or not in the table.
Note on G258: 12/11/24 If F06 = required and F04>= 500kbtu then this text shows up Else if F06 = required and F04 < 500kbtu, then this text shows up without the heat or preheat service water heating part else if F06 - not required, this field in BlankGrayedOut
Note on F259: 12/11/24 = "Required" if: A.02 != 15 And F04 >= 600 kbtuh AND F02 + 0.1 * (F03 - F02) >= 2400 kbtu AND F04 + F05 >= 2200 kbtu OR F03 >= 3600 kbtu AND F04 + 0.1 * F05 >= 700 kBtu Else = "Not Required"

## G. Pumps
| User input |  |  | auto calculated |  |  | From another Table | From look up table
G. PUMPS
[d:OnlyUI] Table Instructions: Complete the following pump schedule to show compliance with Prescriptive hydronic system requirements found in §140.4(k)& §170.2(c)4I applicable to pumps < 5hp. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with Prescriptive hydronic system requirements found in §140.4(k) & §170.2(c)4I applicable to pumps < 5hp. [d:/OnlyRG]
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Name or Item Tag | Equipment Type | Qty | HP | Controls per §140.4(k) & §170.2(c)4I
|  |  |  | Variable Flow | Hydronic Heat Pump Isolation | VSD on Pumps > 5HP | Differential Pressure Sensor
| Dropdown |  |  | Dropdown | Dropdown | Dropdown | Says "Required" if 07 says "Yes"
|  |  |  | Reset | Add Row | Remove Last
Equipment Type
| Primary chilled water |  |  | VF Dropdown | WLHP Dropdown | VSD Dropdown
| Secondary chilled water |  |  | Yes | Yes | Yes
| Primary heating hot water |  |  | NA: < 3 control valves | NA: Not connected to common water loop | NA: Not serving variable flow system
| Secondary heating hot water |  |  | NA: pump system < 1.5 hp | NA: No hydronic heat pump | NA: Condenser water serving only water-cooled chillers
Tertiary heating hot water
Condenser water
Note on E8: Sally Blair: Grey out if user selects "condenser" in column 02 because this only applies to CHW and HHW
Note on F8: Sally Blair: Grey out user chooses either CHW or HHW in column 02.
Note on G8: Sally Blair: grey out if < 5 hp in column 04 OR if HHW selected in column 02

## H. Fan Systems (NRCC)
Note - THIS WHOLE TABLE IS NEW FOR 2022 |  |  |  | Note - This table is showing two fans as an example. You can have multiple fans per fan system, and you can have multiple fan systems within the table.
H. FAN SYSTEMS & AIR ECONOMIZERS
This table is used to demonstrate compliance with prescriptive requirements found in §140.4(c), §140.4(e) §140.4(m), §170.2(c)3 & §170.2(c)4A for fan systems. Fan systems serving only process loads are exempt from these requirements and do not need to be included in Table H
System Name: |  | Quantity |  | Fan System Status: |  | System Zoning |  | Serving Dwelling Units |  | Fan System Airflow(cfm) |  | Site Elevation |  | Economizer | Dropdown
01 | 02 | 03 | 04 | [5 empty] | 05 | 06 | 07 | 08 | 09 | 10 | 11
[11 empty] | Allowance |  | Design
Fan Name or Item Tag | Fan Type | Qty | Components | [5 empty] | Airflow Through Component (%) | Water Gauge (w.g) | Component Allowance | Fan Allowance(watt/cfm)3 | Design Electrical Input Power Method | Motor Nameplate Horsepower | Design Electrical Input Power (kW)
(fan 1) | dropdown |  | Dropdown (component 1) | [7 empty] | component 1 allowance | Fan Allowance | Dropdown | Dropdown
|  |  | (component2) | [7 empty] | component 2 allowance
(fan 2) | dropdown |  | Dropdown (component 1) | [7 empty] | component 1 allowance | Fan Allowance | Dropdown | Dropdown
|  |  | (component2) | [7 empty] | component 2 allowance
Supply Fan Base Allowance(kW): |  |  | Exhuast/Return/Relief/Transfer Fan Base Allowance(kW): | [5 empty] | Total Fan System Allowance(kW)3: |  |  |  | Fan System Electrical Input Power (kW)
1 Fans serving spaces with design background noise goals below NC35
2 Low-turndown single-zone VAV fan system must be capable of and configured to reduce airflow to 50 percent of design airflow and use no more than 30 percent of the design wattage at that airflow. No more than 10 percent of the design load served by the equipment shall have fixed loads.
3 Fan system allowance includes fan system base allowance
4 Filter pressure loss can only be counted once per fan system
5 Complex Fan System means a fan system that combines a signle cabinet fan system with other supply fans, exhaust fans, or both
6 FOOTNOTE: Computer room economizers must meet requirements of §140.9(a) and will be documented on the NRCC-PRC-E document.
7 FOOTNOTE: Indoor fans meeting the requirements of 140.4(a)3D shall turn off when there is no demand for heating or cooling in the space. At 66% air flow the power draw shall be no more than 51% of the fan power at full fan speed and at 33% airflow the power draw shall be no more than 12% of the fan power at full fan speed.
| Fan Type Dropdown |  |  | Status |  | Zoning Dropdown |  | Serving Dwelling Units | [5 empty] | Economizer Dropdown
| supply |  |  | New |  | DOAS <1.0 kW |  | Serving Individual Dwelling Unit | [5 empty] | Fixed Temperature
| relief |  |  | Altered |  | multizone VAV systems |  | Serving Multiple Dwelling Unit | [5 empty] | Fixed Enthalpy
| exhaust |  |  |  |  | all other systems |  | Not Serving Dwelling Units | [5 empty] | Differential Temperature
| return |  |  |  |  | DOAS >= 1.0 kW | [7 empty] | Differential Enthalpy
| Other (vav, transfer) | [12 empty] | Waterside Economizer
| transfer | [12 empty] | NA: < 33 kBtu/h cooling
| >= 3 speeds |  |  | Components Dropdown (Status = New) |  |  |  |  | Use Tables 140.4-A and 140.4-B | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1404prescriptiverequirementsforspaceconditioningsystems.htm#cfansystems1.htm |  |  |  | NA: Special OA filtration
| other |  |  | System serving spaces ≤ 6 floors away |  |  |  |  | Options for Supply Fan in H.02 |  |  |  |  | NA: Multifamily/hotel/motel
|  |  |  | System serving spaces > 6 floors away | [9 empty] | NA: Efficiency per Table 140.4-D
|  |  |  | MERV 13 to MERV 16 Filter upstream of thermal conditioning equipment | [9 empty] | NA: DOAS <54kbtu with EAHR
|  |  |  | MERV 13 to MERV 16 Filter downstream of thermal conditioning equipment | [9 empty] | See NRCC-PRC for details1
|  |  |  | Filtration allowance for > MERV 16 or HEPA Filter | [9 empty] | NA: Altered other than packaged AC or HP< 54kBty/h
|  |  |  | Central Hydronic heating coil | [9 empty] | NA: Controlled Environment Horticulture
|  |  |  | Electric heat | [9 empty] | NA: Increases Overall TDV Energy Use
|  |  |  | Gas heat | [9 empty] | DOAS >54kbtu
|  |  |  | Hydronic/DX cooling coil or heat pump coil | [6 empty] | Method Dropdown | Nameplate |  | NA: Systems Complying with multizone space conditioning requirements of 140.4(a)3ai or ii
|  |  |  | Solid or liquid Desiccant system allowance | [6 empty] | default per Table 140.4-D Variable Speed Drive | ≥1 and <1.5
|  |  |  | Reheat Coil for Dehumidification | [6 empty] | default per Table 140.4-D | ≥1.5 and <2
|  |  |  | Evaporative humidifier/cooler in series with a cooling coil | [6 empty] | manufacturer provided | ≥2 and <3
|  |  |  | 100% outdoor air system | [7 empty] | ≥3 and <5
|  |  |  | Energy recovery 0.50 <= ERR < 0.55 | [7 empty] | ≥5 and <7.5
|  |  |  | Energy recovery 0.55 ≤ ERR <0.60 | [7 empty] | ≥7.5 and <10
|  |  |  | Energy recovery 0.60 ≤ ERR <0.65 | [7 empty] | ≥10 and <15
|  |  |  | Energy recovery 0.65 ≤ ERR <0.70 | [7 empty] | ≥15 and <20
|  |  |  | Energy recovery 0.70 ≤ ERR <0.75 | [7 empty] | ≥20 and <25
|  |  |  | Energy recovery ERR ≥ 0.80 | [7 empty] | ≥25 and <30
|  |  |  | Runaround Loop | [7 empty] | ≥30 and <40
|  |  |  | Gas phase filtration | [7 empty] | ≥40 and <50
|  |  |  | Economizer Return Damper | [7 empty] | ≥50 and <60
|  |  |  | Air blender | [7 empty] | ≥60 and <75
|  |  |  | Sound attenuation section1 | [7 empty] | ≥75 and ≤100
System feeds a terminal unit with a fan with electrical input power < 1kW
Low-turndown single-zone VAV fan systems2
|  |  |  | Exhuast System Base Allowance |  |  |  |  | Options for Exhaust, Return, Relief, Transfer in H.02
Filter (any MERV value)4
Energy Recovery 0.50 ≤ ERR <0.55
Energy Recovery 0.55 ≤ ERR <0.60
Energy Recovery 0.60 ≤ ERR <0.65
Energy recovery 0.65 ≤ ERR <0.70
Energy Recovery 0.70 ≤ ERR <0.75
Energy Recovery 0.75 ≤ ERR <0.80
Energy Recovery >= 0.80
Coil Runaround Loop
Fully Ducted, or Systems that maintain air pressure differential between rooms
Airflow control devices required for space pressurization control
Laboratory and vivarium exhaust system with vertical ducts > 75 ft2
Biosaftey Cabinet
Filters, scrubber or other exhaust treatment
Sound attenuation section
|  |  |  | Additional Component for Altered Fan Systems (this list should be added to the one above used for new systems |  |  |  |  | Use table 141.0-D | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1410additionsalterationsandrepairstoexistingnonresidentia.htm#table1410dadditionalfanpowerallowances.htm
|  |  |  | Supply Fan System |  |  |  |  | Options for Supply Fan in H.02
Supply Fan In-Unit with Adapter Curb
|  |  |  | Exhaust/Relief/Return/Transfer Fan System |  |  |  |  | Options for Exhaust, Return, Relief, Transfer in H.02
Exhaust/Relief/Return/Transfer In-Unit with Adapter Curb
Note - THIS TABLE IS BRAND NEW FOR 2022
H. DWELLING UNIT FAN EFFICACY & ENERGY/HEAT RECOVERY 170.2(c)3B
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12
Fan System Name or Item Tag | Qty | Serving Dwelling Units | Forced Air System | System Airflow (cfm) | Design Power (kW) | Design Watts/CFM §170.2(c)3b | Maximum Watts/CFM §170.2(c)3b | 1ERV/HRV | Design Sensible Recovery/Effectiveness | Required Senisble Recovery/Effectiveness §170.2(c)3biv | 1Recovery Bypass/Directly Economize Controls §170.2(c)3biv
Transfers from Fan And Air Economizer Table | autopopulated from Table H Fan System Quantity | Transfers from Fan And Air Economizer Table (Serving Dwelling Units) | dropdown |  |  |  |  | dropdown
1 CFI = Central Fan Integrated Dwelling Unit
Forced Air System Dropdown
|  |  | Gas Furnace Air Handling Unit |  |  |  |  | ERV/HRV Dropdown |  | Recovery Bypass Dropdown
|  |  | All Other Air Handling Unit |  |  |  |  | ERV Provided |  | Recovery Bypass Provided
|  |  | Not Central Forced AHU |  |  |  |  | HRV Provided |  | Economizer Controls
[8 empty] | NA: CZ 3-10 |  | NA: CFI
NA: CFI
Note - THIS TABLE IS BRAND NEW FOR 2022
H. EXHAUST AIR HEAT RECOVERY 140.4(q), 170.2(c)4o
01 | 02 | 02 | 04 | 05 | 06 | 07 |  | 08 | 09 | 10 | 11
Name or Item Tag | Qty | Hours of Operation Per Year | Design Supply Airflow Rate | Outdoor Airflow | % Outdoor Air at Full Design Airflow | Exemptions to Exhaust Air Heat Recovery Requirement per §140.4(q) & §170.2(c)4o |  | Exhuast Air Heat Recovery §140.4(q) & §170.2(c)4o | Type Of Heat Recovery Rating | Required Recovery Ratio | Energy Recovery Bypass
Populated from Table H Fan System Name | autopopulated from Table H Fan System Quantity | Dropdown | [6 empty] | Dropdown |  | Dropdown
|  | Hours of Operation Dropdown |  |  |  | Exemptions Dropdown |  |  | Type Dropdown |  | Bypass Dropdown
|  | >= 8,000 |  |  |  | No Exemptions Apply |  |  | Sensible Energy Recovery Ratio |  | Energy Recovery Bypass or similar control Installed per 140.4(q)2
|  | <8,000 |  |  |  | NA: Process system serving laboratory and/or factory exhaust |  |  | Enthalpy Recovery Ratio |  | NA: DOAS unit with shut-off capabilities per 140.4(q)2
NA: Serving space not cooled and heated to <60F
NA: >60% outdoor air heating energy provided by site recovered energy in CZ 16
NA: CZ 15 exempt from heating recovery ratio
NA: CZ 01 exempt from cooling recovery ratio
NA: Total airflow exhuasted and relieved within 20ft < 75% per Exception 6 to 140.4(q)
NA: Operating < 20 hours/week
Note - THIS TABLE IS BRAND NEW FOR 2022
Dedicated Outdoor Air System (DOAS)
01 | 02 | 03 | 04 | 05 | 06
Name or Item Tag | Quantity | Delivered Directly To The Space | DOAS Fan Control | Multi-Zone DOAS with Cooling §140.4(p)4 & §170.2(c)4N | Multifamily DOAS
|  | Dropdown | Dropdown | Dropdown | Dropdown
|  | Delivery Dropdown | Fan Control Dropdown | Multi-zone DOAS dropdown | DOAS Dropdown
|  | Yes | >=3 speeds | No heating or heat recovery to warm supply air > 60F when majority of zones require cooling | Not Serving Multifamily Common Use Space
|  | NA: Active Chilled Beam System |  | NA: No Mechanical cooling and heating | Option 1 - 170.2(c)4Nia
|  | NA: Exception 2 per 140.4(p)2/170.2(c)4N |  | NA: Single Zone | Option 2 - 170.2(c)4Nib
|  | NA: Exception 3 per 140.4(p)2/170.2(c)4N |  |  | Option 3 - 170.2(c)4Nic
H. Fan Energy Index (FEI)
01 | 2 |  | 3
Name or Item Tag | FEI Exception |  | FEI
Dropdown
FEI Dropdown
None Applies
Embedded Fan Regulated under 110.2 or 110.1
Computer Room Air Conditioners
DX-DOAS Unit
Embedded Fan < 5HP or < 4.1 kW
Circulating Fan, Ceiling Fan, Air Curtain
Operates Only During Emergencies
Variable Air Volume Fan System
Altered Fan System
Lowrise Multifamily Occupancy
Note on A5: April 2020 Update: Language in the last sentence has been revised to remove language about healthcare.
Note on B6: 12/10/24 If table F is completed, transfer all Table F system names here. Give the option to add more fan systems than there are HVAC systems. If Table F is not in scope, this is user input If Multizone requirement option 1 is selected in F.02, In addition to transferring the system name here, add additional row Named "DOAS serving + name of HVAC system selected as option 1 + Spaces" and for this row, System zoning is limited to DOAS <1.0 kW and DOAS >= 1.0 kW If multizone requirement option 1 or option 2 is selected in F.02, when that system name is transferred here, gray out 04, 05, 06, 07, 08 and Total fan system allowance = Fan System Airflow * 0.35
Note on J6: 4/6/22: If this = "Serving Individual"OR "Serving Multiple" THEN H.01-H.12 AND Fan System Airflow, Site Elevation and Economizer = gray/blank out AND System Name transfers to H.01 of the Dwelling Unit Fan Efficacy
Note on N6: 3.25.22 If >=3,000 feet use the correction factors of Table 140.4C
Note on K11: 8/3/21 Grays out unless H.04 = any of the following: - "Evaporative humidfier/cooler in a series…." - "Gas Phase filtration" - Laboratory or Vivarium - Biosaftey Cabinet - Filters, scrubber or other exhaust treatment
Note on L11: 8.3.21 = allowance from either Table 140.4-A & 140.4-B. Table and column determined by H.02 Fan Type, H.03 System Zoning and System Airflow Use Equation 140.4-A if H.05 is not "100" If H.07 is not gray,H.08 = the value from H.05 * H.07
Note on M11: 8.3.21 = sum for fan all components (H.05 x H.07)
Note on O11: 8.3.21 Gray unless H.09 = default per 140.4-D
Note on P11: 8/3/21 User input if H.09 Method = "manufacturer provided", ELSE automatically calculated based on H.10 selections using Table 140.4-D
Note on L13: 2019 Update: Add Pressure Adj Device duplicates coulumns 07 & 08 (but blank). Remove Last Pressure Adj Device removes the last row added.
Note on L19: 6.20.22 If all Fan System Electrical Input Power rows < 1.0 then Fan System Allowance = blank/grayed out Else = total of fan allowances * their quantity * Fan System Airflow / 1,000 AND If elevation in Table A > 3,000. Multiply * correction factor in Table 140.4-C NOTE: Healthcare facilities have an additional allowance in Table 140.4-B that should be added automatically if Table A includes Healthcare Facility. User will not select this allowance in H.05 ALSO - Base allowances can only be selected once per fan system Base allowances are the first tow options "serving spaces <= or > 6 floors..."
Note on P19: 8.3.21 - sum of design electrical input powers * their quantity
Note on B27: 12/01/24 Helps determine which 140 Table to use. Rows that represent systems that chose multizone option 1 or option 2, Or Rows with system zoning == DOAS <1.0 kW or DOAS > 1.0 kW the only options are vav or >= 3 speeds
Note on G27: 8/3/21 Helps determine which 140 Table to use
Note on G28: 12/9/24 If DOAS is automatically selected based on multizone option 1 in F.02, then 02, 04, 05, 06, 07, 08 grey out and fan system allowance == fan system airflow * .77 Else 02, 04, 05, 06 07 08 grey out and fan system allowance = fan system airflow/1000
Note on E29: 3.30.22 If altered is selected the components dropdown also includes the replacement components and allowances in addition to the new components/allowances.
Note on G31: 12/9/24 If DOAS is automatically selected based on multizone option 1 in F.02, then 02, 04, 05, 06, 07, 08 grey out and fan system allowance == fan system airflow * .77 Else fill out table and calculate fan power allowance as usual
Note on E34: 10/13/21 User can select all that apply
Note on A85: Ben Lalor: Triggers when Table H serving dwelling units = ="Serving individual dwelling units" OR "Serving multiple dwelling units"
Note on A89: 4.6.22 Transfer System Serving Individual or Multiple Dwelling units.
Note on G89: 11/30/21 =(06/ 1,000) /05
Note on H89: 6.8.22 if H.03 = "Individual.." AND A.02 = 1, 2, or 11-16 AND H.04 ="Not Central Forced Air.." AND ERV/HRV="Provided" = 0.60 If H.03 = "Individual..." AND H.04 = "All Others" = .58 If H.03 = "Indivudual..." AND H.04 = "Gas Furnace" = .45 If H.03 = "Multiple" AND A.02 = 1, 2, or 11-16 AND ERV/HRV="Provided" = blank/grey and the fan system transfers to the fan and air economizer table able (needs to meet common area fan power requirements - only for Highrise MF) Else , H.05, H.06, H.07 and H.08= blank/grayed out
Note on K89: 11/30/21 = 67% if 09 = Provided Else = blank/grayed out
Note on L89: 11/30/21 = blank/gray if Serving Dwelling Units = "Individual Dwelling Unit" OR A.02 =3-10 Else dropdown
Note on A105: 6.29.21 Doesn't trigger for Climate Zones 6 and 7, otherwise triggers when Fan Systems are selected in Table B
Note on C109: 8/2/21 Determines which table should be used - 140.4-J or 140.4-K
Note on F109: 3.25.22 = 05 / (04+05)
Note on G109: 7/30/21 If any of the exemptions here are selected, 07 says "Not Required" and 02, 03, 08 09 10 gray out EXCEPT if they use CZ exception special text shows in 08. See logic there.
Note on I109: 12/11/24 Use Table 140.4-J or 140.4-K to determine if EAHR is required or not. Exemptions in H.07 override the tables. If required and heating or cooling exemption not used in H.07, show the appropriate option below. If fan system is connected with a HVAC system that selected multizone requirement package 1 or 2, then don't use the Tables, just require it unless excemption applies. Either: - "Required for both heating and cooling design conditions" - "Not Required" Used this text for heating or cooling exemption in H.07 - "Required for heating design conditions" - "Required for cooling design conditions"
Note on K109: 8/2/21 0.60 if H.08 = "Sensible" 0.50 if H.08 = "Enthalpy"
Note on L109: 4/6/22 "60%" if H.09 = Sensiible "50%" if H.09 = Enthalpy
Note on A127: 12/16/24 Triggers when DOAS is selected in Table F DOAS is selected in Fan Table above
Note on A131: Ben Lalor:
Note on A149: Ben Lalor: Transferred from H.01 Fan and Air Economizer
Note on D149: 5/3/22 This grays out if anything but "None Applies" is selected in column 2.

## H. Fan Systems (LMCC)
Note - THIS WHOLE TABLE IS NEW FOR 2022 |  |  |  | Note - This table is showing two fans as an example. You can have multiple fans per fan system, and you can have multiple fan systems within the table.
H. FAN SYSTEMS & AIR ECONOMIZERS
[d:OnlyUI] Table Instructions: Complete the following Table for fan systems to demonstrate compliance with prescriptive requirements found in §140.4(c), §140.4(e) §140.4(m) §170.2(c)3 & §170.2(c)4A. Fans serving covered process systems such as computer rooms are exempt. First document the system details, then add fans within that system to document compliance with fan power requirements. Fan systems serving only process loads, are exempt from these requirements and do not need to be included in Table H. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with prescriptive requirements found in §140.4(c), §140.4(e) §140.4(m), §170.2(c)3 & §170.2(c)4A for fan systems. Fan systems serving only process loads are exempt from these requirements and do not need to be included in Table H. [d:/OnlyRG]
System Name: |  | Quantity |  | Fan System Status: | Dropdown | System Zoning | Dropdown | Serving Dwelling Units | Dropdown | Fan System Airflow |  | Site Elevation |  | Economizer | Dropdown
01 | 02 | 03 | 04 | [5 empty] | 05 | 06 | 07 | 08 | 09 | 10 | 11
|  | Qty | Components | [5 empty] | Airflow Through Component (%) | Water Gauge (w.g) | Allowance |  | Design
Fan Name or Item Tag | Fan Type | [9 empty] | Component Allowance | Fan Allowance(watt/cfm)3 | Design Electrical Input Power Method | Motor Nameplate Horsepower | Design Electrical Input Power (kW)
(fan 1) | dropdown |  | Dropdown (component 1) | [7 empty] | component 1 allowance | Fan Allowance | Dropdown | Dropdown
|  |  | (component2) | [7 empty] | component 2 allowance
(fan 2) | dropdown |  | Dropdown (component 1) | [7 empty] | component 1 allowance | Fan Allowance | Dropdown | Dropdown
|  |  | (component2) | [7 empty] | component 2 allowance
[9 empty] | Fan System Allowance(kW)3 |  |  |  | Fan System Electrical Input Power (kW)
1 Fans serving spaces with design background noise goals below NC35
2 Low-turndown single-zone VAV fan system must be capable of and configured to reduce airflow to 50 percent of design airflow and use no more than 30 percent of the design wattage at that airflow. No more than 10 percent of the design load served by the equipment shall have fixed loads.
3 Fan system allowance includes fan system base allowance
4 Filter pressure loss can only be counted once per fan system
5 Complex Fan System means a fan system that combines a signle cabinet fan system with other supply fans, exhaust fans, or both
6 FOOTNOTE: Computer room economizers must meet requirements of §140.9(a) and will be documented on the NRCC-PRC-E document.
7 FOOTNOTE: Indoor fans meeting the requirements of 140.4(a)3D shall turn off when there is no demand for heating or cooling in the space. At 66% air flow the power draw shall be no more than 51% of the fan power at full fan speed and at 33% airflow the power draw shall be no more than 12% of the fan power at full fan speed. | [13 empty] | Economizer Dropdown
| Fan Type Dropdown |  |  | Fan System Status |  | Zoning Dropdown |  | Serving Dwelling Units | [5 empty] | Fixed Temperature
| supply |  |  | New |  | DOAS <1.0 kW |  | Serving Individual Dwelling Unit | [5 empty] | Fixed Enthalpy
| relief |  |  | Altered |  | multizone VAV systems |  | Serving Multiple Dwelling Unit | [5 empty] | Differential Temperature
| exhaust |  |  |  |  | all other systems |  | Not Serving Dwelling Units | [5 empty] | Differential Enthalpy
| return |  |  |  |  | DOAS >= 1.0 kW | [7 empty] | Waterside Economizer (See Tbl. F)
| Other (vav, transfer) | [12 empty] | NA: < 33 kBtu/h cooling
| transfer |  |  | Components Dropdown (Status = New) |  |  |  |  | Use Tables 140.4-A and 140.4-B | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1404prescriptiverequirementsforspaceconditioningsystems.htm#cfansystems1.htm |  |  |  | NA: Special OA filtration
| >= 3 speeds |  |  | System serving spaces ≤ 6 floors away |  |  |  |  | Options for Supply Fan in H.02 |  |  |  |  | NA: Multifamily
| other |  |  | System serving spaces > 6 floors away | [9 empty] | NA: Efficiency per Table 140.4-D
|  |  |  | MERV 13 to MERV 16 Filter upstream of thermal conditioning equipment | [9 empty] | NA: DOAS
|  |  |  | MERV 13 to MERV 16 Filter downstream of thermal conditioning equipment | [9 empty] | See NRCC-PRC for details6
|  |  |  | Filtration allowance for > MERV 16 or HEPA Filter | [9 empty] | NA: Altered other than packaged AC or HP< 54kBty/h
|  |  |  | Central Hydronic heating coil | [9 empty] | NA: Controlled Environment Horticulture
|  |  |  | Electric heat | [9 empty] | NA: Increases Overall TDV Energy Use
|  |  |  | Gas heat | [9 empty] | NA: Systems Complying with multizone space conditioning requirements of 140.4(a)3ai or ii
|  |  |  | Hydronic/DX cooling coil or heat pump coil | [6 empty] | Method Dropdown | Nameplate
|  |  |  | Solid or liquid Desiccant system allowance | [6 empty] | default per Table 140.4-D Variable Speed Drive | ≥1 and <1.5
|  |  |  | Reheat Coil for Dehumidification | [6 empty] | default per Table 140.4-D | ≥1.5 and <2
|  |  |  | Evaporative humidifier/cooler in series with a cooling coil | [6 empty] | manufacturer provided | ≥2 and <3
|  |  |  | 100% outdoor air system | [7 empty] | ≥3 and <5
|  |  |  | Energy recovery 0.50 <= ERR < 0.55 | [7 empty] | ≥5 and <7.5
|  |  |  | Energy recovery 0.55 ≤ ERR <0.60 | [7 empty] | ≥7.5 and <10
|  |  |  | Energy recovery 0.60 ≤ ERR <0.65 | [7 empty] | ≥10 and <15
|  |  |  | Energy recovery 0.65 ≤ ERR <0.70 | [7 empty] | ≥15 and <20
|  |  |  | Energy recovery 0.70 ≤ ERR <0.75 | [7 empty] | ≥20 and <25
|  |  |  | Energy recovery ERR ≥ 0.80 | [7 empty] | ≥25 and <30
|  |  |  | Runaround Loop | [7 empty] | ≥30 and <40
|  |  |  | Gas phase filtration | [7 empty] | ≥40 and <50
|  |  |  | Economizer Return Damper | [7 empty] | ≥50 and <60
|  |  |  | Air blender | [7 empty] | ≥60 and <75
|  |  |  | Sound attenuation section1 | [7 empty] | ≥75 and ≤100
System feeds a terminal unit with a fan with electrical input power < 1kW
Low-turndown single-zone VAV fan systems2
|  |  |  | Filter (any MERV value)4 |  |  |  |  | Options for Exhaust, Return, Relief, Transfer in H.02
Energy Recovery 0.50 ≤ ERR <0.55
Energy Recovery 0.55 ≤ ERR <0.60
Energy Recovery 0.60 ≤ ERR <0.65
Energy recovery 0.65 ≤ ERR <0.70
Energy Recovery 0.70 ≤ ERR <0.75
Energy Recovery 0.75 ≤ ERR <0.80
Energy Recovery >= 0.80
Coil Runaround Loop
Fully Ducted, or Systems that maintain air pressure differential between rooms
Airflow control devices required for space pressurization control
Biosaftey Cabinet
Filters, scrubber or other exhaust treatment
Sound attenuation section
|  |  |  | Additional Component for replacement Fan Systems (this list should be added to the one above used for new systems |  |  |  |  | Use table 141.0-D | https://energycodeace.com/site/custom/public/reference-ace-2022/Documents/section1410additionsalterationsandrepairstoexistingnonresidentia.htm#table1410dadditionalfanpowerallowances.htm
|  |  |  | Supply Fan System |  |  |  |  | Options for Supply Fan in H.02
Supply Fan In-Unit with Adapter Curb
|  |  |  | Exhaust/Relief/Return/Transfer Fan System |  |  |  |  | Options for Exhaust, Return, Relief, Transfer in H.02
Exhaust/Relief/Return/Transfer In-Unit with Adapter Curb
Note - THIS TABLE IS BRAND NEW FOR 2022
H. DWELLING UNIT FAN EFFICACY & ENERGY/HEAT RECOVERY 170.2(c)3B
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Fan System Name or Item Tag | Qty | Serving Dwelling Units | Forced Air System | System Airflow (cfm) | Design Power (kW) | Design Watts/CFM §170.2(c)3b | Maximum Watts/CFM §170.2(c)3b | 1ERV/HRV 170.2(c)3biv | Design Sensible Recovery/Effectiveness | 1Required Senisble Recovery/Effectiveness §170.2(c)3biv
Transfers from Fan And Air Economizer Table | autopopulated from Table H Fan System Quantity | Transfers from Fan And Air Economizer Table (Serving Dwelling Units) | dropdown |  |  |  |  | dropdown
1 CFI = Central Fan Integrated Dwelling Unit
|  |  | System Type Dropdown |  |  |  |  | ERV/HRV Dropdown
|  |  | Gas Furnace Air Handling Units |  |  |  |  | ERV Provided
|  |  | All Other Air Handling Units |  |  |  |  | HRV Provided
|  |  | Not Central Forced AHU |  |  |  |  | NA: CZ 3-10
NA: Continuously operating supply/exhuast
Note - THIS TABLE IS BRAND NEW FOR 2022
H. EXHAUST AIR HEAT RECOVERY 140.4(q), 170.2(c)4o
01 | 02 | 03 | 04 | 05 | 06 | 07 |  | 08 | 09 | 10 | 11
Fan System Name | Qty | Hours of Operation Per Year | Design Supply Airflow Rate | Outdoor Airflow | % Outdoor Air at Full Design Airflow | Exemptions to Exhaust Air Heat Recovery Requirement per §140.4(q) & §170.2(c)4o |  | Exhuast Air Heat Recovery §140.4(q) & §170.2(c)4o | Type Of Heat Recovery Rating | Required Recovery Ratio | Energy Recovery Bypass
Populated from Table H Fan System Name | Autopopulated from Fan System Quantity | Dropdown | [6 empty] | Dropdown | "60%" or "50%" | Dropdown
Hours of Operation Dropdown
|  | >= 8,000 |  |  |  | Exemptions Dropdown |  |  | Type Dropdown |  | Bypass Dropdown
|  | <8,000 |  |  |  | No Exemptions Apply |  |  | Sensible Energy Recovery Ratio |  | Energy Recovery Bypass or similar control Installed per 140.4(q)2
[6 empty] | NA: Process system serving laboratory and/or factory exhaust |  |  | Enthalpy Recovery Ratio |  | NA: DOAS unit with shut-off capabilities per 140.4(q)2
NA: Serving space not cooled and heated to <60F
NA: >60% outdoor air heating energy provided by site recovered energy in CZ 16
NA: Total airflow exhuasted and relieved within 20ft < 75% per Exception 6 to 140.4(q)
NA: Operating < 20 hours/week
Note - THIS TABLE IS BRAND NEW FOR 2022
Dedicated Outdoor Air System (DOAS)
01 |  | 03 | 04 | 05 | 06
System Name | Quantity | Delivered Directly To The Space | DOAS Fan Control | Multi-Zone DOAS with Cooling §140.4(p)4 & §170.2(c)4N | MF DOAS
|  | Dropdown | Dropdown | Dropdown | Dropdown
|  | Delivery Dropdown | Fan Control Dropdown | Multi-zone DOAS dropdown | DOAS Dropdown
|  | Yes | >=3 speeds | No heating or heat recovery to warm supply air > 60F when majority of zones require cooling | Not Serving Multifamily Common Use Space
|  | NA: Active Chilled Beam System |  | NA: No Mechanical cooling and heating | Option 1 - 170.2(c)Nia
|  | Exception 2 per 140.4(p)2/170.2(c)4N |  | NA: Single Zone | Option 3 - 170.2(c)Nib
|  | NA: Exception 3 per 140.4(p)2/170.2(c)4N |  |  | Option 3 - 170.2(c)Nic
H. Fan Energy Index (FEI)
01 | 2 |  | 3
Name or Item Tag | FEI Exception |  | FEI
Dropdown
FEI Dropdown
None Applies
Embedded Fan Regulated under 110.2 or 110.1
Computer Room Air Conditioners
DX-DOAS Unit
Embedded Fan < 5HP or < 4.1 kW
Circulating Fan, Ceiling Fan, Air Curtain
Operates Only During Emergencies
Variable Air Volume Fan System
Altered Fan System
Lowrise Multifamily Occupancy
Note on A5: April 2020 Update: Language in the last sentence has been revised to remove language about healthcare.
Note on B6: 12/10/24 If table F is completed, transfer all Table F system names here. Give the option to add more fan systems than there are HVAC systems. If Table F is not in scope, this is user input If Multizone requirement option 1 is selected in F.02, In addition to transferring the system name here, add additional row Named "DOAS serving + name of HVAC system selected as option 1 + Spaces" and for this row, System zoning is limited to DOAS <1.0 kW and DOAS >= 1.0 kW If multizone requirement option 1 or option 2 is selected in F.02, when that system name is transferred here, gray out 04, 05, 06, 07, 08 and Total fan system allowance = Fan System Airflow * 0.35
Note on J6: 4/6/22 If this = "Serving Individual"OR "Serving Multiple" THEN H.01-H.12 AND Fan System Airflow, Site Elevation and Economizer = gray/blank out AND System Name transfers to H.01 of the Dwelling Unit Fan Efficacy
Note on N6: 3.25.22 If >=3,000 feet use the correction factors of Table 140.4C
Note on K11: 8/3/21 Grays out unless H.04= any of the following: - "Evaporative humidfier/cooler in a series…." - "Gas Phase filtration" - Laboratory or Vivarium - Biosaftey Cabinet - Filters, scrubber or other exhaust treatment
Note on L11: 8.3.21 NOTE - One of the allowances in Table 170.2-C is only for highrise and should not be included in the logic here. I have removed it from the components list to the left. = allowance from either Table 140.4-A & 140.4-B. Table and column determined by H.02 Fan Type, H.03 System Zoning and System Airflow Use Equation 140.4-A if H.05 is not "100" If H.07 is not gray,H.08 = the value from H.05 * H.07
Note on M11: 8.3.21 = sum for fan all components (H.05 x H.07)
Note on O11: 8.3.21 Gray unless H.09 = default per 140.4-D
Note on P11: 8/3/21 User input if H.09 Method = "manufacturer provided", ELSE automatically calculated based on H.10 selections using Table 140.4-D
Note on L13: 2019 Update: Add Pressure Adj Device duplicates coulumns 07 & 08 (but blank). Remove Last Pressure Adj Device removes the last row added.
Note on L19: 6.20.22 If fan system electrical input power < 1.0 then Fan System Allowance = blank/grayed out Else = total of fan allowances * their quantity * Fan System Airflow / 1,000 AND If elevation in Table A > 3,000. Multiply * correction factor in Table 140.4-C NOTE: Healthcare facilities have an additional allowance in Table 140.4-B that should be added automatically if Table A includes Healthcare Facility. User will not select this allowance in H.05 ALSO - Base allowances can only be selected once per fan system Base allowances are the first tow options "serving spaces <= or > 6 floors..."
Note on P19: 8.3.21 - sum of design electrical input powers * their quantity
Note on A26: Balneg, Ronald@Energy: Why is this LMCC being changed to accomdate 140.4(a)3 when its specific to office and school buildings? ?
Note on B27: 12/01/24 Helps determine which 140 Table to use. Rows that represent systems that chose multizone option 1 or option 2, Or Rows with system zoning == DOAS <1.0 kW or DOAS > 1.0 kW the only options are vav or >= 3 speeds
Note on G27: 8/3/21 Helps determine which 140 Table to use
Note on G28: 12/9/24 If DOAS is automatically selected based on multizone option 1 in F.02, then 02, 04, 05, 06, 07, 08 grey out and fan system allowance == fan system airflow * .77 Else 02, 04, 05, 06 07 08 grey out and fan system allowance = fan system airflow/1000
Note on E29: 3.30.22 If altered is selected the components dropdown also includes the replacement components and allowances in addition to the new components/allowances.
Note on G31: 12/9/24 If DOAS is automatically selected based on multizone option 1 in F.02, then 02, 04, 05, 06, 07, 08 grey out and fan system allowance == fan system airflow * .77 Else fill out table and calculate fan power allowance as usual
Note on E33: 10/13/21 User can select all that apply
Note on A83: Ben Lalor: Triggers when B.03 = Fan Systems AND A.03 = Multifamily
Note on G87: 11/30/21 =(06/ 1,000) /05
Note on H87: 6.8.22 System Zoning = "multiple dwelling units" AND A.02 = 4-10 AND ERV/HRV= "NA" = 0.4 if H.03 = "Individual.." AND A.02 = 1, 2, or 11-16 AND H.04 ="Not Central Forced Air.." AND ERV/HRV="Provided" = 0.60 If H.03 = "Individual..." AND H.04 = "All Others" = .58 If H.03 = "Indivudual..." AND H.04 = "Gas Furnace" = .45 Else , H.05, H.06, H.07 adn H.08= blank/grayed out
Note on K87: 4.6.22 = 67% if 09 = Provided Else = blank/grayed out
Note on A103: 6.29.21 Doesn't trigger for Climate Zones 6 and 7, otherwise triggers when Fan Systems are selected in Table B
Note on C107: 8/2/21 Determines which table should be used - 140.4-J or 140.4-K
Note on F107: 3.25.22 = 05 / 06
Note on G107: 7/30/21 If any of the exemptions here are selected, 07 says "Not Required" and 02, 03, 08 09 10 gray out EXCEPT if they use CZ exception special text shows in 08. See logic there.
Note on I107: 12/11/24 Use Table 140.4-J or 140.4-K to determine if EAHR is required or not. Exemptions in H.07 override the tables. If required and heating or cooling exemption not used in H.07, show the appropriate option below. If fan system is connected with a HVAC system that selected multizone requirement package 1 or 2, then don't use the Tables, just require it unless excemption applies. Either: - "Required for both heating and cooling design conditions" - "Not Required" Used this text for heating or cooling exemption in H.07 - "Required for heating design conditions" - "Required for cooling design conditions"
Note on K107: 8/2/21 60% if H.08 = "Sensible" 50% if H.08 = "Enthalpy"
Note on L107: 4/6/22 "60%" if H.09 = Sensiible "50%" if H.09 = Enthalpy
Note on A125: 12/16/24 Triggers when DOAS is selected in Table F DOAS is selected in Fan Table above
Note on A129: Ben Lalor:
Note on A147: Ben Lalor: Transferred from H.01 Fan and Air Economizer
Note on D147: 5/3/22 This grays out if anything but "None Applies" is selected in column 2.

## I. Sys Controls (NRCC)
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
I. SYSTEM CONTROLS
[d:OnlyUI] Table Instructions: Complete the following Table to demonstrate compliance with mandatory controls in §110.2 and §120.2 and prescriptive controls in §140.4(f) §140.4(n) §170.2(c)4D, & §170.2(c)4L or requirements in §141.0(b)2E & §180.2(b)2 for altered space conditioning systems. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory controls in §110.2 and §120.2 and prescriptive controls in §140.4(f) and (n) or requirements in §141.0(b)2E for altered space conditioning systems. [d:/OnlyRG]
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
System Name | System Zoning | Conditioned Floor Area Being Served (ft2) | Thermostats §110.2(b), (c)1, §120.2(a), §160.3(a)2a or §141.0(b)2E & §180.2(b)2 | Shut-Off Controls §120.2€ & §160.3(a)2d | Isolation Zone Controls §120.2(g) & §160.3(a)2f | Demand Response §110.12, §120.2(b) & §160.3(a)2b | Supply Air Temp. Reset §140.4(f) & §170.2(c)4d | Window Interlocks per §140.4(n) & §170.2(c)4d | Direct Digital Control (DDC) per 110.12
| See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown
1 FOOTNOTES: Gravity gas wall heaters, gravity floor heaters, gravity room heaters, non-central electric heaters, fireplaces or decorative gas appliances, wood stoves are not required to have setback thermostats.
| System Zoning Dropdown | CFA dropdown | Thermostat Dropdown | Shut Off Dropdown | Isolation Zone Dropdown | Demand Response Dropdown | SA Temp Reset Dropdown | Window Interlock Dropdown | DDC Dropdown
| single zone | < 25,000 ft2 | Setback Thermostat | Auto Timeswitch | Auto Timeswitch | EMCS | Included | Provided | ProvidedDDC controller logic using ASHRAE Guideline 36
| multi-zone | > 25,000 ft2 | EMCS | Occ. Sensor | Occ. Sensor | DR Tstat per §110.12 | NA: Alteration | NA: Auto-closing doors | NA: Single Zone
| multi-zone w/ DDC to zone | NA: Altered per §141.0(b)2E | Setback + DR Tstat per §110.12 | 4 Hour Timer | 4 Hour Timer | NA: PTAC, PTHP, Rm AC, HP | NA: Single Zone | NA: No thermostatic control
|  |  | NA: Eq. type per §110.2(c) exception1 | EMCS | EMCS | NA: Healthcare only | NA: Healthcare only | NA: Alteration project
|  |  |  | Card Key (hotel/motel) | NA: Continuous Heat/Cool | NA: Serves temp. sensitive process | NA: Would increase energy use | NA: No operable windows
|  |  |  | NA: 7 day per §120.2(e)1 | NA: Altered per §141.0(b)2E |  | NA: Serves humidity sensitive process | NA: Healthcare only
|  |  |  | NA: Altered per §141.0(b)2E | NA: Single Zone |  | NA: Controls prevent reheat/recool/simultaneous | NA: Dwelling unit
|  |  |  | NA: Healthcare only | NA: Serves < 25k ft2 |  | NA: Dwelling unit
|  |  |  | NA: Dwelling unit | NA: Dwelling unit
Note on D6: 2019 Update: Added S120.2(a)
Note on G6: 2019 UPDATE: Changed section reference to S110.12 & S120.2(b)
Note on G17: Usability Update: Changed wording
Note on D18: 2019 UPDATE: Removed JA5 choice & NA: Rm AC/HP, added NA: Eq. type option.
Note on G18: Usability Update: changed wording
Note on G19: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on H19: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on E21: Usability Update: Changed wording
Note on I21: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on I22: 2019 UPDATE: Added exemption for HRR
Note on E23: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on H23: Usability Update: Added new "NA" choice
Note on E24: Usability Update: Added new "NA" choice
Note on F24: Usability Update: Added new "NA" choice

## I. Sys Controls (LMCC)
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
I. SYSTEM CONTROLS
[d:OnlyUI] Table Instructions: Complete the following Table to demonstrate compliance with mandatory controls in §110.2 and §120.2 and prescriptive controls in §140.4(f) §140.4(n) §170.2(c)4D, & §170.2(c)4L or requirements in §141.0(b)2E & §180.2(b)2 for altered space conditioning systems. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory controls in §110.2 and §120.2 and prescriptive controls in §140.4(f) and (n) or requirements in §141.0(b)2E for altered space conditioning systems. [d:/OnlyRG]
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
System Name | System Zoning | Conditioned Floor Area Being Served (ft2) | Thermostats §110.2(b), (c)1, §120.2(a), §160.3(a)2a or §141.0(b)2E & §180.2(b)2 | Shut-Off Controls §120.2€ & §160.3(a)2d | Isolation Zone Controls §120.2(g) & §160.3(a)2f | Demand Response §110.12, §120.2(b) & §160.3(a)2b | Supply Air Temp. Reset §140.4(f) & §170.2(c)4d | Window Interlocks per §140.4(n) & §170.2(c)4d | Direct Digital Control (DDC) per 110.12
| See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown | See dropdown
1 FOOTNOTES: Gravity gas wall heaters, gravity floor heaters, gravity room heaters, non-central electric heaters, fireplaces or decorative gas appliances, wood stoves are not required to have setback thermostats.
[6 empty] | Reset | Add System | Remove Last
| System Zoning Dropdown | CFA dropdown | Thermostat Dropdown | Shut Off Dropdown | Isolation Zone Dropdown | Demand Response Dropdown | SA Temp Reset Dropdown | Window Interlock Dropdown | DDC Dropdown
| single zone | < 25,000 ft2 | Setback Thermostat | Auto Timeswitch | Auto Timeswitch | EMCS | Included | Provided | ProvidedDDC controller logic using ASHRAE Guideline 36
| multi-zone | > 25,000 ft2 | EMCS | Occ. Sensor | Occ. Sensor | DR Tstat per §110.12 | NA: Alteration | NA: Auto-closing doors | NA: Single Zone
| multi-zone w/ DDC to zone | NA: Altered per §141.0(b)2E | Setback + DR Tstat per §110.12 | 4 Hour Timer | 4 Hour Timer | NA: PTAC, PTHP, Rm AC, HP | NA: Single Zone | NA: No thermostatic control
|  |  | NA: Eq. type per §110.2(c) exception1 | EMCS | EMCS | NA: Healthcare only | NA: Healthcare only | NA: Alteration project
|  |  |  | NA: 7 day per §120.2(e)1 | NA: Continuous Heat/Cool | NA: Serves temp. sensitive process | NA: Would increase energy use | NA: No operable windows
|  |  |  | NA: Altered per §141.0(b)2E | NA: Altered per §141.0(b)2E |  | NA: Serves humidity sensitive process | NA: Healthcare only
|  |  |  | NA: Healthcare only | NA: Single Zone |  | NA: Controls prevent reheat/recool/simultaneous | NA: Dwelling unit
|  |  |  | NA: Dwelling unit | NA: Serves < 25k ft2 |  | NA: Dwelling unit
NA: Dwelling unit
Note on D6: 2019 Update: Added S120.2(a)
Note on G6: 2019 UPDATE: Changed section reference to S110.12 & S120.2(b)
Note on K6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Alhabibi, Haider@Energy do we need to include the 160.3(b) requirements for defrost and capacity variation with 3rd party thermostats here?
Note on G17: Usability Update: Changed wording
Note on D18: 2019 UPDATE: Removed JA5 choice & NA: Rm AC/HP, added NA: Eq. type option.
Note on G18: Usability Update: changed wording
Note on G19: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on H19: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on E20: Usability Update: Changed wording
Note on I21: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on E22: 2019 UPDATE: Added exemption for Healthcare facilities.
Note on I22: 2019 UPDATE: Added exemption for HRR
Note on E23: Usability Update: Added new "NA" choice
Note on H23: Usability Update: Added new "NA" choice
Note on F24: Usability Update: Added new "NA" choice

## J. Ventilation (NRCC)
|  | User input |  |  | auto calculated |  |  |  | From another Table |  |  | From look up table
J. VENTILATION AND INDOOR AIR QUALITY
[d:OnlyUI] Table Instructions: Complete the following Table to demonstrate compliance with mandatory and prescriptive ventilation requirements in §120.1, §120.2(e)3B, 140.4(p) and 140.4(q) for all nonresidential and hotel/motel and 160.2, 160.3(a)3D, 170.2(a)4N, 170.2(a)4O for high-rise residential occupancies. For alterations, only ventilation systems being altered within the scope of the permit application need to be documented in this table. In lieu of this table, the required outdoor ventilation rates and airflows may be shown on the plans or the calculations can be presented in a spreadsheet. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory ventilation requirements in §120.1 and §120.2(e)3B for all nonresidential, high-rise residential and hotel/motel occupancies. For alterations, only ventilation systems being altered within the scope of the permit application need to be documented in this table. In lieu of this table, the required outdoor ventilation rates and airflows may be shown on the plans or the calculations can be presented in a spreadsheet. [d:/OnlyRG]
01 | ¨ | Check the box if the project is showing ventilation calculations on the plans, or attaching the calculations instead of completing this table.
02 | ¨ | Check this box if the project includes Nonresidenital, Hotel/Motel spaces or Multifamily Common Use Spaces |  |  |  |  | Check this box if the project includes new or altered multifamily dwelling units |  |  |  | ¨
03 | ¨ | Check the box if the project is using natural ventilation in any nonresidential or hotel/motel spaces to meet required ventilation rates per §120.1(c)2.
Nonresidential Hotel/ Motel and Multifamily Common Use Ventilation Systems
04 |  |  | 05 |  |  |  | 06 |  |  | 07
System Name: |  |  | System Design OA CFM Air Flow1 |  |  |  | System Design Transfer Air CFM |  |  | Air Filtration per §120.1(c), §141.0(b)2, 160.2(c)1 and 2
See dropdown
08 | 09 |  | 10 |  | 11 | 12 | 13 | 14 | 15 | 16
Space Name or Item Tag | Mechanical Ventilation Required per §120.1(c)33 & §160.2(c)3 | [6 empty] | Exh. Vent. per §120.1(c)4 & §160.2(c)4 |  | DCV or Occupant Sensor Controls per §120.1(d)3, §120.1(d)5 & §120.2(e)36, §160.2(c)5d, §160.2(c)5e & §160.2(c)diii
| Occupancy Type4 |  | Conditioned Floor Area (ft2) |  | # of showerheads/ toilets | # of people5 | Required Min OA CFM | Required Minimum CFM | Provided per Design CFM
| See dropdown | [8 empty] | DCV | See dropdown
[10 empty] | Occ Sensor | See dropdown
[9 empty] | Reset | Add Occupancy Type | Remove Last
17 | Total System Required Min OA CFM | [5 empty] | sum of col 13 for all spaces in system | 18 | Ventilation for this System Complies? |  | "Yes"/ "No"
1 FOOTNOTES: System CFM should include both mechanical and natural ventilation for the zone/system. | [8 empty] | Reset | Add System | Remove Last
2 Air filtration requirements apply to the following three system types per §120.1(c)1A: space conditioning systems utilizing ducts to supply air to occupiable space; supply-only ventilation systems providing outside air to occupiable space; supply side of balanced ventilation systems including heat recovery and energy recovery ventilation systems providing outside air to occupiable space.
3 Uniform Mechanical Code may have more stringent ventilation requirements; the most stringent code requirement takes precedence.
4 See Standards Tables 120.1-A and 120.1-B.
5 For lecture halls with fixed seating, the expected number of occupants shall be determined in accordance with the California Building Code.
6 §120.2(e)3 requires systems serving rooms that are required by §130.1(c) to have lighting occupancy sensing controls to also have occupancy sensing zone controls for ventilation. Examples of spaces which require lighting occupancy sensors include offices 250ft2 or smaller, multipurpose rooms less than 1,000ft2, classrooms, conference rooms, restrooms, aisles and open areas in warehouses, library book stack aisles, corridors, stairwells, parking garages, and loading and unloading zones, unless excepted by §130.1(c).
7 Air classification and recirculation limitations of air shall be based on the air classification as listed in Table 120.1-A or Table 120.1-C, and in accordance with the requirements of Sections 120.1(g)1 through 4
Multifamily Dwelling Unit Ventilation Systems
¨ | Check the box if the system is using continuous ventilation to meet the ventiliation requirements per §160.2(b)2Aivb2
19 | 20 | 21 | 22 |  | 23 | 24 | 25 | 26 |  | 27
Space Name or Item Tag | Mechanical Ventilation Required per §120.1(b)2 & §160.2(b)2 |  |  |  |  | Ventilation per Design |  | Local Exhaust |  | Air Filtration per 120.1(c) & §160.2(b)1
| Conditioned Floor Area (ft2) | # bedrooms | # dwelling units |  | Required Min OA CFM 1 | Supply Air CFM | Exhaust CFM
[8 empty] | ¨ | Bathroom/Kitchen IAQ | See dropdown
[8 empty] | ¨ | Bathroom/Kitchen IAQ & Vent.
[8 empty] | ¨ | Kitchen Range Hood 2
| 125 | 5 | 10 |  | 487.5 |  |  | ¨ | Bathroom/Ktichen IAQ | See dropdown
[8 empty] | ¨ | Bathroom/Ktichen IAQ & Vent.
[8 empty] | ¨ | Kitchen Range Hood 2
28 | Is this a balanced system? 4 |  |  |  | Yes/No | 29 | Meeting Outside Air Requirements? |  |  |  | Yes/ No
1 FOOTNOTES: Uniform Mechanical Code may have more stringent ventilation requirements; the most stringent code requirement takes precedence. | [8 empty] | Reset | Add Space | Remove Last
2 Kitchen range hood will be verified per NA7.18.1 to confirm model is rated by HVI or AHAM.
3 Air filtration requirements apply to the following three system types per §120.1(b)1A: space conditioning systems utilizing ducts to supply air to occupiable space; supply-only ventilation systems providing outside air to occupiable space; supply side of balanced ventilation systems including heat recovery and energy recovery ventilation systems providing outside air to occupiable space.
4 A balanced ventiltion system provides ventilation airflow to each dwelling-unit at a rate equal to or greater than the required minimum rate, but not more than twenty percent greater.
|  | Column 09- Occupancy Type Dropdown | Minimum Ventilation Rate (cfm/ft2) | Minimum Exhaust Rate (cfm/unit) | Minimum Exhaust Rate (cfm/ft2) | cfm/ft2 for column 13 calc DCV | Minimum Occupant Load Density (persons/1,000ft2) |  |  | Column 07- Air filtration dropdown
|  | All others | 0.15 |  |  |  | 5 |  |  | Provided
|  | Animal imaging (MRI/CT/PET) | 0.15 |  | 0.9 |  | 5 |  |  | NA: Not system type specified in Table J footnote 2
|  | Animal operating rooms | 0.15 |  | 3 |  | 5 |  |  | Evaporative Cooler
|  | Animal postoperative recovery room | 0.15 |  | 1.5 |  | 5
|  | Animal preparation room | 0.15 |  | 1.5 |  | 5
|  | Animal procedure room | 0.15 |  | 2.25 |  | 5
|  | Animal surgery scub | 0.15 |  | 1.5 |  | 5
|  | Animal necropsy | 0.15 |  | 2.25 |  | 5
|  | Art Classroom | 0.15 |  | 0.7 |  | 25
|  | Assembly- multiuse | 0.5
|  | Auditorium seating area | 1.07 0.15 |  |  | 0.15 | 7
|  | Auto-repair room | 0.15 |  | 1.5 | [5 empty] | Coulmn 16- DCV Dropdown
|  | Bank or bank lobby | 0.15 |  |  |  | 5 |  |  |  | Provided per §120.1(d)4
|  | Bank Vault/safe deposit | 0.15 |  |  |  | 5 |  |  |  | NA: Not required per §120.1(d)3
|  | Bar/ cocktail lounge | 0.5 0.2 |  |  | 0.2 | 33 |  |  |  | NA: Space exhaust is > design ventilation rate exception
|  | Barbershop | 0.4 |  | 0.5 0.60 |  | 17 |  |  |  | NA: Processes that generate dust, fumes, etc.& no local exhaust
|  | Barracks sleeping area | 0.15 |  |  |  | 5 |  |  |  | NA: Area <150 ft2 or design occupancy < 10 people
|  | Beauty/ nail salon | 0.4 |  | 0.6 |  | 17
|  | Bedroom/Living room (hotel/motel/dorm) | 0.15 |  |  |  | 3
|  | Bowling alley (seating) | 1.07 0.15 |  |  | 0.15 | 7
|  | Break room | 0.5 0.15 |  |  | 0.15 | 33 |  |  |  | Column 16- Occ Sens Dropdown
|  | Cafeteria/ fast-food dining | 0.5 0.15 |  |  | 0.15 | 33 |  |  |  | Provided per §120.1(d)5
|  | Cells with toilet | 0.15 |  | 1 | [5 empty] | NA: Continously operated per §120.2(e)3 exception
|  | Classroom (age 5-18) | 0.38 0.15 |  |  | 0.15 | 25 |  |  |  | NA: System < 2kW demand + manual shutoff per §120.2(e)3 exception
|  | Classroom (age 9-18) | 0.15 |  |  |  | 25
|  | Coffee station | 0.5 0.15 |  |  | 0.15 | 33 |  |  |  | NA: Hotel/ motel + manual shutoff per §120.2(e)3 exception
|  | Coin-operated Laundry | 0.3 |  |  |  | 17 |  |  |  | NA: Not required space type
|  | Computer (not printing) | 0.15 |  |  |  | 5
|  | Computer Lab | 0.15 |  |  |  | 25
|  | Conference/ meeting | 0.5 0.15 |  |  | 0.15 | 33
|  | Copy/ printing room | 0.15 |  | 0.5
|  | Corridor | 0.15 |  |  |  | 5 |  |  |  | Column 27- Air filtration dropdown
|  | Courtroom | 0.19 0.15 |  |  | 0.15 | 13 |  |  |  | Provided
|  | Darkroom | 0.15 |  | 1 | [5 empty] | NA: Evaporative Cooler
|  | Daycare (through age 4) | 0.21 0.15 |  |  | 0.15 | 14
|  | Daycare Sickroom | 0.15 |  |  |  | 5
|  | Disco/ dance floor | 1.5 0.15 |  |  | 0.15 | 100
|  | Freezer and refrigerated spaces | 0 |  |  |  | 0
|  | Gambling casino | 0.68 0.15 |  |  | 0.15 | 45
|  | Game arcade | 0.68 0.15 |  |  | 0.15 | 45
|  | General Manufacturing- non chemical | 0.15
|  | Gym/ sports arena (play area) | 0.5 0.15 |  | 0.5 | 0.15 | 10
|  | Health club/ aerobics | 0.15 |  |  |  | 10
|  | Health club/ weight room | 0.15 |  |  |  | 10
|  | Janitor closet | 0.15 |  | 1
|  | Kitchen (cooking) | 0.15 |  | 0.7 |  | 3
|  | Kitchenettes | 0.15 |  | 0.3
|  | Large animal holding room |  |  | 2.25
|  | Laundry (soiled storage) | 0.15 |  | 1
|  | Laundry room (central) | 0.15 |  |  |  | 5
|  | Laundry room (dwelling unit) | 0.15 |  |  |  | 5
|  | Lecture Hall (fixed seats) | 0.15 |  |  | 0.15 | -71
|  | Lecture/ postsecondary classroom | 0.38 0.15 |  |  | 0.15 | 25
|  | Legislative chamber | 0.19 0.15 |  |  | 0.15 | 13
|  | Library- reading room/stacks | 0.15 |  |  |  | 10
|  | Lobbies/pre function | 0.5 0.15 |  |  | 0.15 | 33
|  | Locker room (all others) | 0.15 |  | 0.25
|  | Locker room (athletic facility) | 0.15 |  | 0.5
|  | Main Entry Lobby | 0.5 0.15 |  |  | 0.115 | 33
|  | Mall common area | 0.25 0.15 |  |  | 0.15 | 17
|  | Media Center | 0.15 |  |  |  | 25
|  | Multipurpose assembly | 0.5 0.15 |  |  |  | 33
|  | Multiuse assembly | 0.5 |  |  | 0.15
|  | Museum (children's) | 0.25 0.15 |  |  | 0.15 | 17
|  | Museum/gallery | 0.25 0.15 |  |  | 0.15 | 17
|  | Music/theater/dance | 1.07 0.15 |  |  | 0.15 | 33
|  | Occupiable storage for dry materials | 0.15 |  |  |  | 2
|  | Occupiable storage for liquids/gels | 0.15 |  | 1.5 |  | 2
|  | Office space | 0.15 |  |  |  | 5
|  | Parking Garage | 0.15 |  | 0.75
|  | Pet shop (animal area) | 0.25 0.2 |  | 0.9 | 0.15 | 17
|  | Pharmacy (prep area) | 0.15 |  |  |  | 5
|  | Photo studio | 0.15 |  |  |  | 5
|  | Places of religious worship | 1.07 0.15 |  |  | 0.15 | 7
|  | Reception area | 0.15 |  |  |  | 5
|  | Restaurant Dining Rooms | 0.5 0.15 |  |  | 0.15 | 33
|  | Retail sales | 0.25 0.20 |  |  | 0.2 | 17
|  | Science Laboratories | 0.15 |  | 1 |  | 25
|  | Shipping/ receiving | 0.15 |  |  |  | 5
|  | Shower room | 0.15 | 50
|  | Shower room- cont. exh. | 0.15 | 20
|  | Sorting/packing/ light assembly | 0.15 |  |  |  | 5
|  | Small-animal-cage room (static cages) |  |  | 2.25
|  | Small-animal-cage room (ventilated cages) |  |  | 1.5
|  | Spectator area (sports) | 0.5 0.15 |  | 0.5 | 0.15 | 33
|  | Stages, studios | 0.5 0.15 |  |  | 0.15 | 33
|  | Supermarket | 0.25 0.2 |  |  | 0.2 | 17
|  | Swimming deck | 0.5 0.15 |  |  | 0.15 | 33
|  | Swimming pool | 0.15 |  |  |  | 10
|  | Telephone closet | 0.15 |  |  |  | 5
|  | Telephone/ data entry | 0.15 |  |  |  | 33
|  | Toilet (private) | 0.15 | 50
|  | Toilet (private)- cont. exh. | 0.15 | 25
|  | Toilet (public) | 0.15 | 70
|  | Toilet (public)- cont. ehx. | 0.15 | 50
|  | Transportation waiting | 0.5 0.15 |  |  | 0.15 | 33
|  | Trash/ recycling | 0.15 |  | 1
|  | University/College Laboratory | 0.15 |  | 1 |  | 25
|  | Warehouse | 0.15 |  |  |  | 1
|  | Wood/ Metal shop | 0.15 |  | 0.5 |  | 33
Note on B6: 2019 Update: If this box checks, columns 02-18 grey out. Note in Table D row 15 about attached calcs.
Note on B7: 2019: If this box checks, Nonresidential and Hotel/Motel ventilation systems subtable below opens for user input.
Note on L7: Usability Update: If this box checks, High-Rise Residential Dwelling Unit Systems subtable below opens for user input.
Note on B8: Sally Blair: If this box is checked, Note in Table D row 16 about natural ventilation being used to meet ventilation rates.
Note on A9: 2019 Update: New Heading Row
Note on K10: 2019 Update: Because columns have been added for 2019, subsequent column numbers have all changed. Need to recheck calc logic uses the correct columns for all calcs in table.
Note on J11: 2019 Update: Any number entered > 0 should trigger note in Table D row 13.
Note on F16: 2019 Update: This greys out unless column 09 is "Shower room" or "Toilet…"
Note on G16: 11/11/24 If space does not have fixed seating(identified in the UI but not reported) then J12 == the greater of: the number specified by the building designer * 15cfm (added by Ron CEC) or J10 * the Minimum Occupant Load Density for the occupancy type selected in J.09 (MOLD is found in column 1 of Table 120.1A) If space does have fixed seating (identifed in the UI but not reported) then J12 = the value that is determined in accordance with the California Building Code Section 1004.6 (user entered value) If Multifamily is NOT selected in Table A, grays out if user selects No Fixed Seating within the UI. Fixed seating question is not a reported field. If MF is selected, we don't ask user about fixed seating and this is always user input.
Note on H16: 11/11/24 J.13 = the greater of: J.10 * J.09 OR J.12 * 15.0 REMEMBER: J.09 rate is determined by J.16 DCV row. If DCV row = "Provided", then J.09 should use the DCV rate shown below. If J.16 DV row = anything other than "Provided", then J.09 rate should be "cfm/ft2 for column 13 calc" seen below.
Note on I16: 2019 Update: If 09 is anything OTHER THAN - Shower rooms - Toilets col 14 = col 10 x col 09 (cfm/ft2) If 09 is Shower rooms or Toilets: col 14 = col 11 x col 09 (cfm/unit) If no value in col 09 designated for col 14 calc, then col 14 & 15 greys out.
Note on K18: Sally Blair: Adds new (blank) row for user entry same as row 16/17. (under this system). Remove last removes this added row. Reset clears all entries for this system.
Note on L19: 2019 Update: Says "Yes" if column 05+column 06 > column 17 AND col 15 > col 14 if not grey, otherwise "No" Make sure it is EQUAL or greater is yes
Note on K20: Sally Blair: Add System button duplicates Rows 10-19, but blank. Remove Last removes that entire system. Reset clears entire table.
Note on A29: 09/11/20: If the box is checked, J28 grays out
Note on B29: 2019 Update: If this box checks, columns J28 grey out. Note in Table D row 15 about attached calcs.
Note on I30: 3/29/22 If neither bathroom/Kitchen IAQ or Bathroom/Kitchen IAQ & Vent is selected, trigger note in Table D row 24
Note on F33: 2019 Update: = column 22 x ((0.03 x column 20) + (7.5 x (column 21 + 1)))
Note on I33: 2019 Update: If checked, moves NRCV-MCH-32 form from "No" to "Yes" in Table P.
Note on I34: 2019 Update: If checked, moves NRCV-MCH 27 AND NRCV-MCH-32 forms from "No" to "Yes" in Table P.
Note on I35: 2019 Update: If checked, moves NRCV-MCH-32 form from "No" to "Yes" in Table P.
Note on F39: J.29 = "Yes" if ((column 24-column 25)/column 24) <= 0.2 for all rows in subtable, J.29 = Grayed out if continuous ventilation has been selected otherwise says "No"
Note on L39: 2019 Update: Says "Yes" if either of the conditions below are met for all rows in subtable: - column 23 <= column 24 OR - column 23 <= column 25, otherwise says "No"
Note on K40: 2019 Update: Excel rows 35-36 are example of what happens with this button is clicked. Same logic as rows 32-34 apply to this new space.
Note on C47: Balneg, Ronald@Energy: Not understanding why there is a ventilation rate and exhaust rate. This is under the exhaust rate table only, or is this under 'all others'
Note on H56: Balneg, Ronald@Energy: This was a typo, latest table shows 71 for 'auditorium seating area, and places of religious worship'
Note on F61: Balneg, Ronald@Energy: this should not have changed. This is still 0.5
Note on H86: Balneg, Ronald@Energy: should be 5
Note on F87: Balneg, Ronald@Energy: not sure where this comes from
Note on C97: 2019 Update: This selection changes the formula in column 13
Note on H97: Balneg, Ronald@Energy: should be 71, the negative is a typo/or strikeout of a space.
Note on D108: Balneg, Ronald@Energy: should be 0.15
Note on H108: Balneg, Ronald@Energy: should be 33
Note on H119: Balneg, Ronald@Energy: should be 71
Note on H124: Balneg, Ronald@Energy: should be 2 for 'shipping/receiving' and for 'sorting, packing, light assembly'
Note on C126: 2019 Update: These two selections changes the formula in column 14
Note on H127: Balneg, Ronald@Energy: should be 2
Note on C138: 2019 Update: These four selections change the formula in column 14
Note on H145: Balneg, Ronald@Energy: this should be 10

## J. Ventilation (LMCC)
|  | User input |  | auto calculated |  |  |  | From another Table |  |  | From look up table
J. VENTILATION AND INDOOR AIR QUALITY
[d:OnlyUI] Table Instructions: Complete the following Table to demonstrate compliance with mandatory and prescriptive ventilation requirements in §120.1, §120.2(e)3B, 140.4(p) and 140.4(q) for all nonresidential and 160.2, 160.3(a)3D, 170.2(a)4N, 170.2(a)4O for high-rise residential occupancies. For alterations, only ventilation systems being altered within the scope of the permit application need to be documented in this table. In lieu of this table, the required outdoor ventilation rates and airflows may be shown on the plans or the calculations can be presented in a spreadsheet. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory ventilation requirements in §120.1 and §120.2(e)3B for all nonresidential, high-rise residential and hotel/motel occupancies. For alterations, only ventilation systems being altered within the scope of the permit application need to be documented in this table. In lieu of this table, the required outdoor ventilation rates and airflows may be shown on the plans or the calculations can be presented in a spreadsheet. [d:/OnlyRG]
01 | ¨ | Check the box if the project is showing ventilation calculations on the plans, or attaching the calculations instead of completing this table.
02 | ¨ | Check this box if the project includes Nonresidenital, Hotel/Motel spaces or Multifamily Common Use Spaces |  |  |  | Check this box if the project includes new or altered multifamily dwelling units |  |  |  | ¨
03 | ¨ | Check the box if the project is using natural ventilation in any nonresidential spaces to meet required ventilation rates per §120.1(c)2.
Nonresidential Hotel/ Motel and Multifamily Common Use Ventilation Systems
04 |  |  | 05 |  |  | 06 |  |  | 07
System Name: |  |  | System Design OA CFM Air Flow1 |  |  | System Design Transfer Air CFM |  |  | Air Filtration per §120.1(c), §141.0(b)2, 160.2(c)1 and 2
See dropdown
08 | 09 |  | 10 | 11 | 12 | 13 | 14 | 15 | 16
Space Name or Item Tag | Mechanical Ventilation Required per §120.1(c)33 & §160.2(c)3 | [5 empty] | Exh. Vent. per §120.1(c)4 & §160.2(c)4 |  | DCV or Occupant Sensor Controls per §120.1(d)3, §120.1(d)5 & §120.2(e)36, §160.2(c)5d, §160.2(c)5e & §160.2(c)diii
| Occupancy Type4 |  | Conditioned Floor Area (ft2) | # of showerheads/ toilets | # of people5 | Required Min OA CFM | Required Minimum CFM | Provided per Design CFM
| See dropdown | [7 empty] | DCV | See dropdown
[9 empty] | Occ Sensor | See dropdown
[8 empty] | Reset | Add Occupancy Type | Remove Last
17 | Total System Required Min OA CFM |  |  |  |  | sum of col 13 for all spaces in system | 18 | Ventilation for this System Complies? |  | "Yes"/ "No"
1 FOOTNOTES: System CFM should include both mechanical and natural ventilation for the zone/system. | [7 empty] | Reset | Add System | Remove Last
2 Air filtration requirements apply to the following three system types per §120.1(c)1A: space conditioning systems utilizing ducts to supply air to occupiable space; supply-only ventilation systems providing outside air to occupiable space; supply side of balanced ventilation systems including heat recovery and energy recovery ventilation systems providing outside air to occupiable space.
3 Uniform Mechanical Code may have more stringent ventilation requirements; the most stringent code requirement takes precedence.
4 See Standards Tables 120.1-A and 120.1-B.
5 For lecture halls with fixed seating, the expected number of occupants shall be determined in accordance with the California Building Code.
6 §120.2(e)3 requires systems serving rooms that are required by §130.1(c) to have lighting occupancy sensing controls to also have occupancy sensing zone controls for ventilation. Examples of spaces which require lighting occupancy sensors include offices 250ft2 or smaller, multipurpose rooms less than 1,000ft2, classrooms, conference rooms, restrooms, aisles and open areas in warehouses, library book stack aisles, corridors, stairwells, parking garages, and loading and unloading zones, unless excepted by §130.1(c).
7 Air classification and recirculation limitations of air shall be based on the air classification as listed in Table 120.1-A or Table 120.1-C, and in accordance with the requirements of Sections 120.1(g)1 through 4
Multifamily Dwelling Unit Ventilation Systems
¨ | Check the box if the system is using continuous ventilation to meet the ventiliation requirements per §160.2(b)2Aivb2
19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 |  | 27
Space Name or Item Tag | Mechanical Ventilation Required per §120.1(b)2 & §160.2(b)2 |  |  |  | Ventilation per Design |  | Local Exhaust |  | Air Filtration per 120.1(c) & §160.2(b)1
| Conditioned Floor Area (ft2) | # bedrooms | # dwelling units | Required Min OA CFM 1 | Supply Air CFM | Exhaust CFM
[7 empty] | ¨ | Bathroom/Kitchen IAQ | See dropdown
[7 empty] | ¨ | Bathroom/Kitchen IAQ & Vent.
[7 empty] | ¨ | Kitchen Range Hood 2
| 125 | 5 | 10 | 487.5 |  |  | ¨ | Bathroom/Ktichen IAQ | See dropdown
[7 empty] | ¨ | Bathroom/Ktichen IAQ & Vent.
[7 empty] | ¨ | Kitchen Range Hood 2
28 | Is this a balanced system? 4 |  |  | Yes/No | 29 | Meeting Outside Air Requirements? |  |  |  | Yes/ No
1 FOOTNOTES: Uniform Mechanical Code may have more stringent ventilation requirements; the most stringent code requirement takes precedence. | [7 empty] | Reset | Add Space | Remove Last
2 Kitchen range hood will be verified per NA7.18.1 to confirm model is rated by HVI or AHAM.
3 Air filtration requirements apply to the following three system types per §120.1(b)1A: space conditioning systems utilizing ducts to supply air to occupiable space; supply-only ventilation systems providing outside air to occupiable space; supply side of balanced ventilation systems including heat recovery and energy recovery ventilation systems providing outside air to occupiable space.
4 A balanced ventiltion system provides ventilation airflow to each dwelling-unit at a rate equal to or greater than the required minimum rate, but not more than twenty percent greater.
|  | Column 09- Occupancy Type Dropdown | Minimum Ventilation Rate (cfm/ft2) | Minimum Exhaust Rate (cfm/unit) | Minimum Exhaust Rate (cfm/ft2) | cfm/ft2 for column 13 calc DCV | Minimum Occupant Load Density (persons/1,000ft2) |  | Column 07- Air filtration dropdown
|  | All others | 0.15 |  |  |  | 5 |  | Provided
|  | Animal imaging (MRI/CT/PET) | 0.15 |  | 0.9 |  | 5 |  | NA: Not system type specified in Table J footnote 2
|  | Animal operating rooms | 0.15 |  | 3 |  | 5 |  | Evaporative Cooler
|  | Animal postoperative recovery room | 0.15 |  | 1.5 |  | 5
|  | Animal preparation room | 0.15 |  | 1.5 |  | 5 |  |  | Coulmn 16- DCV Dropdown
|  | Animal procedure room | 0.15 |  | 2.25 |  | 5 |  |  | Provided per §120.1(d)4
|  | Animal surgery scub | 0.15 |  | 1.5 |  | 5 |  |  | NA: Not required per §120.1(d)3
|  | Animal necropsy | 0.15 |  | 2.25 |  | 5 |  |  | NA: Space exhaust is > design ventilation rate exception
|  | Art Classroom | 0.15 |  | 0.7 |  | 25 |  |  | NA: Processes that generate dust, fumes, etc.& no local exhaust
|  | Assembly- multiuse | 0.5 | [6 empty] | NA: Area <150 ft2 or design occupancy < 10 people
|  | Auditorium seating area | 1.07 0.15 |  |  | 0.15 | 7
|  | Auto-repair room | 0.15 |  | 1.5
|  | Bank or bank lobby | 0.15 |  |  |  | 5
|  | Bank Vault/safe deposit | 0.15 |  |  |  | 5 |  |  | Column 16- Occ Sens Dropdown
|  | Bar/ cocktail lounge | 0.5 0.2 |  |  | 0.2 | 33 |  |  | Provided per §120.1(d)5
|  | Barbershop | 0.4 |  | 0.5 0.60 |  | 17 |  |  | NA: Continously operated per §120.2(e)3 exception
|  | Barracks sleeping area | 0.15 |  |  |  | 5 |  |  | NA: System < 2kW demand + manual shutoff per §120.2(e)3 exception
|  | Beauty/ nail salon | 0.4 |  | 0.6 |  | 17 |  |  | NA: Hotel/ motel + manual shutoff per §120.2(e)3 exception
|  | Bedroom/Living room (hotel/motel/dorm) | 0.15 |  |  |  | 3 |  |  | NA: Not required space type
|  | Bowling alley (seating) | 1.07 0.15 |  |  | 0.15 | 7
|  | Break room | 0.5 0.15 |  |  | 0.15 | 33
|  | Cafeteria/ fast-food dining | 0.5 0.15 |  |  | 0.15 | 33
|  | Cells with toilet | 0.15 |  | 1
|  | Classroom (age 5-18) | 0.38 0.15 |  |  | 0.15 | 25 |  |  | Column 27- Air filtration dropdown
|  | Classroom (age 9-18) | 0.15 |  |  |  | 25 |  |  | Provided
|  | Coffee station | 0.5 0.15 |  |  | 0.15 | 33 |  |  | NA: Evaporative Cooler
|  | Coin-operated Laundry | 0.3 |  |  |  | 17
|  | Computer (not printing) | 0.15 |  |  |  | 5
|  | Computer Lab | 0.15 |  |  |  | 25
|  | Conference/ meeting | 0.5 0.15 |  |  | 0.15 | 33
|  | Copy/ printing room | 0.15 |  | 0.5
|  | Corridor | 0.15 |  |  |  | 5
|  | Courtroom | 0.19 0.15 |  |  | 0.15 | 13
|  | Darkroom | 0.15 |  | 1
|  | Daycare (through age 4) | 0.21 0.15 |  |  | 0.15 | 14
|  | Daycare Sickroom | 0.15 |  |  |  | 5
|  | Disco/ dance floor | 1.5 0.15 |  |  | 0.15 | 100
|  | Freezer and refrigerated spaces | 0 |  |  |  | 0
|  | Gambling casino | 0.68 0.15 |  |  | 0.15 | 45
|  | Game arcade | 0.68 0.15 |  |  | 0.15 | 45
|  | General Manufacturing- non chemical | 0.15
|  | Gym/ sports arena (play area) | 0.5 0.15 |  | 0.5 | 0.15 | 10
|  | Health club/ aerobics | 0.15 |  |  |  | 10
|  | Health club/ weight room | 0.15 |  |  |  | 10
|  | Janitor closet | 0.15 |  | 1
|  | Kitchen (cooking) | 0.15 |  | 0.7 |  | 3
|  | Kitchenettes | 0.15 |  | 0.3
|  | Large animal holding room |  |  | 2.25
|  | Laundry (soiled storage) | 0.15 |  | 1
|  | Laundry room (central) | 0.15 |  |  |  | 5
|  | Laundry room (dwelling unit) | 0.15 |  |  |  | 5
|  | Lecture Hall (fixed seats) | 0.15 |  |  | 0.15 | -71
|  | Lecture/ postsecondary classroom | 0.38 0.15 |  |  | 0.15 | 25
|  | Legislative chamber | 0.19 0.15 |  |  | 0.15 | 13
|  | Library- reading room/stacks | 0.15 |  |  |  | 10
|  | Lobbies/pre function | 0.5 0.15 |  |  | 0.15 | 33
|  | Locker room (all others) | 0.15 |  | 0.25
|  | Locker room (athletic facility) | 0.15 |  | 0.5
|  | Main Entry Lobby | 0.5 0.15 |  |  | 0.115 | 33
|  | Mall common area | 0.25 0.15 |  |  | 0.15 | 17
|  | Media Center | 0.15 |  |  |  | 25
|  | Multipurpose assembly | 0.5 0.15 |  |  |  | 33
|  | Multiuse assembly | 0.5 |  |  | 0.15
|  | Museum (children's) | 0.25 0.15 |  |  | 0.15 | 17
|  | Museum/gallery | 0.25 0.15 |  |  | 0.15 | 17
|  | Music/theater/dance | 1.07 0.15 |  |  | 0.15 | 33
|  | Occupiable storage for dry materials | 0.15 |  |  |  | 2
|  | Occupiable storage for liquids/gels | 0.15 |  | 1.5 |  | 2
|  | Office space | 0.15 |  |  |  | 5
|  | Parking Garage | 0.15 |  | 0.75
|  | Pet shop (animal area) | 0.25 0.2 |  | 0.9 | 0.15 | 17
|  | Pharmacy (prep area) | 0.15 |  |  |  | 5
|  | Photo studio | 0.15 |  |  |  | 5
|  | Places of religious worship | 1.07 0.15 |  |  | 0.15 | 7
|  | Reception area | 0.15 |  |  |  | 5
|  | Restaurant Dining Rooms | 0.5 0.15 |  |  | 0.15 | 33
|  | Retail sales | 0.25 0.20 |  |  | 0.2 | 17
|  | Science Laboratories | 0.15 |  | 1 |  | 25
|  | Shipping/ receiving | 0.15 |  |  |  | 5
|  | Shower room | 0.15 | 50
|  | Shower room- cont. exh. | 0.15 | 20
|  | Sorting/packing/ light assembly | 0.15 |  |  |  | 5
|  | Small-animal-cage room (static cages) |  |  | 2.25
|  | Small-animal-cage room (ventilated cages) |  |  | 1.5
|  | Spectator area (sports) | 0.5 0.15 |  | 0.5 | 0.15 | 33
|  | Stages, studios | 0.5 0.15 |  |  | 0.15 | 33
|  | Supermarket | 0.25 0.2 |  |  | 0.2 | 17
|  | Swimming deck | 0.5 0.15 |  |  | 0.15 | 33
|  | Swimming pool | 0.15 |  |  |  | 10
|  | Telephone closet | 0.15 |  |  |  | 5
|  | Telephone/ data entry | 0.15 |  |  |  | 33
|  | Toilet (private) | 0.15 | 50
|  | Toilet (private)- cont. exh. | 0.15 | 25
|  | Toilet (public) | 0.15 | 70
|  | Toilet (public)- cont. ehx. | 0.15 | 50
|  | Transportation waiting | 0.5 0.15 |  |  | 0.15 | 33
|  | Trash/ recycling | 0.15 |  | 1
|  | University/College Laboratory | 0.15 |  | 1 |  | 25
|  | Warehouse | 0.15 |  |  |  | 1
|  | Wood/ Metal shop | 0.15 |  | 0.5 |  | 33
Note on B6: 2019 Update: If this box checks, columns 02-18 grey out. Note in Table D row 15 about attached calcs.
Note on B7: 2019: If this box checks, Nonresidential and Hotel/Motel ventilation systems subtable below opens for user input.
Note on K7: Usability Update: If this box checks, High-Rise Residential Dwelling Unit Systems subtable below opens for user input.
Note on B8: Sally Blair: If this box is checked, Note in Table D row 16 about natural ventilation being used to meet ventilation rates.
Note on A9: 2019 Update: New Heading Row
Note on J10: 2019 Update: Because columns have been added for 2019, subsequent column numbers have all changed. Need to recheck calc logic uses the correct columns for all calcs in table.
Note on I11: 2019 Update: Any number entered > 0 should trigger note in Table D row 13.
Note on E16: 2019 Update: This greys out unless column 09 is "Shower room" or "Toilet…"
Note on F16: 11/11/24 If space does not have fixed seating(identified in the UI but not reported) then J12 == the greater of the number specified by the building designer or J10 * the Minimum Occupant Load Density for the occupancy type selected in J.09 (MOLD is found in column 1 of Table 120.1A) If space does have fixed seating (identifed in the UI but not reported) then J12 = the value that is determined in accordance with the California Building Code Section 1004.6 (user entered value) If Multifamily is NOT selected in Table A, grays out if user selects No Fixed Seating within the UI. Fixed seating question is not a reported field. If MF is selected, we don't ask user about fixed seating and this is always user input.
Note on G16: 11/11/24 J.13 = the greater of: J.10 * J.09 OR J.12 * 15.0 REMEMBER: J.09 rate is determined by J.16 DCV row. If DCV row = "Provided", then J.09 should use the DCV rate shown below. If J.16 DV row = anything other than "Provided", then J.09 rate should be "cfm/ft2 for column 13 calc" seen below.
Note on H16: 2019 Update: If 09 is anything OTHER THAN - Shower rooms - Toilets col 14 = col 10 x col 09 (cfm/ft2) If 09 is Shower rooms or Toilets: col 14 = col 11 x col 09 (cfm/unit) If no value in col 09 designated for col 14 calc, then col 14 & 15 greys out.
Note on J18: Sally Blair: Adds new (blank) row for user entry same as row 16/17. (under this system). Remove last removes this added row. Reset clears all entries for this system.
Note on K19: 2019 Update: Says "Yes" if column 05+column 06 > column 17 AND col 15 > col 14 if not grey, otherwise "No" Make sure it is EQUAL or greater is yes
Note on J20: Sally Blair: Add System button duplicates Rows 10-19, but blank. Remove Last removes that entire system. Reset clears entire table.
Note on A29: 09/11/20: If the box is checked, J28 grays out
Note on B29: 2019 Update: If this box checks, columns J28 grey out. Note in Table D row 15 about attached calcs.
Note on H30: 3/29/22 If neither bathroom/Kitchen IAQ or Bathroom/Kitchen IAQ & Vent is selected, trigger note in Table D row 24
Note on E33: 2019 Update: = column 22 x ((0.03 x column 20) + (7.5 x (column 21 + 1)))
Note on H33: 2019 Update: If checked, moves NRCV-MCH-32 form from "No" to "Yes" in Table P.
Note on H34: 2019 Update: If checked, moves NRCV-MCH 27 AND NRCV-MCH-32 forms from "No" to "Yes" in Table P.
Note on H35: 2019 Update: If checked, moves NRCV-MCH-32 form from "No" to "Yes" in Table P.
Note on E39: J.29 = "Yes" if ((column 24-column 25)/column 24) <= 0.2 for all rows in subtable, J.29 = Grayed out if continuous ventilation has been selected otherwise says "No"
Note on K39: 2019 Update: Says "Yes" if either of the conditions below are met for all rows in subtable: - column 23 <= column 24 OR - column 23 <= column 25, otherwise says "No"
Note on J40: 2019 Update: Excel rows 35-36 are example of what happens with this button is clicked. Same logic as rows 32-34 apply to this new space.
Note on C45: Balneg, Ronald@Energy: please review, probably same issues pointed in previous tab for NRCC for vent rates and person density
Note on C97: 2019 Update: This selection changes the formula in column 13
Note on C126: 2019 Update: These two selections changes the formula in column 14
Note on C138: 2019 Update: These four selections change the formula in column 14

## K. VAV Controls
| User input |  | auto calculated | [7 empty] | From another Table | From look up table | 2019 Changes
K. TERMINAL BOX CONTROLS
[d:OnlyUI] Table Instructions: Complete the following Table to demonstrate compliance with prescriptive zone control requirements in §140.4(d) & §170.2(c)4B. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with prescriptive zone control requirements in §140.4(d) & §170.2(c)4B. [d:/OnlyRG]
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12
Zone/System/VAV Box Name or Item Tag | Zonal Control Strategy per §140.4(d) | Design |  |  | Deadband Compliance |  |  |  | Reheated, Recooled, Mixed Air Compliance |  | Complies
|  | Peak Primary Airflow CFM | Primary Air in Deadband CFM | Reheated Recooled Mixed Airflow CFM | Outside Air CFM | 30% of Peak Primary Airflow CFM | Max Deadband Airflow CFM | 50% of Peak Primary Airflow | 1st Stage Modulates <95oF and Maintains DB Rate? | 2nd Stage Modulates from DB Flow to Heating Max Flow?
| See dropdown | [7 empty] | See dropdown | See dropdown | "Yes"/ "No"
[9 empty] | Reset | Add Row | Remove Last
Zonal Ctrl Strategy dropdown
| No Reheat, Recool, Mixing | [7 empty] | 1st Stage Dropdown | 2nd Stage Dropdown
| VAV w DDC @ zone | [7 empty] | Yes | Yes
VAV w/o DDC @ zone
NA: Pressurization control
NA: Reheat via site/solar source
NA: Humidity control
NA: Peak SA < 300 CFM
NA: Healthcare Facility
Note on G9: 11.11.21 = (0.3 x 03) if 02 is VAV w/o DDC Else blank/gray
Note on H9: 11/11/21 If K.02 = "VAV w DDC @ Zone", K.08 = K.06 If K.02 = "VAV w/o DDC @ Zone", K.08 = max of K.06 and K.07
Note on I9: Mart-Laptop: 0.5 X Col-03
Note on L9: 11.11.21 Ben, says "Yes" if column 02 selection is ANY of the following - No Reheat, Recool, Mixing - NA: Pressurization Control - NA: Reheat via site/solar source - NA: Humidity Control - NA: Peak SA < 300 CFM - NA: Healthcare Facility OR says "Yes" if column 02 says "VAV w/o DDC@zone" AND 05<08 OR says "Yes" if column 02 says "VAV w DDC@zone" AND 05<MAX(09 AND 06) AND 04<08 AND both columns 10 & 11 say "Yes".
Note on B11: Sally Blair: Selection of VAV w DDC opens 03-11. Selection of VAV w/o DDC opens 03, 05,06,07,08.
Note on B19: 2019 Update: Added exception fro HCF

## L. Distribution
| User input |  |  | auto calculated |  |  | From another Table |  | From look up table
L. DISTRIBUTION (DUCTWORK and PIPING)
[d:OnlyUI] Table Instructions: Complete the following tables to show compliance with mandatory pipe insulation requirements found in §120.3 and mandatory requirements found in §120.4 and 160.3(b) for duct sealing. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory pipe insulation requirements found in §120.3 and mandatory requirements found in §120.4(g) for duct sealing. [d:/OnlyRG]
Mandatory Pipe Insulation
01 | ¨ | Insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Insulation exposed to weather shall be installed with a cover suitable for outdoor service. Insulation covering chilled water piping and refrigerant suction piping located outside the conditioned space shall have a Class I or Class II vapor retarder. All penetrations and joints of which shall be sealed.
02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 10a
System Type | Nominal Pipe Diameter (in) | Fluid Temperature Range (oF) | Conductivity Range (Btu-in per hr per ft2 per oF) | Insulation Mean Rating Temp. (oF) | Min. Insulation Thickness Required per Table 120.3-A (in) | Min. Insulation Thickness Required per §120.3(c)2 & §160.3(c)1dii (in) | Insulation Thickness per Design (in) | Exception to §120.3 & §160.3(c) (if applicable) | Serving Res or NR Space?
Dropdown | Dropdown | Dropdown | Dropdown | Value from Table 120.3-A based on column 04 | Value from Table 120.3-A based on columns 03/04 |  |  | Dropdown | Dropdown
Duct Leakage Testing
The answers to the questions below apply to the following duct system(s): |  |  |  | Duct System #1 | NR/Common Use: Duct leakage testing shall not exceed X% per NA7.5.3 required for these systems? |  |  |  | 18
Dwelling Units: Total duct leakage of duct system shall not exceed 12% or duct leakage system to outside shall not exceed 6% per RA3.1.4 required for these systems?
Duct leakage testing per CMC Section 603.9.2 required for these systems?
11 | Dropdown | The scope of the project includes only duct systems serving healthcare facilites.
12 | Dropdown | Duct system provides conditioned air to an occupiable space for a constant volume, single zone, space-conditioning system.
13 | Dropdown | The space conditioning system serves less than 5,000 ft2 of conditioned floor area.
14 | Dropdown | The combined surface area of ducts located outdoors or in unconditioned spaces is more than 25% of the total surface area of the entire duct system:
|  | ¨ | Outdoors
|  | ¨ | In a space directly under a roof that has a U-factor greater than the U-factor of the ceiling, or if the roof does not meet the requirements of §140.3(a)1B or if the roof has fixed vents or openings to the outside/ unconditioned spaces
|  | ¨ | In an unconditioned crawlspace
|  | ¨ | In other unconditioned spaces
15 | Dropdown | The scope of the project includes extending an existing duct system, which is constructed, insulated or sealed with asbestos.
16 | Dropdown | The scope of the project includes an existing duct system that is documented to have been previously sealed as confirmed through field verification and diagnostic testing in accordance with procedures in the Reference Nonresidential Appendix NA2.
18 | Dropdown | All ductwork is an extension of an existing duct system
19 | Dropdown | Ductwork serving dwelling unit
20 | Dropdown | <25 ft of new or replacement space conditioning duct installed
21 | Dropdown | Duct Insulation R Value
22 | Dropdown | Ductwork existing to remain
23 | Dropdown | Duct system connected to altered space conditioning system
System Type Dropdown | Pipe Dia Dropdown | Fluid Temp Range Dropdown if Space Heating in 02 | Conductivity Range Dropdown |  | Duct Insulation R Value Dropdown |  |  | Applicable Exception Dropdown | Space Dropdown
Space heating | < 1 | Above 350 | 0.32 - 0.34 |  | R0 |  |  | No exception taken | Residential
Space cooling | 1 to <1.5 | 251-350 | Other |  | R2.1 |  |  | Factory installed piping within certified equip. | Nonresidential
| 1.5 to <4 | 201-250 | Conductivity Range Dropdown |  | R4.2 |  |  | Fluid design operating temp. 60-105oF
| 4 to <8 | 141-200 | 0.29 - 0.32 |  | R6 |  |  | Lack of insulation will not increase energy use
| 8+ | 105-140 | Other |  | R8
|  |  | Conductivity Range Dropdown |  | R10
|  | Fluid Temp Range Dropdown if Space Cooling in 02 | 0.27 - 0.30 |  | R12
|  | 40-60 | Other |  | Rvalue Verified Duct System
|  | Below 40 | Conductivity Range Dropdown
| Duct Leakage Sealing Dropdowns (11/12/13/14/15/16/18/20) |  | 0.25 - 0.29
| Yes |  | Other
| No |  | Conductivity Range Dropdown
0.22 - 0.28
Other
| Duct Leakage Sealing Dropdowns (17) |  | Conductivity Range Dropdown
| Yes |  | 0.21 - 0.27
| Exposed Ductwork located in occupied space |  | Other
Conductivity Range Dropdown
0.20 - 0.26
Other
Note on E9: Sally Blair: 06 & 07 blank and grey out if "Other" selected in 05.
Note on G9: Sally Blair: Starts as grey unless user selects "Other" in column 05
Note on F12: 5.10.23 If 18 == Yes & 20 == No OR 23 = Yes X = 15 Else X = 6
Note on J12: 5/18/23 Yes if 12-14 are Yes and 11, 15, 16, 19, 20 & 22 are No. Otherwise, "No"
Note on J13: 5.24.23 If L.19 == Yes AND L.18, 20, 22, & 23 == No AND Climate Zone != 1, 3, 5, or 7 - Only applies to HRR = "Yes" and duct system = "12%" and outside = "6%" If L.19 == Yes AND L15 & L22== No AND ((L.18 == Yes AND L20 == No) OR (L.23 == Yes & L15 & L16==No ) = "Yes and duct system = 15% and outside = 10% Otherwise = "No"
Note on J14: 5/18/23 = Yes if NR/Common Area == No AND Dwelliung Units = "No" AND 22 = No
Note on A15: Ben Lalor: Numbers of rows have been updated by shifting down one number
Note on B15: 6.16.22 If row 11 = "Yes" rows 12-20 grey out
Note on C19: Sally Blair: User can select more than one.
Note on B27: 6.16.22 This is blank/gray unless 18 = "Yes"
Note on B28: 6.16.22 This is blank/gray unless 18 = "Yes"
Note on D32: Ben Lalor: Custom Dropdown when column 04 = Above 350
Note on F32: 7.5.22 This is needed for downstream CF2R and does not trigger other fields or affect compliance logic
Note on D34: Sally Blair: If the user selects "Other", columns 06 & 07 blank and grey out & column 08 opens for user input.
Note on D35: Ben Lalor: Custom Dropdown when column 04 = 251-350
Note on D38: Ben Lalor: Custom Dropdown when column 04 = 201-250
Note on D41: Ben Lalor: Custom Dropdown when column 04 = 141 - 200
Note on D44: Ben Lalor: Custom Dropdown when column 04 = 105 - 140
Note on D47: Sally Blair: Custom Dropdown when column 04 = 40-60
Note on D50: Sally Blair: Custom Dropdown when column 04 = Below 40

## M.Cooling Tower
| user entered |  |  |  | auto calculated |  |  |  |  | From another Table |  |  |  | From look up table
M. COOLING TOWERS
[d:OnlyUI] Table Instructions: Complete the following Table for open and closed circuit cooling towers with a rated capacity > 150 tons to demonstrate compliance with mandatory requirements in §110.2(e)2. This Table calculates the Maximum Achievable Cycles of Concentration using the Langelier Saturation Index (LSI) calculations per §110.2(e)2. [d:/OnlyUI] [d:OnlyRG] This table is used to demonstrate compliance with mandatory requirements in §110.2(e)2 for cooling towers with a rated capacity > 150 tons. This Table calculates the Maximum Cycles of Concentration using the Langelier Saturation Index (LSI) calculations per §110.2(e)2. [d:/OnlyRG]
01 | ¨ | Check the box if the project is showing calculations on the plans, or attaching the calculations instead of completing this Table.
02 | 03 | 04 | 06 | 05 | 06 | 07 | 08 | 09 | 0910 | 1011 | 1112 | 13 | 14 | 15
Name or Item Tag | Design Conditions |  | Economizer Conditions | Rated Conditions | Maximum Skin Temp (◦F) | Conductivity | M-Alkalinity Excluding Galvanized Steel | M-Alkalinity Including Galvanized Steel | Calcium Hardness | Magnesium Hardness | Total Dissolved Solids Target Tower Cycles | Chlorides | Sulfates | Silica
| Design GPM | Min Flow GPM | GPM | GPM/HP
[7 empty] | 1216 | 1317 | 1419 | 1518
[7 empty] | Target Tower Cycles Calculated pH @ Target Cycles | Maximum Achievable Cycles of Concentration pH Saturation @ Target Cycles | Tower LSI Based on Calculated pH | Complies
equals M.12-M.13
1 Open-circuit cooling tower is defined as an open, or direct contact, cooling tower which exposes water directly to the cooling atmosphere, thereby transferring the source heat load from the water directly to the air by a combination of heat and mass transfer.
2 Closed-circuit cooling tower is defined as a cooling tower that utilizes indirect contact between a heated fluid, typically water or glycol, and the cooling atmosphere to transfer the source heat load through sensible heat, latent heat, and mass transfer indirectly to the air, essentially combining a heat exchanger and cooling tower into an integrated and relatively compact device.
3 Blowdown must not occur until one or more of the parameters in Table 110.2-A-1 reaches the maximum value. According to CEC calculations in 110.2(e)2, this will occur after the maximum achievable cycles of concentration calculated in field M17
Climate Zone Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on B5: 12/12/24: If checked, grey out columns 02-158 & Trigger the note in row 14 on Table D.
Note on G13: Sally Blair: Name/item tag copied down from column 02
Note on I13: 12/12/24 = the smaller of the following: 2970 /M07 1845 / M13 540/M08 450/M09 540/M10 270/M14 225/M15 135/M16 LSI (screenshot below)
Note on K13: 12/12/24 = "Complies", if M16<=M17 Else = "Does Not Comply "Yes" if column 14 is < 2.5. "No" if column 14 is > 2.5.

## N. NRCI (NRCC)
| User input |  |  | auto calculated | From another Table | From look up table
N. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ [d:/OnlyRG]
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | NRCI-MCH-01-E - Must be submitted for all buildings. | o | o
● | m | 2022 NRCI-MCH-20-F Duct Leakage Diagnostic Test | o | o
● | m | 2022 NRCI-MCH-22-F Fan Efficacy | o | o
● | m | 2022-NRCI-MCH-23-F Airflow Rate | o | o
● | m | 2022-NRCI-MCH-25-F Refrigerant Charge Verification | o | o
Note on A4: 2019 Update: Updated hyperlink
Note on A7: Sally Blair: Ben, this defaults to "Yes" and can’t be moved to "No"
Note on A8: 5/3/22 Triggers "Yes" if Table L Duct Leakage Testing, Dwelling Units = "Yes". Otherwise = "No"
Note on A9: 5/3/22 If Table H Serving Dwelling Units = "Serving Individual Dwelling Units". Otherwise = "No"
Note on A10: 5/3/22 If Table H Serving Dwelling Units = "Serving Individual Dwelling Units". Otherwise = "No"
Note on A11: 5/3/22 If Table H serving Dwelling Units = "Serving Individual Dwelling Units" AND A.02 = 2 or 8-15, = "Yes". Otherwise = "No"

## N. LMCI (LMCC)
| User input |  |  | auto calculated | From another Table | From look up table
N. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ [d:/OnlyRG]
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | LMCI-MCH-01-E - Must be submitted for all buildings. | o | o
● | m | LMCI-MCH-20-H Duct Leakage Diagnostic Test | o | o
● | m | LMCI-MCH-21-H Duct Location Verification | o | o
● | m | LMCI-MCH-22-H Fan Efficacy | o | o
● | m | LMCI-MCH-23-H Airflow Rate | o | o
● | m | LMCI-MCH-24-H Building Envelope Air Leakage Worksheet | o | o
● | m | LMCI-MCH-25 Refrigerant Charge Verification | o | o
● | m | LMCI-MCH-26-H Rated Space Conditioning System Equipment Verification | o | o
● | m | LMCI-MCH-27b-H Indoor Air Quality and Mechanical Ventilation | o | o
● | m | LMCI-MCH-28-H Return Duct Design and Air Filter Grille Device Sizing | o | o
● | m | LMCI-MCH-29-H Duct Surface Area Reduction; Buried Ducts Compliance Credit | o | o
● | m | LMCI-MCH-32-H Local Mechanical Exhaust | o | o
● | m | LMCI-MCH-33-H Variable Capacity Heat Pump Compliance Credit | o | o
Note on A4: 2019 Update: Updated hyperlink
Note on A7: Sally Blair: Ben, this defaults to "Yes" and can’t be moved to "No"
Note on A8: 5/3/22 Triggers "Yes" if Table L Duct Leakage Testing, Dwelling Units = "Yes". Otherwise = "No"
Note on A9: 6.6.22 Default = No
Note on A10: 5/3/22 If Table H Serving Dwelling Units = "Serving Individual Dwelling Units". Otherwise = "No"
Note on A11: 5/3/22 If Table H Serving Dwelling Units = "Serving Individual Dwelling Units". Otherwise = "No"
Note on A12: 6.6.22 Triggers yes if J.28 = gray/blank. Otherwise = No
Note on A13: 6.6.22 If "Individual Dwelling Unit" is selected in Table F System Information and Table 170.2-K requires Refrigerant charge verification based on climate zone in Table A, this = Yes Otherwise = No
Note on A14: 6.6.22 = Yes if "Unitary Heat Pump", "Unitary Heat Pump (no elec resistance)" or "Dual Fuel Heat Pump" has been selected in Table F Otherwise = No
Note on A15: 6.6.22 Triggers based for new construction and additions greater than 1,000 sf, may need to add this question to the UI (not reported) because we don't ask for this information currently
Note on A16: 6.6.22 Default = No
Note on A17: 6.6.22 Default = No
Note on A18: 6.20.22 = Yes if Kitchen Range hood is selected in J26. Otherwise = No
Note on A19: 6.20.22 = default = "no"

## O. NRCA
| User input |  |  |  | auto calculated |  |  | From another Table | From look up table
O. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCA/. [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and any with "-A" in the form name must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html
YES | NO | Form/Title | Systems To Be Field Verified | Field Inspector |  | Trigger
|  |  |  | Pass | Fail |  | Logic
m | m | NRCA-MCH-02-A Outdoor Air must be submitted for all newly installed HVAC units. |  | o | o | Newly installed HVAC unit. (CFM is listed somwhere in this form…) | PROJECT SCOPE 01 = New Construction OR Altered Mechanical System 04 = Ventilation
m | m | NRCA-MCH-03-A Constant Volume Single Zone HVAC |  | o | o | Newly installed Unitary Unit | PROJECT SCOPE 01 = New Construction OR Altered Mechanical System 04 = Unitary (Packaged/Split)
m | m | NRCA-MCH-04 Air Distribution Duct Leakage |  | o | o | New Duct System Altered Space Conditioning System - Air Handler changeout - Condensing unit of Split System - Cooling coil changeout Altered Duct System <75% new Low Leakage Air-Handling Unit | PROJECT SCOPE 01 = New Construction OR Altered Mechanical System AND 04 = Fan Systems AND/ OR Unitary (Packaged/Split) AND/OR Zonal Systems/ Terminal Boxes AND/OR Ductwork
m | m | NRCA-MCH-05-A Air Economizer, DOAS, HRV, & ERV Controls |  | o | o | New or Altered Air Economizer | FAN SYSTEMS If Economizer Dropdown Selection ≠ NA
m | m | NRCA-MCH-06-A Demand Control Ventilation Systems Acceptance must be submitted for all systems required to employ demand controlled ventilation (refer to §120.1(c)3) can vary outside ventilation flow rates based on maintaining interior carbon dioxide (CO2) concentration setpoints. |  | o | o | Have an air side economizer AND Occupant density ≥ 25 people/ 1000sf AND Single zone systems with any controls OR Multizone system with DDC to the zone level. | I. FAN SYSTEMS If Economizer Dropdown Selection "Fixed Temp. - Diff Enthalpy" AND Occupant Density ≥ 25 people/ 1000sf J. SYSTEM CONTROLS 02 = Single Zone OR multi-zone w/DDC to zone
m | m | NRCA-MCH-07-A Supply Fan Variable Flow Controls |  | o | o | VAV Supply Fan | I. FAN SYSTEMS Fan Function Dropdown = Supply Fan Type Dropdown = Variable Air Volume
m | m | NRCA-MCH-08-A Valve Leakage Test |  | o | o | New Construction | H. PUMPS 05 Variable Flow Dropdown = Yes
m | m | NRCA-MCH-09-A Supply Water Temperature Reset Controls |  | o | o | New or Replaced Chiller or Boiler | G. HVAC SYSTEMS Boiler Efficiency and Controls 09 Tempterature Reset Dropdown = Yes AND/OR Chiller Efficiency and Controls 10 Temperature Reset Dropdown = Yes
m | m | NRCA-MCH-10-A Hydronic System Variable Flow Controls |  | o | o |  | H. PUMPS 05 Variable Flow Dropdown = Yes
m | m | NRCA-MCH-11-A Automatic Demand Shed Controls |  | o | o |  | DDC to zone level
m | m | NRCA-MCH-12-A FDD for Packaged Direct Expansion Units |  | o | o |  | PROJECT SCOPE New Mechanical Systems OR Altered Mechanical System HVAC SYSTEMS 02 = Unitary AC/ Condensers OR Packaged AC/ Heat
m | m | NRCA-MCH-13-A Automatic FDD for Air Handling Units and Zone Terminal Units Acceptance |  | o | o
m | m | NRCA-MCH-14-A Distributed Energy Storage DX AC Systems Acceptance |  | o | o
m | m | NRCA-MCH-15-A Thermal Energy Storage (TES) System Acceptance |  | o | o
m | m | NRCA-MCH-16-A Supply Air Temperature Reset Controls |  | o | o |  | J. SYSTEM CONTROLS 08 = Included
m | m | NRCA-MCH-17-A Condenser Water Temperature Reset Controls |  | o | o
m | m | NRCA-MCH-18 Energy Management Control Systems |  | o | o
m | m | NRCA-MCH-19 Occupancy Sensor Controls |  | o | o
m | m | NRCA-MCH-20 Multi-Family Ventilation |  | o | o
m | m | NRCA-MCH-21 Multi-Family Envelope Leakage |  | o | o
m | m | NRCA-MCH-22-A MF Duct Leakage |  | o | o
m | m | NRCA-MCH-23-A MF HRV/ERV Verification |  | o | o
m | m | NRCA-MCH-24A-Cooling Tower Conductivity Controls |  | o | o
Note on A4: 2019 Update: Removed "AND VERIFICATION" because NRCVs were moved to Table P. Modified instructions too.
Note on B6: Sally Blair: Form will select based on user input in other Tables. User can edit, but if they do a note will show up in Table D. See Table D row 12 for note.
Note on D6: 9/11/20: This is a user entry column where users would list the systems that require each form.
Note on A8: 1/12/23: Defaults to "No". Moves to "Yes" if Table B. Project Scope 03 = Ventilation Note: MCH-02-A can be performed in conjunction with MCH-07-A Supply Fan VFD Acceptance (if applicable) since testing activities overlap.
Note on A9: 7/23/24 Defaults to "No". If I.02 == Single Zone AND I04 == Setback or Setback + DR AND Project is not healthcare NRCA-MCH-03 moves to Yes.
Note on A10: 2/24/23: Defaults to "No". Moves to "Yes" if Table L: If ANY systems shows "Yes" for NR/Common Use Duct leakage testing
Note on C10: 10/17/22 It's hard to see, but the "-A" is struck-through. We want to remove it for 2022
Note on A11: 11/12/24 If FAN SYSTEMS Economizer Dropdown Selection = "Fixed Temp., Fixed Enthalpy, Diff Temp., OR Diff Enthalpy" Or Table H.10 Dwelling Unit == HRV Provided or ERV Provided Or H.08 EAHR == Provided Or F.02 Dry System Sizing == DOAS result = Yes Else result = No
Note on A12: 1/12/23: Defaults to "No". Moves to "Yes" if Table J col 16 (top row) says "Provided per §120.1(d)4" for DCV dropdown.
Note on G12: Katie Gustafson: What does "single zone systems with any conrols" mean? Basically anything? Does this impact the DR dropdown.
Note on A13: 1/12/23: Defaults to "No". Moves to "Yes" if FAN SYSTEMS Fan Type = Supply System Zoning = multizone VAV systems
Note on A14: 1/12/23: Defaults to "No". Moves to "Yes" if PUMPS 05 Variable Flow Dropdown = Yes
Note on A15: 1/12/23: F. HVAC SYSTEMS Boiler Efficiency and Controls 09 Tempterature Reset Dropdown = Yes AND/OR Chiller Efficiency and Controls 10 Temperature Reset Dropdown = Yes
Note on A16: 1/12/23: Defaults to "No". Move to "Yes" if PUMPS 05 Variable Flow Dropdown = Yes
Note on A17: 7/23/24 If I.04 = EMCS the NRCA-MCH-11 == Required, Otherwise == No
Note on A18: 1/12/23: Defaults to "No". If NRCA-MCH-05-A moves to "Yes" AND Table F. HVAC SYSTEMS 02 = Unitary AC/ Condensers
Note on A19: 1/12/23: Defaults to "No". If NRCA-MCH-05-A moves to "Yes" AND Table F. HVAC SYSTEMS 02 = "Unitary Heat Pump", "PTAC/PTHP", "SPVAC/SPVHP", "Heat Pump + AC", OR "Furnace + AC"
Note on A20: 1/12/23: This form does not automatically move to "Yes". If Distributed Energy Storage DX AC Systems are included in the scope, permit applicant should move this form to "Yes".
Note on A21: 1/12/23: Defaults to "No". Move to "Yes" if Chilled Water Storage, Ice-on-Coil Internal Melt, Ice-on-Coil External Melt, Ice Harvester, Brine, Ice-Slurry, Eutectic Salt, Clathrate Hydrate Slurry (CHS), Cryogenic or Encapulated (Ice Ball) Systems are included in the scope.
Note on A22: 1/12/23: Defaults to "No". Moves to Yes if I08 says "Included"
Note on A23: 1/12/23: Defaults to "No". Moves to "Yes" if HVAC SYSTEM Heat Rejection Equipment 12 Condenser Water Temp Reset Controls = Yes
Note on A24: 1/12/23: Defaults to "No". Moves to "Yes" if I04, I05, I06 OR I07 has an "EMCS" selection.
Note on A25: 1/12/23: Defaults to "No". Moves to "Yes" if EITHER I05 is "Occ. Sensor" OR J16 (bottom row) is "Provided per §120.1(d)5"
Note on A26: 1/12/23: Defaults to "No". Moves to "Yes" if "Ventilation" is checked in Table B AND High-rise Res is selected in Table A.
Note on A27: 1/12/23: Defaults to "No". Moves to "Yes" if Balanced Ventilation System row in Table J says "No"
Note on A28: 1/12/23: Defaults to "No". Moves to "Yes" if Table L Duct Leakage Testing, Dwelling Units = "Yes". Otherwise = "No"
Note on A29: 1/12/23: Defaults to "No". Moves to "Yes if Table H Dwelling Unit Fan Efficacy & Energy/Heat Recovery Column 9 = "…provided". Otherwise = "No"
Note on A30: 11/11/24 Defaults to "No". Moves to "Yes" When Table B Cooling Tower has been selected.

## P. NRCV (NRCC)
| User input |  |  |  | auto calculated |  |  |  | From another Table | From look up table
P. DECLARATION OF REQUIRED CERTIFICATES OF VERIFICATION
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ [d:/OnlyRG]
YES | NO | Form/Title | Systems To Be Field Verified | Field Inspector |  | Trigger |  | Ben, this is the logic that moves the selection from "No" to "Yes"
|  |  |  | Pass | Fail |  | Logic
m | m | NRCV-MCH-04-H Duct Leakage Test NOTE: Must be completed by a HERS Rater |  | o | o |  |  | Moves to Yes if NRCA-MCH-04-A moves to Yes
m | m | NRCV-MCH-24 Enclosure Air Leakage Worksheet NOTE: Must be completed by a HERS Rater |  | o | o |  |  | Moves to "Yes" if A03 = "High-rise Residential" AND "Ventilation" in B03 is checked.
m | m | NRCV-MCH-27 Indoor Air Quality and Mechanical Ventilation NOTE: Must be completed by a HERS Rater |  | o | o |  |  | Moves to "Yes" if "Bathroom IAQ & Vent." is checked in J26.
m | m | NRCV-MCH-32 Local Mechanical Exhaust NOTE: Must be completed by a HERS Rater |  | o | o |  |  | Moves to "Yes" if any of the three boxes are checked in J26.
Table Tip:
[d:OnlyUI] In addition to the Certificates of Compliance, the Standards may also require Certificates of Verification to be submitted to the authority having jurisdiction. This section of the compliance documentation serves as an acknowledgement of, and a declaration that Certificates of Verification are required to be submitted for compliance. The boxes must be checked for every Certificate of Verification that applies to the job. [d:/OnlyUI]
Note on A4: 2019 Update: This whole table is new for 2019
Note on B6: 2019 Update: Form will select based on user input in other Tables. User can edit, but if they do a note will show up in Table D. See Table D row 22 for note.
Note on A8: 12/8/22: Moves to Yes if NRCA-MCH-04-A moves to Yes
Note on C8: 2019 Update: Moved from NRCA Table O.
Note on D8: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on A9: 12/8/22: Moves to "Yes" if A03 = "High-rise Residential" AND "Ventilation" in B03 is checked.
Note on C9: 2019 Update: These last 3 are new for 2019.
Note on I9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This should be low and high rise and is only reuqired if balanced ventilation not used, so not sure about this trigger
Note on A10: 12/8/22: Moves to "Yes" if "Bathroom IAQ & Vent." is checked in J26.
Note on I10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: low and high rise
Note on A11: 12/8/22: Moves to "Yes" if any of the three boxes are checked in J26.
Note on A14: UI ONly: Table tip only applies to UI, does not apply to report generator.

## P. LMCV (LMCC)
| User input |  |  |  | auto calculated |  |  |  | From another Table | From look up table
P. DECLARATION OF REQUIRED CERTIFICATES OF VERIFICATION
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ [d:/OnlyRG]
P. DECLARATION OF REQUIRED CERTIFICATES OF VERIFICATION | [5 empty] | Trigger |  | Ben, this is the logic that moves the selection from "No" to "Yes"
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be completed by a HERS Rater and provided to the building inspector during construction. The final documents must be created by a HERS Providers registry, but drafts can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCV/ [d:/OnlyRG] | [6 empty] | Logic
YES | NO | Form/Title | Systems To Be Field Verified | Field Inspector
|  |  |  | Pass | Fail
m | m | LMCV-MCH-20 Duct Leakage Test NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-21 Duct Location Verification NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-22-H Fan Efficacy NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-23-H Airflow Rate NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-24 Enclosure Air Leakage Worksheet NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-25 Refrigerant Charge Verification NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-26-H Rated Space Conditioning System Equipment Verification NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-27 Indoor Air Quality and Mechanical Ventilation NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-28-H Return Duct Design and Air Filter Grille Device Sizing NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-29-H Duct Surface Area Reduction; Buried Ducts Compliance Credit NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-32 Local Mechanical Exhaust NOTE: Must be completed by a HERS Rater |  | o | o
m | m | LMCV-MCH-33-H Variable Capacity Heat Pump Compliance Credit NOTE: Must be completed by a HERS Rater |  | o | o
Table Tip:
[d:OnlyUI] In addition to the Certificates of Compliance, the Standards may also require Certificates of Verification to be submitted to the authority having jurisdiction. This section of the compliance documentation serves as an acknowledgement of, and a declaration that Certificates of Verification are required to be submitted for compliance. The boxes must be checked for every Certificate of Verification that applies to the job. [d:/OnlyUI]
Note on A4: 2019 Update: This whole table is new for 2019
Note on A6: 2019 Update: This whole table is new for 2019
Note on B8: 2019 Update: Form will select based on user input in other Tables. User can edit, but if they do a note will show up in Table D. See Table D row 22 for note.
Note on A10: Trujillo, Charlie: 7.11.2023 Triggers "Yes" if Table L Duct Leakage Testing, Dwelling Units = "Yes". Otherwise = "No"
Note on C10: 2019 Update: Moved from NRCA Table O.
Note on D10: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on A11: Trujillo, Charlie: 7.11.2023 Default = No
Note on C11: 2019 Update: Moved from NRCA Table O.
Note on D11: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on A12: Trujillo, Charlie: 7.11.2023 If Table H Serving Dwelling Units = "Serving Individual Dwelling Units". Otherwise = "No"
Note on C12: 2019 Update: Moved from NRCA Table O.
Note on D12: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on C13: 2019 Update: Moved from NRCA Table O.
Note on D13: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on A14: Trujillo, Charlie: 7.11.2023 Triggers yes if J.28 = gray/blank. Otherwise = No
Note on C14: 2019 Update: These last 3 are new for 2019.
Note on C15: 2019 Update: Moved from NRCA Table O.
Note on D15: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on C16: 2019 Update: Moved from NRCA Table O.
Note on D16: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on C18: 2019 Update: Moved from NRCA Table O.
Note on D18: 4.9.21 These cells are user input on the dynamic form and autopopulated in the VCA/Schema
Note on A20: Trujillo, Charlie: 7.11.2023 = Yes if Kitchen Range hood is selected in J26. Otherwise = No
Note on A24: UI ONly: Table tip only applies to UI, does not apply to report generator.

## Q. Mand Measures
| User input |  |  | auto calculated | From another Table | From look up table
Q. MANDATORY MEASURES DOCUMENTATION LOCATION
[d:OnlyUI] Table Instructions: Indicate where mandatory measures are documented in the plan set or construction documentation. For any mandatory measures that do not apply, mark the plan sheet or construction document location as "N/A", any active cells that are left blank will result in non-compliance in Table C. [d:/OnlyUI] [d:OnlyRG] This table is used to indicate where mandatory measures are documented in the plan set or construction documentation. [d:/OnlyRG]
01 |  |  | 02
Compliance with Mandatory Measures documented through MCH Mandatory Measures Note Block: |  | Dropdown | Plan sheet or construction document location
03 |  |  | 04
Mandatory Measure |  |  | Plan sheet or construction document location
Heating Equipment Efficiency per §110.1
Cooling Equipment Efficiency per §110.1
Furnace Standby Loss Control per §110.2(d)
Duct Insulation per §120.4
Heating Hot Water Equipment Efficiency per §110.1
Cooling Chilled and Condenser Water Equipment Efficiency per §110.1
Open and Closed Circuit Cooling Towers conductivity of flow-based controls per §110.2(e)1
Open and Closed Circuit Cooling Towers Flow Meter with analog output per §110.2(e)3
Open and Closed Circuit Cooling Towers Overflow Alarm per §110.2(e)4
Open and Closed Circuit Cooling Towers Efficient Drift Eliminators per §110.2(e)5
Pipe Insulation per §120.3(b)
Combustion air shutoff, combustion air fan controls and stack design and controls for boilers per §120.9
Heat Pump with Supplementary Electric Resistance Heater Controls per §110.2(b)
The air duct and plenum system is designed per §120.4(a)-(f)
Kitchen range hoods shall be rated for sound in accordance with Section 7.2 of ASHRAE 62.2
MM Note Block Dropdown
Yes
No
Note on A3: 2019 Update: Updated Table to Q.
Note on E7: Katie Gustafson: Ben, only active if Dropdown = "Yes", otherwise greyed out.
Note on A8: Katie Gustafson: Ben, rows 8-21 are hidden unless the user selects "No" in column 01. Then these rows expand for user input. October 2019 Update: rows 8-24 need to be hidden unless the user selects "No" in column 01. Then these rows expand for user input.
Note on A20: Sally Blair: All code sections referenced throughout the form will hyperlink to the correct page in the Standards pdf on CEC website. See Hyperlinks tab for hyperlinks.