| Project Name and Address | Authority Having Jurisdiction |
| --- | --- |
| Name: Project Name | Enforcement Agency: Agency |
| Address: Project Address | Permit Number: Permit Number |
| City, Zip: City, Zip Code | Permit Application Date: Date |

| Building: Enter Value | Floor: Enter Value | Room: Enter Value | Control/tag: Value |
| --- | --- | --- | --- |

| Construction inspection and functional testing comply Does Not Comply | Date Submitted to AHJ: Date |
| --- | --- |

| Intent: | - This acceptance test is intended for multifamily dwelling units where CONTINUOUS ventilation is used. This acceptance test is not permitted for Central Fan Integration (CFI) systems or other intermittent ventilation systems. - Submit one Certificate of Acceptance for each ventilation system installed to verify conformance with the requirements of the Energy Standards §160.2(b)2, Nonresidential Reference Appendices NA7.18.1.1 and NA2.2, and California Energy Commission adopted version of ANSI/ASHRAE Standards 62.2-2019. - NRCA-MCH-20a-H must be completed prior to beginning NRCA-MCH-20b-H. - If using Supply-only or Exhaust-only ventilation, Certificate of Acceptance NRCA-MCH-21-H must be completed prior to beginning NRCA-MCH-20b-H. NOTE: An uncertified technician may complete this acceptance test using this form if a HERS Rater performs the required verification, or a certified ATT may perform this acceptance test with no HERS Rater verification needed. |
| --- | --- |

Table B-1: Functional Testing – Kitchen Range Hood

| Step | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1.0 | Enter Name | Kitchen range hood manufacturer name. | NA7.18.1.1.1(e), NA2.2.4.1.4(a) |
| 2.0 | Enter Model | Equipment model number. | NA7.18.1.1.1(e), NA2.2.4.1.4(a) |
| 3.0 | No Entry | Confirm the kitchen range hood is listed in the HVI, AHAM or other CEC approved directory by selecting one of the following. | N/A |
| 3.1, or | Pass Fail N/A | The kitchen range hood is HVI certified. https://www.hvi.org/hvi-certified-products-directory/ (Pass, Fail, N/A) | NA7.18.1.1.1(f), NA2.2.4.1.4(b), §160.2(b)2Bii |
| 3.2, or | Pass Fail N/A | The kitchen range hood is AHAM certified. https://www.aham.org/AHAM/What_We_Do/Kitchen_Range_Hood_Certification (Pass, Fail, N/A) | NA7.18.1.1.1(f), NA2.2.4.1.4(b), §160.2(b)2Bii |
| 3.3 | Name or N/A | If the kitchen range hood is certified by another CEC approved directory (enter name or N/A). | NA7.18.1.1.1(f), NA2.2.4.1.4(b), §160.2(b)2Bii |
| 4.0 | Enter Value | Record the rated airflow or capture efficiency value listed in the directory. (CFM) | NA2.2.4.1.4(c) |
| 5.0 | Enter Value | Record the sound rating value listed in the directory. (Sone) | NA2.2.4.1.4(d) |
| 6.0 | Enter Value | Record the design airflow or capture efficiency value (CFM or eff.) | NRCC-MCH-E Table J |
| 7.0 | Enter Value | Record the design value (Sone) | NRCC-MCH-E Table Q |
| 8.0 | Pass Fail | Passes if the rated airflow value is greater than or equal to the design value. Check if B-1,4 >= B-1,6. | NA2.2.4.1.4(e), §160.2(b)2Avi, §160.2(b)2Bii |
| 9.0 | Pass Fail | Passes if the sound rating value is less than or equal to the design value. Check if B-1,5 <= B-1,7. | NA2.2.4.1.4(e), §160.2(b)2Avi, §160.2(b)2Bii |
| 10.0 | Pass Fail | Passes if Steps 1 through 9 are all completed and checked. | N/A |

| Declaration Statement | Signatory |
| --- | --- |
| Document Author I assert that this Certificate of Acceptance documentation is accurate and complete. | Name Company Name Author Signature Date Signed |
| Field Technician I certify the following under penalty of perjury, under the laws of the State of California: The information provided on this Certificate of Acceptance is true and correct. I am the person who performed the acceptance verification reported on this Certificate of Acceptance (Field Technician). The construction or installation identified on this Certificate of Acceptance complies with the applicable acceptance requirements indicated in the plans and specifications approved by the enforcement agency and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and signed by the responsible builder/installer and has been posted or made available with the building permit(s) issued for the building. | Name Company Name ATT No.: ATT Cert. No. Title Phone Signature Date Signed |
| Responsible Person I assert the following under penalty of perjury, under the laws of the State of California: I am the Field Technician, or the Field Technician is acting on my behalf as my employee or my agent and I have reviewed the information provided on this Certificate of Acceptance. I am eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Acceptance and attest to the declarations in this statement (responsible acceptance person). The information provided on this Certificate of Acceptance substantiates that the construction or installation identified on this Certificate of Acceptance complies with the acceptance requirements indicated in the plans and specifications approved by the enforcement agency and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and is posted or made available with the building permit(s) issued for the building. I understand that a completed, signed copy of this Certificate of Acceptance shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections, and I will take the necessary steps to ensure this requirement is accomplished. I understand that a signed copy of this Certificate of Acceptance is required to be included with the documentation the builder provides to the building owner at occupancy, and I will take the necessary steps to ensure this requirement is accomplished. | Name Company Name Lic. No.: License No. Title Phone Signature Date Signed |