| Project Name and Address | Authority Having Jurisdiction |
| --- | --- |
| Name: Project Name | Enforcement Agency: Agency |
| Address: Project Address | Permit Number: Permit Number |
| City, Zip: City, Zip Code | Permit Application Date: Date |

| Building: Enter Value | Floor: Enter Value | Room: Enter Value | Control/tag: Value |
| --- | --- | --- | --- |

| Construction inspection and functional testing comply Does not comply | Date Submitted to AHJ: Date |
| --- | --- |

| Intent: | - This acceptance test is intended for multifamily dwelling units where CONTINUOUS ventilation is used. This acceptance test is not permitted for Central Fan Integration (CFI) systems or other intermittent ventilation systems. - Submit one Certificate of Acceptance for each ventilation system installed to verify conformance with the requirements of the Energy Standards §160.2(b)2, Nonresidential Reference Appendices NA7.18.1.1 and NA2.2, and California Energy Commission adopted version of ANSI/ASHRAE Standards 62.2-2019. - NRCA-MCH-20a-H must be completed prior to beginning NRCA-MCH-20c-H. - If using Supply-only or Exhaust-only ventilation, Certificate of Acceptance NRCA-MCH-21-H must be completed prior to beginning NRCA-MCH-20c-H. NOTE: HERS verification or ATT acceptance testing required |
| --- | --- |

Table B-1: Functional Testing – IAQ Ventilation System

| Step | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail N/A | If multiple fans are specified to operate simultaneously to provide the total required ventilation airflow, the measurements within this functional test must be made with all applicable fans operating simultaneously. Verify that all fans are operational. (Pass, Fail, N/A) | NA2.2.4.1 |
| 2 | Pass Fail | Activate the ventilation system using the system control and record all values in Table B-2. | NA2.2.4.1 NA2.2.4.1.1(b) |

Table B-2: Functional Testing - Record Fan Data (NA2.2.4.1.1(a)(b)(c))

| STEP | Fan Location or ID | Exhaust Measurement (CFM) | Supply Measurement (CFM) |
| --- | --- | --- | --- |
| 1 | Enter Location or ID | Enter Value | Enter Value |
| 2 | Enter Location or ID | Enter Value | Enter Value |
| 3 | Enter Location or ID | Enter Value | Enter Value |
| 4 | Enter Location or ID | Enter Value | Enter Value |
| 5 | Enter Location or ID | Enter Value | Enter Value |
| 6 | Total of all Fans | 6.1 Enter Value | 6.2 Enter Value |
| 7 | Average of All Fans | 7.1 Enter Value | 7.2 Enter Value |

Table B-3: Functional Testing – Required Calculations

| Step | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1 | Enter Value | Record the design ventilation air flow rate for the dwelling unit. (CFM) | NRCC-MCH-E Table J |
| 2 | Percent or N/A | BALANCED SYSTEM Only: Calculate the percent difference between the exhaust and supply airflow rates. Calculate 100x(B-2,6.1–B-2,6.2)÷B-2,6.1 (Enter value in units of percent or N/A) | NA2.2.4.1.1.2(e) |

Table B-4: Functional Testing – Conditions for Passing

Conditions for passing ventilation systems that serve one dwelling unit

| Step | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail N/A | Supply Only or Exhaust Only Ventilation System passes if ALL of the following are true: - B-2,6.2 >= B-3,1, AND - NRCA-MCH-21-H is completed and complies. (Pass, Fail, N/A) | NA2.2.4.1.1(c) §160.2(b)2Aivb2 |
| 2 | Pass Fail N/A | Balanced Only Ventilation System passes if ALL of the following are true: - B-3,2 < 20%, AND - Exhaust(B-2,7.1) >= B-3,1, AND - Supply(B-2,7.2) >= B-3,1 (Pass, Fail, N/A) | NA2.2.4.1.1(g) §160.2(b)2Aivb1 |

Table B-5: Functional Testing – Conditions for Passing

Conditions for passing ventilation systems that serve multiple dwelling-units

| Step | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1 | P, F, N/A | Supply Only or Exhaust Only Ventilation System passes if both of the following are true: - B-4,1 passes, and - Exhaust: B-2,6.1 < (1.2 x B-3,1) or - Supply: B-2,6.2 < (1.2 x B-3,1) (Pass, Fail, N/A) | §160.2(b)2Avc |
| 2 | P, F, N/A | Balanced Ventilation System passes if all of the following are true: - B-4,2 Passes, AND - B-2,7.1 < (1.2 x B-3,1), AND - B-2,7.2 < (1.2 x B-3,1) (Pass, Fail, N/A) | §160.2(b)2Avc |

Table B-6: Functional Testing – Conditions for Passing

Check for passing conditions

| Step | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail | Return system to normal operating conditions. | N/A |
| 2 | Pass Fail | System passes if Tables B-1 through B-5 are completed as required and one of the following conditions for passing are checked: Table B-4, 1 or 2, indicate PASS or Table B-5, 1 or 2 indicate PASS | N/A |

| Declaration Statement | Signatory |
| --- | --- |
| Document Author I assert that this Certificate of Acceptance documentation is accurate and complete. | Name Company Name Author Signature Date Signed |
| Field Technician I certify the following under penalty of perjury, under the laws of the State of California: The information provided on this Certificate of Acceptance is true and correct. I am the person who performed the acceptance verification reported on this Certificate of Acceptance (Field Technician). The construction or installation identified on this Certificate of Acceptance complies with the applicable acceptance requirements indicated in the plans and specifications approved by the enforcement agency and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and signed by the responsible builder/installer and has been posted or made available with the building permit(s) issued for the building. | Name Company Name ATT No.: ATT Cert. No. Title Phone Signature Date Signed |
| Responsible Person I assert the following under penalty of perjury, under the laws of the State of California: I am the Field Technician, or the Field Technician is acting on my behalf as my employee or my agent and I have reviewed the information provided on this Certificate of Acceptance. I am eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Acceptance and attest to the declarations in this statement (responsible acceptance person). The information provided on this Certificate of Acceptance substantiates that the construction or installation identified on this Certificate of Acceptance complies with the acceptance requirements indicated in the plans and specifications approved by the enforcement agency and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and is posted or made available with the building permit(s) issued for the building. I understand that a completed, signed copy of this Certificate of Acceptance shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections, and I will take the necessary steps to ensure this requirement is accomplished. I understand that a signed copy of this Certificate of Acceptance is required to be included with the documentation the builder provides to the building owner at occupancy, and I will take the necessary steps to ensure this requirement is accomplished. | Name Company Name Lic. No.: License No. Title Phone Signature Date Signed |