| Project Name and Address | Authority Having Jurisdiction |
| --- | --- |
| Name: Project Name | Enforcement Agency: Agency |
| Address: Project Address | Permit Number: Permit # |
| City, Zip: City, Zip Code | Permit Application Date: Date |

| Building: Enter Value | Floor: Enter Value | Room: Enter Value | Control/tag: Value |
| --- | --- | --- | --- |

| Construction inspection and functional testing comply Does not comply | Date Submitted to AHJ: Date |
| --- | --- |

| Intent: | To demonstrate adiabatic condensers and condenser fan motor variable speed controls comply with the requirements of the Energy Code. Reference NRCC-MCH-E for nonresidential (including nonresidential spaces in high-rise multifamily) building permits or LMCC-MCH-E for nonresidential spaces in low-rise multifamily building permits. Submit one Certificate of Acceptance for each system that must demonstrate compliance. Reference120.6(a)4, 120.6(a)7, 140.4(h), 170.2(c)4F, and NA7.10.3.3. |
| --- | --- |

Table A: Construction Inspection
Prior to functional testing, verify and document all of the following:

| Step | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1.0 | Pass Fail | Verify the control system minimum Saturated Condensing Temperature (SCT) setpoint is at or below 70°F. | NA7.10.3.3.1(a) |
| 2.0 | Pass Fail | Verify the control system maximum SCT setpoint (if used) is at or near the system design SCT. | NA7.10.3.3.1(b) |
| 3.0 | Pass Fail | Verify accuracy of refrigerant pressure-temperature conversions and consistent use of either temperature or pressure for the controlled variable setpoint in the control system. | NA7.10.3.3.1(c) |
| 4.0 | Pass Fail | Verify the discharge pressure sensor (or condenser pressure if used) reads accurately, using a National Institute of Standards and Technology (NIST) traceable reference pressure gauge or meter. At the minimum, the discharge pressure sensor accuracy shall be verified at two different pressures within the typical operating range. Calibrate if needed. Replace if outside manufacturer’s recommended calibration range and retest. | NA7.10.3.3.1(d) |
| 5.0 | Pass Fail | Verify the ambient dry bulb temperature using a NIST traceable instrument, including verification of at least two different ambient readings. Calibrate if needed. Replace if outside manufacturer’s recommended calibration range and retest. | NA7.10.3.3.1(e) |
| 6.0 | Pass Fail | Verify all ambient dry bulb temperature sensors are not mounted in direct sunlight or are provided within a suitable solar shield. | NA7.10.3.3.1(f) |
| 7.0 | Pass Fail | Verify that all sensor readings used by the condenser controller convert or calculate to the correct conversion units and are displayed at the controller (e.g., observed pressure reading is correctly converted to appropriate saturated temperature, etc.). | NA7.10.3.3.1(g) |
| 8.0 | Pass Fail | Verify that all fan motors are operational and rotating in the correct direction. | NA7.10.3.3.1(h) |
| 9.0 | Pass Fail | Verify that all condenser fan speed controls operate automatically in response to changes in both pressure (SCT) and ambient temperature. | NA7.10.3.3.1(i) |
| 10.0 | Pass Fail | Check “Pass” if construction inspection complies with all requirements. Check “Fail” if construction inspection does not comply with all requirements. | N/A |

Table B: Functional Testing

| Step | Entry | Functional Testing | Code Reference |
| --- | --- | --- | --- |
| 0 | Pass Fail | Confirm that the cooling load and ambient conditions allow for typical system operation with the condenser in dry mode. | NA7.10.3.3.2 |
| 1.0 | No Entry | Verify mechanical controls and other strategies will not affect tests using steps 1.1, 1.2, 1.3, and 1.4. | NA7.10.3.3.2 Step 1 |
| 1.1 | Pass Fail | Verify condenser pressure low-limit holdback and/or bypass regulating valves, if any, are set below the minimum SCT setpoint. | NA7.10.3.3.2 Step 1(a) |
| 1.2 | Pass Fail | Turn off any heat reclaim controls and any intermittent defrost pressure offset strategies that would affect condenser setpoint control. | NA7.10.3.3.2 Step 1(b) |
| 1.3 | Enter Value | Change the adiabatic mode switching temperature in the controller to just below current ambient conditions and document the adiabatic switching setpoint. (°F) | NA7.10.3.3.2 Step 1(c) |
| 1.4 | Pass Fail | Adiabatic pads are completely dry before beginning tests. | NA7.10.3.3.2 Step 1(c) |
| 2.0 | No Entry | Verify stable fan operation at a mid-range speed level using steps 2.1 and 2.2. | NA7.10.3.3.2 Step 2 |
| 2.1 | Pass Fail | Verify the condenser control value is operating in the variable setpoint control range (i.e., above the minimum SCT setpoint and below the maximum SCT setpoint). | NA7.10.3.3.2 Step 2(a) |
| 2.2 | Pass Fail | Observe control operation for at least 30 minutes to confirm stable control operation, as shown by condenser fan speed varying as compressor capacity changes, and not ranging from maximum to minimum fan speed or constant “hunting”. | NA7.10.3.3.2 Step 2(b) |
| 3.0 | No Entry | Identify control Temperature Difference using steps 3.1, 3.2, 3.3, and 3.4. | NA7.10.3.3.2 Step 3 |
| 3.1 | Enter Value °F Enter Value psig Disch Press Cond Press | Record the current outdoor ambient-air dry bulb and refrigeration system condensing temperature/condensing pressure readings from the control system. Note whether discharge pressure or a dedicated condenser pressure sensor is used for condenser pressure control. | NA7.10.3.3.2 Step 3(a) |
| 3.2 | Enter Value psig Enter Value °F(TD) | Document current head pressure control setpoints, including the Temperature Difference (TD) setpoint. | NA7.10.3.3.2 Step 3(b) |
| 3.3 | Enter Value °F(TD) | Calculate and record the actual observed TD, defined as the difference between the dry bulb temperature and the refrigeration system SCT. | NA7.10.3.3.2 Step 3(c) |
| 3.4 | Pass Fail | Confirm agreement between the current control system TD setpoint and the observed TD. If values are different, address and correct controls system methods. | NA7.10.3.3.2 Step 3(d) |
| 4.0 | No Entry | Test adjusted control Temperature Difference (Setpoint 1) using steps 4.1, 4.2, 4.3, 4.4, and 4.5. | NA7.10.3.3.2 Step 4 |
| 4.1 | Enter Value | Enter a smaller TD value into the control system sufficient to cause an observable response, such as 1 to 2 degrees smaller, but not small enough to cause the system to operate continuously at 100% fan speed. Record this value as TD Test Setpoint 1. (°F TD) | NA7.10.3.3.2 Step 4(a) |
| 4.2 | Pass Fail | Observe change in control system operation which should include an increase in fan speed and a decrease in condensing temperature. | NA7.10.3.3.2 Step 4(b) |
| 4.3 | Enter Value psig Enter Value °F(TD) | Allow time for the control system to achieve stable operation. Document current head pressure control setpoint and TD | NA7.10.3.3.2 Step 4(c)-(d) |
| 4.4 | Enter Value | Calculate and record the actual observed TD, defined as the difference between the wet bulb temperature and the refrigeration system SCT. (°F TD) | NA7.10.3.3.2 Step 4(e) |
| 4.5 | Pass Fail | Confirm agreement between the current control system TD setpoint and the observed TD. If values are different, address and correct control system methods. | NA7.10.3.3.2 Step 4(f) |
| 5.0 | No Entry | Test adjusted control Temperature Difference (Setpoint 2) using steps 5.1 through 5.7. | NA7.10.3.3.2 Step 5 |
| 5.1 | Enter Value | Enter a TD value into the control system that is different from TD Test Setpoint 1 sufficient to cause an observable response. Record this value. (°F TD) | NA7.10.3.3.2 Step 5 |
| 5.2 | Pass Fail | Observe change in control system operation which should include an increase in fan speed and a decrease in condensing temperature. | NA7.10.3.3.2 Step 5(a) |
| 5.3 | Enter Value | Allow time for the control system to achieve stable operation. Record the current outdoor ambient dry bulb temperature. (°F) | NA7.10.3.3.2 Step 5(b)-(c) |
| 5.4 | Enter Value °F Enter Value psig | Record the current refrigeration system condensing temperature/condensing pressure readings from the control system. | NA7.10.3.3.2 Step 5(d) |
| 5.5 | Enter Value psig Enter Value °F(TD) | Document current head pressure control setpoints, including the TD setpoint. | NA7.10.3.3.2 Step 5(e) |
| 5.6 | Enter Value | Calculate and record the actual observed TD, defined as the difference between the dry bulb temperature and the refrigeration system SCT. (°F TD) | NA7.10.3.3.2 Step 5(f) |
| 5.7 | Pass Fail | Confirm agreement between the current control system TD setpoint and the observed TD. If values are different, address and correct control system methods. | NA7.10.3.3.2 Step 5(g) |
| 6.0 | Enter Value | Document current minimum condensing temperature setpoint using steps 6.1, 6.2, 6.3, and 6.4. (°F) | NA7.10.3.3.2 Step 6 |
| 6.1 | No Entry | Using the control system, change the minimum condensing temperature setpoint to a value greater than the current operating condensing temperature. | NA7.10.3.3.2 Step 6 |
| 6.2 | Pass Fail | Condenser fan controls modulate to decrease capacity. | NA7.10.3.3.2 Step 6(a) |
| 6.3 | Pass Fail | All condenser fans serving common condenser loop modulate in unison. | NA7.10.3.3.2 Step 6(b) |
| 6.4 | Pass Fail | Condenser fan controls stabilize within a 5-minute period. | NA7.10.3.3.2 Step 6(c) |
| 7.0 | No Entry | Using the control system, reset the system head pressure controls, fan motor controls and minimum condensing temperature control setpoint to original settings documented in Steps 3 and 6. | NA7.10.3.3.2 Step 7 |
| 8.0 | No Entry | Restore any heat reclaim, floating suction pressure, floating head pressure and defrost functionality. Reset the minimum condensing temperature setpoint to the value documented in Step 6. | NA7.10.3.3.2 Step 8 |
| 9.0 | Pass Fail | Check “Pass” if all Functional Test results comply with requirements. | N/A |

| Declaration Statement | Signatory |
| --- | --- |
| Document Author I assert that this Certificate of Acceptance documentation is accurate and complete. | Name Company Name Author Signature Date Signed |
| Field Technician I certify the following under penalty of perjury, under the laws of the State of California: The information provided on this Certificate of Acceptance is true and correct. I am the person who performed the acceptance verification reported on this Certificate of Acceptance (Field Technician). The construction or installation identified on this Certificate of Acceptance complies with the applicable acceptance requirements indicated in the plans and specifications approved by the enforcement agency and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and signed by the responsible builder/installer and has been posted or made available with the building permit(s) issued for the building. | Name Company Name ATT No.: ATT Cert. No. Title Phone Signature Date Signed |
| Responsible Person I assert the following under penalty of perjury, under the laws of the State of California: I am the Field Technician, or the Field Technician is acting on my behalf as my employee or my agent and I have reviewed the information provided on this Certificate of Acceptance. I am eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Acceptance and attest to the declarations in this statement (responsible acceptance person). The information provided on this Certificate of Acceptance substantiates that the construction or installation identified on this Certificate of Acceptance complies with the acceptance requirements indicated in the plans and specifications approved by the enforcement agency and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and is posted or made available with the building permit(s) issued for the building. I understand that a completed, signed copy of this Certificate of Acceptance shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections, and I will take the necessary steps to ensure this requirement is accomplished. I understand that a signed copy of this Certificate of Acceptance is required to be included with the documentation the builder provides to the building owner at occupancy, and I will take the necessary steps to ensure this requirement is accomplished. | Name Company Name Lic. No.: License No. Title Phone Signature Date Signed |