| Project Name and Address | Authority Having Jurisdiction |
| --- | --- |
| Name: Project Name | Enforcement Agency: Agency |
| Address: Project Address | Permit Number: Permit # |
| City, Zip: City, Zip Code | Permit Iss. Date: Date |

| Building: Enter Value | Floor: Enter Value | Room: Enter Value | Control: Enter Value |
| --- | --- | --- | --- |

| Construction Inspection and Functional Testing Comply Does not comply | Date Submitted to AHJ: Date |
| --- | --- |

| Intent: | Verify that the evaporative condenser has ambient wet-bulb following control and fan motor variable speed control. Reference NRCC-MCH-E for nonresidential (including nonresidential spaces in high-rise multifamily) building permits or LMCC-MCH-E for nonresidential spaces in low-rise multifamily building permits. Submit one Certificate of Acceptance for each system that must demonstrate compliance. Reference 120.6(a)7, 140.4(h), 170.2(c)4F; NA10.3.1.. |
| --- | --- |

Table A. Construction Inspection (NA7.10.3.1.1)
Prior to functional testing, verify and document all of the following:

| STEP | Entry | Item | Code Reference |
| --- | --- | --- | --- |
| 1 | Pass Fail | Verify that the minimum condensing temperature control setpoint is at or below 70°F | NA7.10.3.1.1(a) |
| 2 | Pass Fail | Verify that the master system controller saturated condensing temperature input is the temperature equivalent reading of the condenser pressure sensor.. | NA7.10.3.1.1(b) |
| 3 | Pass Fail N/A | Verify that all drain leg pressure regulator valves (if used) are set below the minimum condensing temperature/pressure setpoint.. | NA7.10.3.1.1(c) |
| 4 | Pass Fail N/A | Verify that all the receiver pressurization valves, such as the outlet pressure regulator (OPR), (if used) are set lower than the drain leg pressure regulator valve setting.. | NA7.10.3.1.1(d) |
| 5 | Pass Fail | Verify that all condenser pressure, temperature, and humidity sensors read accurately. | NA7.10.3.1.1 (e,f,g) |
| 6 | Pass Fail | Verify that all temperature sensors used by the controller are mounted in a location that is not exposed to direct sunlight.. | NA7.10.3.1.1(h) |
| 7 | Pass Fail | Verify that all sensor readings used by the condenser controller convert or calculate to the correct conversion units at the controller. | NA7.10.3.1.1(i) |
| 8 | Pass Fail | Verify that all condenser fan motors are operational and rotating in the correct direction.. | NA7.10.3.1.1(j) |
| 9 | Pass Fail | Verify that all condenser fan speed controls are operational and connected to condenser fan motors to operate the fans serving a common condenser loop in unison.. | NA7.10.3.1.1(k) |
| 10 | Pass Fail | Verify that all speed controls are in “auto” mode. | NA7.10.3.1.1(l) |
| 11 | Pass Fail | Check “Pass” if construction inspection complies with all requirements. Check “Fail” if construction inspection does not comply with all requirements. | N/A |

Table B. Functional Testing (NA7.10.3.1.2)

The system cooling load must be sufficiently high to run the test, i.e. with a condensing temperature above the minimum SCT set point. The loads can often be increased somewhat as required to perform the Functional Testing.

| STEP | Entry | Functional Test | Code Reference |
| --- | --- | --- | --- |
| 1 | No Entry | Override any conflicting controls before performing functional tests.. | NA7.10.3.1.2 Step 1 |
| 2 | No Entry | Document the current operating conditions and the current set points in 2.1, 2.2, 2.3, 2.4, 2.5, and 2.6:. | NA7.10.3.1.2(a) |
| 2.1 | Enter Value | Current ambient relative humidity(RH). (% RH) | NA7.10.3.1.2 Step 2(a) |
| 2.2 | Enter Value | Current ambient wet-bulb temperature. (°F WBT) Calculate this value from the value or 2.1 and the ambient dry-bulb temperature as necessary.. | NA7.10.3.1.2 Step 2(a) |
| 2.3 | Enter Value °F psig | Current saturated condensing temperature (SCT) or condensing pressure.. | NA7.10.3.1.2 Step 2(a) |
| 2.4 | Enter Value | Calculate the actual condenser temperature difference (Actual TD) [SCT – WBT]. (°F). | NA7.10.3.1.2 Step 2(b) |
| 2.5 | Enter Value °F psig | Current SCT or pressure control set point.. | NA7.10.3.1.2 Step 2(b) |
| 2.6 | Enter Value | Current condenser control temperature difference (Control TD). (°F). | NA7.10.3.1.2 Step 2(c) |
| 3 | No Entry | Update the Control TD set point to the Actual TD obtained in Step 2. This will be referred to as the “test set point.” Allow 5 minutes for condenser fan speed to normalize.. | NA7.10.3.1.2 Step 3 |
| 4 | No Entry | Raise the test setpoint in 1°F increments until the condenser fan control modulates to minimum fan motor speed.. | NA7.10.3.1.2 Step 4 |
| 4.1 | Pass Fail | Verify that the fan motor speed decreases.. | NA7.10.3.1.2 Step 4(d) |
| 4.2 | Pass Fail | Verify that all condenser fan motors serving common condenser loop decrease speed in unison in response to controller output; observed at the control system and at the condenser(s).. | NA7.10.3.1.2 Step 4(e) |
| 4.3 | Enter Value rpm % | Record the minimum fan speed. Enter with units as rpm, or percent of full speed (%).. | NA7.10.3.1.2 Step 4(f) |
| 4.4 | No Entry | If system is already operating at minimum saturated condensing temperature/head pressure, reverse Steps 4 and 5 | NA7.10.3.1.2 Step 4(g) |
| 5 | No Entry | Lower the test setpoint in 1°F increments until the condenser fan control modulates to increase fan motor speed.. | NA7.10.3.1.2 Step 5 |
| 5.1 | Pass Fail | Verify that the fan motor speed increases.. | NA7.10.3.1.2 Step 5(h) |
| 5.2 | Pass Fail | Verify that all condenser fan motors serving common condenser loop increase speed in unison in response to controller output; observed at the control system and at the condenser(s).. | NA7.10.3.1.2 Step 5(i) |
| 6 | No Entry | Verify the override minimum SCT setpoint.. | NA7.10.3.1.2 Step 6 |
| 6.1 | Enter Value | Document the current minimum SCT setpoint. (°F). | NA7.10.3.1.2 Step 6 |
| 6.2 | No Entry | Using the control system, change the minimum condensing temperature setpoint to a value greater than the current operating condensing temperature. | NA7.10.3.1.2 Step 6 |
| 6.3 | Pass Fail | Verify that the condenser fan controls modulate to decrease capacity. | NA7.10.3.1.2 Step 6(j) |
| 6.4 | Pass Fail | Verify that all condenser fans serving common condenser loop modulate in unison. | NA7.10.3.1.2 Step 6(k) |
| 6.5 | Pass Fail | Verify that the condenser fan controls stabilize within a 5-minute period. | NA7.10.3.1.2 Step 6(l) |
| 7 | No Entry | Restore the Control TD and the minimum SCT setpoint to the values recorded Step #2.5 and #6.1. | NA7.10.3.1.2 Step 7 |
| 8 | No Entry | Restore any controls disabled in Step #1. | NA7.10.3.1.2 Step 8 |
| 9 | Pass Fail | Check if Functional Test complies with all requirements. | N/A |

| Declaration Statement | Signatory |
| --- | --- |
| Document Author I assert that this Certificate of Acceptance documentation is accurate and complete. | Name Company Name Author Signature Date Signed |
| Field Technician I assert the following under penalty of perjury, under the laws of the State of California: The information provided on this Certificate of Acceptance is true and correct. I am the person who performed the acceptance verification reported on this Certificate of Acceptance (Field Technician). The construction or installation identified on this Certificate of Acceptance complies with the applicable acceptance requirements indicated in the plans and specifications approved by the enforcement agency, and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and signed by the responsible builder/installer and has been posted or made available with the building permit(s) issued for the building. | Name Company Name ATT No.: ATT Cert. No. Title Phone Signature Date Signed |
| Responsible Person I assert the following under penalty of perjury, under the laws of the State of California: I am the Field Technician, or the Field Technician is acting on my behalf as my employee or my agent and I have reviewed the information provided on this Certificate of Acceptance. I am eligible under Division 3 of the Business and Professions Code in the applicable classification to accept responsibility for the system design, construction or installation of features, materials, components, or manufactured devices for the scope of work identified on this Certificate of Acceptance and attest to the declarations in this statement (responsible acceptance person). The information provided on this Certificate of Acceptance substantiates that the construction or installation identified on this Certificate of Acceptance complies with the acceptance requirements indicated in the plans and specifications approved by the enforcement agency, and conforms to the applicable acceptance requirements and procedures specified in Reference Nonresidential Appendix NA7. I have confirmed that the Certificate(s) of Installation for the construction or installation identified on this Certificate of Acceptance has been completed and is posted or made available with the building permit(s) issued for the building. I will ensure that a completed, signed copy of this Certificate of Acceptance shall be posted, or made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a signed copy of this Certificate of Acceptance is required to be included with the documentation the builder provides to the building owner at occupancy. | Name Company Name Lic. No.: License No. Title Phone Signature Date Signed |